## Note
Note to 2024 ETYS Appendix B
All the ratings provided in the subsequent sections represent the post fault thermal ratings of the equipment, with the exception of those with the value '9999' (in tab B-2-1a/B-2-2a). Elements with ratings of 9999 are representative of bus couplers that are encountered during the PSS/e to PowerFactory conversion process. Additionally, there are a further few line circuit breakers included in tab B-2-1a/B-2-2a, and are represented with R=0.0100, X=0.0100 and B= 0.0000.
SSSC refers to Static Synchronous Series Compensators (Power flow control devices)
All future year data is non-binding and is liable to change.

## Menu
Electricity Ten Year Statement (ETYS) 2024
Appendix B - Supplementary Technical Data
Table | Title
B-1-1a | SHE Transmission Index of Substation Codes
B-1-1b | SPT Index of Substation Codes
B-1-1c | NGET Index of Substation Codes
B-1-1d | OFTO Index of Substation Codes
B-2-1a | SHE Transmission Circuits 2024/25
B-2-1b | SPT Circuits 2024/25
B-2-1c | NGET Circuits 2024/25
B-2-1d | OFTO Circuits 2024/25
B-2-2a | SHE Transmission Circuit Changes 2025/26 to 2035/36
B-2-2b | SPT Circuit Changes 2025/26 to 2035/36
B-2-2c | NGET Circuit Changes 2025/26 to 2035/36
B-2-2d | OFTO Circuit Changes 2025/26 to 2035/36
B-3-1a | SHE Transmission Transformers Winter 2024/25
B-3-1b | SPT Transformers Winter 2024/25
B-3-1c | NGET Transformers Winter 2024/25
B-3-1d | OFTO Transformers Winter 2024/25
B-3-2a | SHE Transmission Transformer Changes 2025/26 to 2035/36
B-3-2b | SPT Transformer Changes 2025/26 to 2035/36
B-3-2c | NGET Transformer Changes 2025/26 to 2035/36
B-3-2d | OFTO Transformer Changes 2025/26 to 2035/36
B-4-1a | SHE Transmission Reactive Compensation Equipment Winter 2024/25
B-4-1b | SPT Reactive Compensation Equipment Winter 2024/25
B-4-1c | NGET Reactive Compensation Equipment Winter 2024/25
B-4-1d | OFTO Reactive Compensation Equipment Winter 2024/25
B-4-2a | SHE Transmission Reactive Compensation Equipment Changes 2025/26 to 2035/36
B-4-2b | SPT Reactive Compensation Equipment Changes 2025/26 to 2035/36
B-4-2c | NGET Reactive Compensation Equipment Changes 2025/26 to 2035/36
B-4-2d | OFTO Reactive Compensation Equipment Changes 2025/26 to 2035/36
B.5.1 | Intra GB HVDC 2024/25 to 2035/36

## B-1-1a
B-1-1a - SHE Transmission Index of Substation Codes
Site Code | Site Name | Voltage (kV)
ABBA | ABERDEEN BAY WINDFARM | 132
ABED | ABERARDER ONSHORE WIND FARM | 132
ABNE | ABERNETHY | 132
ABNE | ABERNETHY | 33
ACHE | ACHANY EXTENSION | 132
ACHE | ACHANY EXTENSION | 33
AIGA | AIGAS HYDRO | 132
AIGA | AIGAS HYDRO | 11
AIGN | AIGAS NORTH | 132
AIGN | AIGAS NORTH | 11
ALNE | ALNESS GSP | 132
ALNE | ALNESS GSP | 33
ALYT | ALYTH | 275
ALYT | ALYTH | 400
AMUL | AMULREE | 132
ANSN | AN SUIDHE NORTH | 275
ANSN | AN SUIDHE NORTH | 33
ANSU | AN SUIDHE | 132
ANSU | AN SUIDHE | 33
ARBR | ARBROATH | 132
ARBR | ARBROATH | 33
ARDK | ARDKINGLAS WIND | 132
ARDK | ARDKINGLAS WIND | 33
ARMA | ARMADALE | 132
ARMO | ARDMORE | 132
ARMO | ARDMORE | 33
ASBS | ALYTH SOLAR AND BATTERY STORAGE | 132
ASBS | ALYTH SOLAR AND BATTERY STORAGE | 400
AYRE | AYRE OFFSHORE WIND FARM | 400
BAGP | BAILLIE GREENER GRID PARK | 275
BALA | BALALLAN | 132
BANN | BANNISKIRK | 400
BEAT | BEATRICE ONSHORE | 400
BEAU | BEAULY | 132
BEAU | BEAULY | 275
BEAU | BEAULY | 33
BEAU | BEAULY | 400
BEIN | BEINNEUN WIND FARM | 132
BEIN | BEINNEUN WIND FARM | 33
BERB | BERRY BURN | 275
BERB | BERRY BURN | 33
BEWF | BEAW FIELD | 132
BEWF | BEAW FIELD | 33
BHLA | BHLARAIDH WIND FARM | 132
BHLA | BHLARAIDH WIND FARM | 33
BIHI | BIRKHILL | 132
BING | BINGALLY | 400
BLBS | BLACKHILLOCK BATTERY STORAGE | 33
BLBS | BLACKHILLOCK BATTERY STORAGE | 400
BLEX | BHLARAIDH EXTENSION | 132
BLEX | BHLARAIDH EXTENSION | 33
BLGH | BLARGHOUR | 132
BLHI | BLACKHILLOCK | 132
BLHI | BLACKHILLOCK | 275
BLHI | BLACKHILLOCK | 400
BOAG | BOAT OF GARTEN | 132
BOAG | BOAT OF GARTEN | 33
BONB | BONNYBRIDGE BORDER NODE | 275
BONB | BONNYBRIDGE BORDER NODE | 400
BOWD | BOWDUN OFFSHORE | 400
BRCW | BRACO WEST | 132
BRCW | BRACO WEST | 275
BRCW | BRACO WEST | 33
BREC | BRECHIN | 132
BRID | BRIDGE OF DUN | 132
BRID | BRIDGE OF DUN | 33
BROA | BROADFORD | 132
BROA | BROADFORD | 33
BROR | BRORA | 132
BROR | BRORA | 33
BUCH | Buchan | 400
BUMU | BURGHMUIR | 132
BUMU | BURGHMUIR | 33
CAAD | CARRADALE | 132
CAAD | CARRADALE | 33
CAAI | CARNAIG | 400
CADU | CAIRN DUHIE | 275
CAID | CAIRN DUHIE WIND FARM | 275
CAID | CAIRN DUHIE WIND FARM | 33
CAIN | CAIRNFORD | 275
CAIN | CAIRNFORD | 33
CAIN | CAIRNFORD | 400
CALD | CALEDONIA OFFSHORE | 400
CASS | CASSLEY | 132
CASS | CASSLEY | 33
CEAN | CEANNACROC | 132
CEAN | CEANNACROC | 11
CHAR | CHARLESTON | 132
CHAR | CHARLESTON | 33
CHLS | CHLEANSAID | 132
CLAC | CLACHAN | 132
CLAC | CLACHAN | 11
CLAY | CLAYHILLS | 132
CLAY | CLAYHILLS | 33
CLGO | CLASH GOUR WIND FARM | 132
CLGO | CLASH GOUR WIND FARM | 275
CLOI | CLOICHE WIND FARM | 132
CLOI | CLOICHE WIND FARM | 33
CLUN | CLUNIE | 132
CLUN | CLUNIE | 11
CMBS | CAMBUSHINNIE | 400
COFD | COACHFORD | 400
COGA | CORRIEGARTH WIND FARM | 132
COGA | CORRIEGARTH WIND FARM | 33
COGL | COIRE GLAS PUMPED STORAGE | 400
CONN | CONNAGILL | 132
CONN | CONNAGILL | 275
CORI | CORRIEMOILLIE | 132
CORI | CORRIEMOILLIE | 33
COST | COSTA HEAD | 132
COST | COSTA HEAD | 33
COUA | COUPAR ANGUS | 132
COUA | COUPAR ANGUS | 33
CRAI | CRAIGIEBUCKLER | 132
CRAI | CRAIGIEBUCKLER | 33
CRAR | CRARAE | 132
CRAR | CRARAE | 33
CRAS | CRARAE SOUTH | 275
CRAS | CRARAE SOUTH | 33
CRDH | CREAG DHUBH | 132
CRDH | CREAG DHUBH | 275
CREA | CREAG RIABHACH WINDFARM | 132
CREA | CREAG RIABHACH WINDFARM | 33
CRMU | CRAIG MURRAIL | 275
CRMU | CRAIG MURRAIL | 33
CRSN | CROSSAIG NORTH | 132
CRSN | CROSSAIG NORTH | 275
CRSS | CROSSAIG | 132
CRSS | CROSSAIG | 275
CRSS | CROSSAIG | 33
CULL | CULLIGRAN | 132
CULL | CULLIGRAN | 11
DAAS | DALLAS SUBSTATION | 275
DAAS | DALLAS SUBSTATION | 33
DALB | DALMALLY BORDER NODE | 275
DEAN | DEANIE | 132
DEAN | DEANIE | 11
DEAW | DEANIE WEST | 132
DEAW | DEANIE WEST | 11
DELL | DELL | 132
DENS | DENSIDE | 132
DLCH | DALCHORK | 132
DORE | DORENELL WIND FARM | 132
DORE | DORENELL WIND FARM | 33
DOUN | DOUNREAY | 132
DOUN | DOUNREAY | 275
DOUN | DOUNREAY | 33
DOUN | DOUNREAY | 400
DUBE | DUNBEATH | 132
DUBE | DUNBEATH | 33
DUCC | DUNMORE CABLE COMPOUND | 132
DUDH | DUDHOPE | 132
DUDH | DUDHOPE | 33
DUGR | DUNVEGAN GRID | 132
DUGR | DUNVEGAN GRID | 33
DUNA | DUNACH WIND FARM | 132
DUNM | DUNMAGLASS | 132
DUNM | DUNMAGLASS | 33
DUNO | DUNOON | 132
DUNO | DUNOON | 33
DYCE | DYCE | 132
DYCE | DYCE | 33
EARR | EARRAGHAIL | 275
EARR | EARRAGHAIL | 33
EDAY | EDAY | 132
EDIN | EDINBANE 132/33KV | 132
EDIN | EDINBANE 132/33KV | 33
EDIN | EDINBANE 132/33KV | 11
ELCH | ELCHIES | 132
ELCH | ELCHIES | 33
ELGI | ELGIN | 132
ELGI | ELGIN | 33
ELIB | ELLIBISTER SWITCHING STATION | 132
EMMO | EMMOCK | 400
ENEI | ENERGY ISLES WIND FARM | 132
ERED | EREDINE | 275
ERED | EREDINE | 33
ERRO | ERROCHTY | 132
ERRO | ERROCHTY | 33
ERRO | ERROCHTY | 11
FAAR | FARR WINDFARM | 132
FAAR | FARR WINDFARM | 33
FARI | FARIGAIG | 132
FARI | FARIGAIG | 275
FASN | FASNAKYLE | 132
FASN | FASNAKYLE | 275
FASN | FASNAKYLE | 33
FASQ | FASQUE | 132
FASQ | FASQUE | 33
FAUG | FORT AUGUSTUS | 132
FAUG | FORT AUGUSTUS | 275
FAUG | FORT AUGUSTUS | 33
FAUG | FORT AUGUSTUS | 400
FERO | FERNOCH WIND | 132
FERO | FERNOCH WIND | 33
FETT | FETTERESSO | 132
FETT | FETTERESSO | 275
FETT | FETTERESSO | 33
FETT | FETTERESSO | 400
FIDD | FIDDES | 132
FIDD | FIDDES | 33
FINL | FINLARIG | 132
FINL | FINLARIG | 11
FINS | ORKNEY FINSTOWN | 132
FINS | ORKNEY FINSTOWN | 275
FINS | ORKNEY FINSTOWN | 33
FNLN | FANELLAN | 400
FOGG | FOGGIETON | 132
FOYE | FOYERS | 275
FOYE | FOYERS | 275
FRAS | FRASERBURGH | 132
FRAS | FRASERBURGH | 33
FWIL | FORT WILLIAM | 132
FWIL | FORT WILLIAM | 33
FYRI | FYRISH | 132
FYRI | FYRISH | 275
GARB | GARELOCH BOUNDARY | 132
GILB | GILLS BAY SUBSTATION | 132
GLAG | GLENAGNES | 132
GLDO | GLENDOE SUBSTATION | 132
GLDO | GLENDOE SUBSTATION | 11
GLDY | GLENDYE | 132
GLEN | GLENMORISTON | 132
GLEN | GLENMORISTON | 11
GLFA | GLENFARCLAS | 132
GLFA | GLENFARCLAS | 33
GLKO | GLEN KYLLACHY | 132
GLNU | GLEN ULLINISH WINDFARM | 132
GLNU | GLEN ULLINISH WINDFARM | 33
GLRB | GLENROTHES BOUNDARY | 275
GLRB | GLENROTHES BOUNDARY | 400
GLUE | GLEN ULLINISH EXTENSION | 132
GORW | GORDONBUSH WINDFARM | 275
GORW | GORDONBUSH WINDFARM | 33
GREM | GREMISTA | 132
GREM | GREMISTA | 33
GRIF | GRIFFIN WINDFARM (SSE) | 132
GRIF | GRIFFIN WINDFARM (SSE) | 33
GRNS | GREENS | 400
GRNV | GREEN VOLT OFFSHORE WIND FARM | 400
GRUB | GRUDIE BRIDGE | 132
GRUB | GRUDIE BRIDGE | 33
HARI | HARRIS | 132
HARI | HARRIS | 33
HEST | HESTA HEAD | 33
HICL | HIGH CONSTELLATION | 132
HOME | HOLLANDMEY | 132
HOME | HOLLANDMEY | 33
HUNN | HUNTERSTON NORTH | 275
HURL | HURLIE | 400
HVBY | HAVBREDEY OFFSHORE WIND FARM | 400
INGA | INVERGARRY | 132
INGA | INVERGARRY | 11
INNE | INVERNESS | 132
INNE | INVERNESS | 33
INRU | INVERUGIE | 132
INVB | INVERANAN BOUNDARY | 275
INVE | INVERARAY | 132
INVR | INVERARNAN | 132
KEIT | KEITH | 132
KEIT | KEITH | 275
KEIT | KEITH | 33
KERG | KERGORD | 132
KIIN | KILLIN | 132
KIIN | KILLIN | 33
KILC | KILLIN CASCADE GROUP | 132
KILO | KINLOCHLEVEN | 132
KILO | KINLOCHLEVEN | 33
KINA | KINARDOCHY | 275
KINA | KINARDOCHY | 400
KINB | KINCARDINE BOUNDARY | 275
KINB | KINCARDINE BOUNDARY | 400
KINM | KINMUCK | 275
KINM | KINMUCK | 400
KINT | KINTORE | 132
KINT | KINTORE | 275
KINT | KINTORE | 33
KINT | KINTORE | 400
KION | KILMORACK NORTH | 132
KION | KILMORACK NORTH | 11
KIOR | KILMORACK | 132
KIOR | KILMORACK | 11
KNOC | KNOCKNAGAEL | 132
KNOC | KNOCKNAGAEL | 275
KRKN | KIRKTON | 132
KRKN | KIRKTON | 33
LAGG | LAGGAN | 132
LAIR | LAIRG | 132
LAIR | LAIRG | 33
LAIS | LAIRG SOUTH | 132
LAIS | LAIRG SOUTH | 33
LEWI | LEWIS SUBSTATION | 132
LEWI | LEWIS SUBSTATION | 400
LHEU | LOCH NAN EUN PSH | 275
LIMK | LIMEKILNS WINDFARM | 132
LKEM | LOCH KEMP PUMPED STORAGE | 275
LOCB | LOCH BUIDHE | 132
LOCB | LOCH BUIDHE | 275
LOCH | LOCHAY | 132
LOCH | LOCHAY | 11
LOCL | LOCH LUNDIE | 132
LOCL | LOCH LUNDIE | 400
LOSD | LONGSIDE | 132
LOSD | LONGSIDE | 400
LUIC | LUICHART | 132
LUIC | LUICHART | 11
LUMB | LUMBS | 132
LUNA | LUNANHEAD | 132
LUNA | LUNANHEAD | 33
LUND | LUNDAVRA | 132
LYND | LYNDHURST | 132
LYND | LYNDHURST | 33
MACD | MACDUFF | 132
MACD | MACDUFF | 33
MARA | MARRAM OFFSHORE | 400
MELG | MELGARVE SUBSTATION | 132
MELG | MELGARVE SUBSTATION | 400
MELG | MELGARVE SUBSTATION | 11
MEYG | MEYGEN | 132
MILC | MILTON OF CRAIGIE | 132
MILC | MILTON OF CRAIGIE | 33
MILW | MILLENIUM WIND | 132
MILW | MILLENIUM WIND | 33
MORF | MORAY EAST ONSHORE | 400
MOSS | MOSSFORD | 132
MOSS | MOSSFORD | 11
MOTA | MOULTAIVE | 132
MOWO | MORAY WEST ONSHORE | 400
MSHL | MOSSY HILL | 33
MUAI | MUAITHEBHEAL WIND FARM | 132
MUAI | MUAITHEBHEAL WIND FARM | 33
MUMR | MUIR MHOR OFFSHORE WIND FARM | 400
MYBS | MYBSTER | 132
MYBS | MYBSTER | 33
NAIR | NAIRN | 132
NAIR | NAIRN | 33
NANT | NANT (LOCH NANT) | 132
NANT | NANT (LOCH NANT) | 11
NASS | NEW ABERDEENSHIRE SUBSTATION | 275
NASS | NEW ABERDEENSHIRE SUBSTATION | 400
NEDE | NEW DEER | 400
NPIC | SPIORAD NA MARA OFFSHORE WIND FARM | 400
ORRI | ORRIN | 132
ORRI | ORRIN | 33
ORRI | ORRIN | 11
OWFD | OWF-100 | 132
OWPL | OWPL WINDFARM | 400
PEHE | PETERHEAD | 132
PEHE | PETERHEAD | 275
PEHE | PETERHEAD | 400
PEHG | PETERHEAD GRANGE | 132
PEHG | PETERHEAD GRANGE | 33
PEHS | PETERHEAD SHELL | 11
PERS | PERSLEY | 132
PERS | PERSLEY | 275
PERS | PERSLEY | 33
PORA | PORT ANN | 132
PORA | PORT ANN | 33
QUOI | QUOICH | 132
QUOI | QUOICH | 11
RANN | RANNOCH | 132
RANN | RANNOCH | 33
REDM | REDMOSS | 132
REDM | REDMOSS | 33
REJO | RED JOHN PSH STORAGE | 275
ROTI | ROTHIENORMAN | 33
ROTI | ROTHIENORMAN | 400
SALM | SALAMANDER OFFSHORE WIND FARM | 132
SCRA | SCARABEN OFFSHORE WIND FARM | 132
SFEE | ST FERGUS EAST | 132
SFEE | ST FERGUS EAST | 11
SFEG | ST FERGUS GAS TERMINAL | 132
SFEM | ST FERGUS MOBIL | 132
SFER | ST FERGUS | 132
SFEV | ST FERGUS VSD | 132
SFIL | ST FILLANS | 132
SFIL | ST FILLANS | 11
SGRX | SEAGREEN ONE 275KV ONSHORE | 275
SHIN | SHIN | 132
SHIN | SHIN | 33
SHIN | SHIN | 11
SLCK | SLICKLY WIND FARM | 132
SLKB | SLACKBUIE | 132
SLOY | SLOY | 132
SLOY | SLOY | 11
SPIT | SPITTAL | 132
SPIT | SPITTAL | 275
STCS | STRATHY COLLECTOR STATION | 132
STMR | STROMAR OFFSHORE WIND FARM | 400
STNG | STANNERGATE | 33
STNG | STANNERGATE | 132
STOR | STORNOWAY | 132
STOR | STORNOWAY | 33
STRB | STRATH BRORA WIND | 275
STRB | STRATH BRORA WIND | 33
STRI | STRICHEN | 132
STRI | STRICHEN | 33
STRL | STRONELAIRG WIND FARM (SSE) | 132
STRL | STRONELAIRG WIND FARM (SSE) | 33
STRW | STRATHY WIND | 132
STRW | STRATHY WIND | 33
STSO | STRATHY SOUTH | 132
STSO | STRATHY SOUTH | 33
STWO | STRATHY WOOD | 132
STWO | STRATHY WOOD | 33
SYEL | SOUTH YELL | 132
TARL | TARLAND | 132
TARL | TARLAND | 33
TAYN | TAYNUILT | 132
TAYN | TAYNUILT | 33
TEAL | TEALING | 132
TEAL | TEALING | 275
TEAL | TEALING | 33
THUS | THURSO SOUTH | 132
THUS | THURSO SOUTH | 275
THUS | THURSO SOUTH | 33
THUS | THURSO SOUTH | 400
TLSK | TALISK OFFSHORE WIND FARM | 400
TNGF | TANGY IV | 132
TNGF | TANGY IV | 33
TOMT | TOMATIN | 132
TOMT | TOMATIN | 275
TUMB | TUMMEL BRIDGE | 132
TUMB | TUMMEL BRIDGE | 11
TUMM | TUMMEL | 132
TUMM | TUMMEL | 275
TUMM | TUMMEL | 400
WFIB | WESTFIELD BOUNDARY | 275
WFIB | WESTFIELD BOUNDARY | 400
WHIB | WHITE BRIDGE | 132
WHTB | WHISTLEFIELD BORDER | 132
WIOW | WILLOWDALE | 132
WIOW | WILLOWDALE | 33
WOHI | WOODHILL | 132
WOHI | WOODHILL | 33

## B-1-1b
B-1-1b - SPT Index of Substation Codes
Site Code | Site Name | Voltage (kV)
AIKE | AIKENGALL | 33
AREC | ARECLEOCH | 132
AREC | ARECLEOCH | 33
AREX | ARECLEOCH EXTENSION | 132
AREX | ARECLEOCH EXTENSION | 33
ARCR | ARECLEOCH REPOWERING | 275
ARCR | ARECLEOCH REPOWERING | 33
ARRS | ARRESGILL | 132
ARRS | ARRESGILL | 33
ARFO | ARTFIELD FOREST WF | 132
ARFO | ARTFIELD FOREST WF | 33
AUCH | AUCHENCROSH | 275
AUBU | AUCHENMADY BURN | 132
AUBU | AUCHENMADY BURN | 33
AUCW | AUCHENWYND | 132
AYR- | AYR | 275
AYR- | AYR | 33
AYRS | AYRSHIRE GRID COLLECTOR | 400
BAIN | BAINSFORD | 132
BAIN | BAINSFORD | 33
BAGA | BATHGATE | 132
BAGA | BATHGATE | 33
BENB | BENBRACK WIND FARM | 132
BENB | BENBRACK WIND FARM | 33
BERW | BERWICK | 132
BERW | BERWICK | 33
BLCW | BLACKCRAIG | 132
BLCW | BLACKCRAIG | 33
BLKS | BLACKCRAIG SOUTH | 33
BLAH | BLACKHILL | 132
BLAH | BLACKHILL | 33
BLKL | BLACKLAW | 132
BLKL | BLACKLAW | 33
BLLX | BLACKLAW EXTENSION | 132
BLLX | BLACKLAW EXTENSION | 33
BONN | BONNYBRIDGE | 400
BONN | BONNYBRIDGE | 275
BONN | BONNYBRIDGE | 132
BONN | BONNYBRIDGE | 33
BONB | BONNYBRIDGE BORDER NODE | 400
BONB | BONNYBRIDGE BORDER NODE | 275
BPGR | BP GRANGEMOUTH | 33
BRAP | BRAEHEAD PARK | 132
BRAP | BRAEHEAD PARK | 33
BRNX | BRANXTON | 400
BREE | BREEZY HILL | 132
BROC | BROKEN CROSS | 132
BROT | BROKEN CROSS TEE | 132
BROX | BROXBURN | 132
BROX | BROXBURN | 33
BUSB | BUSBY | 275
CATY | CARNTYNE | 132
CATY | CARNTYNE | 33
CRCK | CARRICK | 275
CRCK | CARRICK | 33
CAFA | CARSFAD | 132
CAFA | CARSFAD | 11
CHAP | CHAPELCROSS | 132
CHAP | CHAPELCROSS | 33
CHAS | CHARLOTTE STREET | 275
CHAS | CHARLOTTE STREET | 33
CHMO | CHIRMORIE | 132
CLAU | CLAUCHRIE | 132
CLAU | CLAUCHRIE | 33
CLAW | CLAWFIN | 132
CLFO | CLOICH FOREST | 132
CLFO | CLOICH FOREST | 33
CLYN | CLYDE NORTH | 275
CLYN | CLYDE NORTH | 33
CLYS | CLYDE SOUTH | 275
CLYS | CLYDE SOUTH | 33
CLYM | CLYDE'S MILL | 400
CLYM | CLYDE'S MILL | 275
CLYM | CLYDE'S MILL | 33
COAL | COALBURN | 400
COAL | COALBURN | 132
COAL | COALBURN | 33
COAB | COALBURN BATTERY STORAGE FACILITY | 400
COBA | COALBURN BATTERY STORAGE TWO | 400
COBA | COALBURN BATTERY STORAGE TWO | 33
COAN | COALBURN NORTH | 400
COAT | COATBRIDGE | 275
COAT | COATBRIDGE | 33
COCK | COCKENZIE | 400
COCK | COCKENZIE | 275
COCK | COCKENZIE | 33
CONL | CONLAND | 400
CONL | CONLAND | 275
COYL | COYLTON | 400
COYL | COYLTON | 275
COYL | COYLTON | 132
COYL | COYLTON | 33
COYT | COYLTON TEE | 132
COYW | COYLTON WEST | 275
CROO | CROOKSTON | 132
CROO | CROOKSTON | 33
CRDY | CROSSDYKES | 33
CRUA | CRUACHAN | 275
CRUA | CRUACHAN | 275
CRUA | CRUACHAN | 275
CRYR | CRYSTAL RIG | 400
CRYR | CRYSTAL RIG | 132
CRYR | CRYSTAL RIG | 33
CULR | CULROSS | 275
CCSS | CUMBERHEAD COLLECTOR | 132
CCSS | CUMBERHEAD COLLECTOR | 33
CUMW | CUMBERHEAD WEST | 132
CUMW | CUMBERHEAD WEST | 33
CUMH | CUMBERHEAD WF SUBSTATION | 33
CUMB | CUMBERNAULD | 275
CUMB | CUMBERNAULD | 132
CUMB | CUMBERNAULD | 33
CUPA | CUPAR | 132
CUPA | CUPAR | 33
CURR | CURRIE | 400
CURR | CURRIE | 275
CURR | CURRIE | 132
CURR | CURRIE | 33
CURR | CURRIE | 11
DAER | DAER WINDFARM | 132
DAER | DAER WINDFARM | 33
DALL | DALMALLY | 275
DALB | DALMALLY BORDER NODE | 275
DALM | DALMARNOCK | 275
DALM | DALMARNOCK | 132
DALM | DALMARNOCK | 33
DENN | DENNY NORTH | 400
DENN | DENNY NORTH | 275
DENN | DENNY NORTH | 132
DESA | DERSALLOCH | 132
DESA | DERSALLOCH | 33
DEBS | DEVILLA BATTERY STORAGE FACILITY | 275
DEBS | DEVILLA BATTERY STORAGE FACILITY | 33
DEVM | DEVOL MOOR | 400
DEVM | DEVOL MOOR | 132
DEVM | DEVOL MOOR | 33
DEVO | DEVONSIDE | 132
DEVO | DEVONSIDE | 33
DEWP | DEWAR PLACE | 275
DEWP | DEWAR PLACE | 33
DONO | DOUGLAS NORTH COLLECTOR | 132
DONO | DOUGLAS NORTH COLLECTOR | 33
DWEX | DOUGLAS WEST EXTENSION | 33
DRUM | DRUMCHAPEL | 275
DRUM | DRUMCHAPEL | 33
DRCR | DRUMCROSS | 132
DRCR | DRUMCROSS | 33
DUMF | DUMFRIES | 132
DUMF | DUMFRIES | 33
DUMN | DUMFRIES NORTH | 400
DUNB | DUNBAR | 132
DUNB | DUNBAR | 33
DUNF | DUNFERMLINE | 132
DUNF | DUNFERMLINE | 33
DUNH | DUNHILL | 132
DUNH | DUNHILL | 33
DUNE | DUNLAW EXTENSION | 132
DUNE | DUNLAW EXTENSION | 33
EAST | EARLSTOUN | 132
EAST | EARLSTOUN | 11
EKIL | EAST KILBRIDE | 275
EKIL | EAST KILBRIDE | 33
EKIS | EAST KILBRIDE SOUTH | 275
EKIS | EAST KILBRIDE SOUTH | 33
EERH | EASTERHOUSE | 275
EERH | EASTERHOUSE | 33
ECCF | ECCLEFECHAN | 132
ECCL | ECCLES | 400
ECCL | ECCLES | 132
ECCL | ECCLES | 33
ELDE | ELDERSLIE | 132
ELDE | ELDERSLIE | 33
ELVA | ELVANFOOT | 400
ELVA | ELVANFOOT | 275
ELVA | ELVANFOOT | 132
ELVA | ELVANFOOT | 33
ENHI | ENOCH HILL WIND FARM | 132
ENHI | ENOCH HILL WIND FARM | 33
ERSK | ERSKINE | 132
ERSK | ERSKINE | 33
ESST | ESSENSIDE | 132
ETTR | ETTRICK | 400
EUCH | EUCHANHEAD | 132
EUCH | EUCHANHEAD | 33
EWEH | EWE HILL | 132
EWEH | EWE HILL | 33
FALL | FALLAGO | 400
FALL | FALLAGO | 33
FASI | FAW SIDE | 132
FELL | FELL WIND FARM | 132
FELL | FELL WIND FARM | 33
FIGS | FIFE GRID SERVICES | 275
FINN | FINNIESTON | 132
FINN | FINNIESTON | 33
GALN | GALA NORTH | 400
GALN | GALA NORTH | 132
GALA | GALASHIELS | 132
GALA | GALASHIELS | 132
GALA | GALASHIELS | 33
GAWH | GALAWHISTLE | 132
GAWH | GALAWHISTLE | 33
GARE | GARELOCH | 132
GARB | GARELOCH BOUNDARY | 132
GIFF | GIFFNOCK | 275
GIFF | GIFFNOCK | 33
GLAP | GLEN APP | 33
GLGL | GLENGLASS | 132
GLGL | GLENGLASS | 33
GLLE | GLENLEE | 132
GLLE | GLENLEE | 11
GLLU | GLENLUCE | 132
GLLU | GLENLUCE | 33
GLMU | GLENMUCKLOCH | 33
GHPS | GLENMUCKLOCH HYDRO PUMPED STORAGE | 400
GHPS | GLENMUCKLOCH HYDRO PUMPED STORAGE | 132
GHPS | GLENMUCKLOCH HYDRO PUMPED STORAGE | 33
GLNI | GLENNISTON | 132
GLNI | GLENNISTON | 33
GLRO | GLENROTHES | 275
GLRO | GLENROTHES | 33
GLRB | GLENROTHES BOUNDARY | 400
GLRB | GLENROTHES BOUNDARY | 275
GNSH | GLENSHIMMEROCH | 132
GNSH | GLENSHIMMEROCH | 33
GORG | GORGIE | 132
GORG | GORGIE | 33
GOVA | GOVAN | 132
GOVA | GOVAN | 33
GRMO | GRANGEMOUTH | 275
GRMO | GRANGEMOUTH | 33
GRNA | GRETNA | 400
GRNA | GRETNA | 132
GRNA | GRETNA | 33
HADH | HADYARD HILL | 132
HADH | HADYARD HILL | 33
HAGR | HAGGS ROAD | 132
HAGR | HAGGS ROAD | 33
HAHA | HAGSHAW HILL PHASE 1 | 33
HAGH | HAGSHAW HILL PHASE 2 | 33
HARB | HARBURN | 400
HARE | HARESTANES | 132
HARE | HARESTANES | 33
HAKB | HARKER BORDER NODE | 400
HAKB | HARKER BORDER NODE | 132
HARR | HARTING RIG WIND FARM | 33
HAWI | HAWICK | 132
HAWI | HAWICK | 33
HAZE | HAZELSIDE | 132
HAZE | HAZELSIDE | 33
HLND | HEATHLAND | 132
HLND | HEATHLAND | 33
HELE | HELENSBURGH | 132
HELE | HELENSBURGH | 33
HOLM | HOLM HILL | 132
HORI | HOPSRIG COLLECTOR | 132
HORI | HOPSRIG COLLECTOR | 33
HUER | HUNTERSTON | 400
HUER | HUNTERSTON | 132
HBES | HUNTERSTON BATTERY STORAGE | 400
HUCS | HUNTERSTON CONVERTER STATION | 400
HUCR | HUNTERSTON CRYOBATTERY | 400
HUNE | HUNTERSTON EAST | 400
HUNE | HUNTERSTON EAST | 132
HESF | HUNTERSTON ENERGY STORAGE FACILITY | 400
HUNF | HUNTERSTON FARM | 132
HUNF | HUNTERSTON FARM | 33
HUNN | HUNTERSTON NORTH | 400
HUNN | HUNTERSTON NORTH | 275
HUNN | HUNTERSTON NORTH | 33
INWI | INNERWICK | 132
INVR | INVERARNAN | 275
INVB | INVERARNAN BORDER NODE | 275
INKE | INVERKEITHING | 132
INKE | INVERKEITHING | 33
JOHN | JOHNSTONE | 132
JOHN | JOHNSTONE | 33
JUNA | JUNCTION A | 132
JUNB | JUNCTION B | 132
JUNV | JUNCTION V | 132
KAIM | KAIMES | 275
KAIM | KAIMES | 33
KEIH | KEITHSHILL | 33
KEOO | KENDOON | 132
KEOO | KENDOON | 11
KENN | KENNOXHEAD | 132
KENN | KENNOXHEAD | 33
KENE | KENNOXHEAD WINDFARM EXTENSION | 33
KILB | KILBOWIE | 132
KILB | KILBOWIE | 33
KILB | KILBOWIE | 11
KILG | KILGALLIOCH | 275
KILG | KILGALLIOCH | 33
KIER | KILLERMONT | 132
KIER | KILLERMONT | 33
KILS | KILMARNOCK SOUTH | 400
KILS | KILMARNOCK SOUTH | 275
KILS | KILMARNOCK SOUTH | 132
KILS | KILMARNOCK SOUTH | 33
KILT | KILMARNOCK TOWN | 275
KILT | KILMARNOCK TOWN | 33
KILW | KILWINNING | 132
KILW | KILWINNING | 33
KINC | KINCARDINE | 400
KINC | KINCARDINE | 275
KINB | KINCARDINE BORDER NODE | 400
KINB | KINCARDINE BORDER NODE | 275
KINN | KINCARDINE NORTH | 400
KINN | KINCARDINE NORTH | 275
KNOK | KNOCKODHAR | 132
KNOK | KNOCKODHAR | 33
KNSH | KNOCKSHEE | 132
KYPE | KYPE MUIR | 132
KYPE | KYPE MUIR | 33
LAMB | LAMBHILL | 400
LAMB | LAMBHILL | 275
LEGO | LESMAHAGOW | 132
LEGO | LESMAHAGOW | 33
LETH | LETHANS | 132
LETH | LETHANS | 33
LEVE | LEVEN | 132
LEVE | LEVEN | 33
LEVT | LEVEN TEE | 132
LINM | LINNMILL | 132
LINM | LINNMILL | 33
LING | LIVINGSTON | 132
LING | LIVINGSTON | 33
LOAN | LONGANNET | 400
LOAN | LONGANNET | 275
LOAN | LONGANNET | 275
LORG | LORG | 132
LORG | LORG | 33
MAHI | MARK HILL | 275
MAHI | MARK HILL | 132
MAHI | MARK HILL | 33
MAYB | MAYBOLE | 132
MAYB | MAYBOLE | 33
MAYT | MAYBOLE TEE | 132
MEAD | MEADOWHEAD | 132
MIDM | MIDDLE MUIR | 132
MIDM | MIDDLE MUIR | 33
MINN | MINNYGAP | 33
MOFF | MOFFAT | 400
MOFF | MOFFAT | 132
MOFF | MOFFAT | 33
MONQ | MONQUHILL | 33
MOSM | MOSSMORRAN | 400
MOSM | MOSSMORRAN | 275
MOSM | MOSSMORRAN | 132
MOSM | MOSSMORRAN | 33
MOSH | MOSSMORRAN SHELL | 132
MOSH | MOSSMORRAN SHELL | 11
NEIL | NEILSTON | 400
NEIL | NEILSTON | 275
NEIL | NEILSTON | 132
NEIL | NEILSTON | 33
NETH | NETHERTON ENERGY | 33
NECU | NEW CUMNOCK | 400
NECU | NEW CUMNOCK | 275
NECU | NEW CUMNOCK | 132
NEAR | NEWARTHILL | 275
NEAR | NEWARTHILL | 33
NETS | NEWTON STEWART | 132
NETS | NEWTON STEWART | 33
NOKY | NORTH KYLE | 132
NOKY | NORTH KYLE | 33
NLEI | NORTH LOWTHER ENERGY INITIATIVE | 132
NLEI | NORTH LOWTHER ENERGY INITIATIVE | 33
OFOA | OLD FOREST OF AE | 132
OFOA | OLD FOREST OF AE | 33
ORLA | ORANGE LANE | 132
ORLA | ORANGE LANE | 33
OHLL | OVERHILL | 132
OHLL | OVERHILL | 33
PAIS | PAISLEY | 132
PAIS | PAISLEY | 33
PART | PARTICK | 132
PART | PARTICK | 33
PLOE | PENCLOE | 33
POGB | POGBIE | 33
PORD | PORT DUNDAS | 275
PORD | PORT DUNDAS | 33
POOB | PORTOBELLO | 275
POOB | PORTOBELLO | 33
PRST | PRIESTGILL | 33
QUAN | QUANTANS HILL | 132
QUAN | QUANTANS HILL | 33
RAVE | RAVENSCRAIG | 33
REDH | REDHOUSE | 132
REDH | REDHOUSE | 33
REDS | REDSHAW | 400
REDS | REDSHAW | 132
REDS | REDSHAW | 33
SACO | SALTCOATS | 132
SACO | SALTCOATS | 33
SAKN | SANDY KNOWE | 132
SAKN | SANDY KNOWE | 33
SNQR | SANQUHAR | 33
SANQ | SANQUHAR II WIND FARM | 132
SCOP | SCOOP HILL WIND FARM | 132
SHRG | SHEPHERDS RIG | 132
SHRU | SHRUBHILL | 275
SHRU | SHRUBHILL | 33
SIGH | SIGHTHILL | 275
SIGH | SIGHTHILL | 33
SMEA | SMEATON | 400
SMEA | SMEATON | 275
SMEA | SMEATON | 132
SMEA | SMEATON | 33
SOKY | SOUTH KYLE | 132
SPAV | SPANGO VALLEY | 132
SPAV | SPANGO VALLEY | 33
SPRB | SPIREBUSH | 132
SPRB | SPIREBUSH | 33
SANX | ST ANDREWS CROSS | 132
SANX | ST ANDREWS CROSS | 33
STWB | STELLA WEST BORDER NODE | 400
STIR | STIRLING | 132
STIR | STIRLING | 33
STOC | STRANOCH WIND FARM | 132
STOC | STRANOCH WIND FARM | 33
STHA | STRATHAVEN | 400
STHA | STRATHAVEN | 275
STHA | STRATHAVEN | 33
STLE | STRATHLEVEN | 132
STLE | STRATHLEVEN | 33
TELR | TELFORD ROAD | 132
TELR | TELFORD ROAD | 33
TEVI | TEVIOT | 400
TEVI | TEVIOT | 132
TEVB | Teviot Border Node | 400
TODD | TODDLEBURN | 33
TONG | TONGLAND | 132
TONG | TONGLAND | 33
TONG | TONGLAND | 11
TORN | TORNESS | 400
TORN | TORNESS | 132
TRLO | TRALORG | 33
TRSN | TROSTON | 132
TRSN | TROSTON | 33
WCNB | WCNC BORDER NODE | 400
WGEO | WEST GEORGE STREET | 275
WGEO | WEST GEORGE STREET | 33
WESE | WESTERDOD | 132
WFIE | WESTFIELD | 400
WFIE | WESTFIELD | 275
WFIE | WESTFIELD | 132
WFIE | WESTFIELD | 33
WFIB | WESTFIELD BOUNDARY | 400
WFIB | WESTFIELD BOUNDARY | 275
WHTL | WHISTLEFIELD | 132
WHTL | WHISTLEFIELD | 33
WHTB | WHISTLEFIELD BOUNDARY | 132
WHHO | WHITEHOUSE | 275
WHHO | WHITEHOUSE | 33
WHBR | WHITELAW BRAE | 33
WLEE | WHITELEE | 275
WLEE | WHITELEE | 33
WLEX | WHITELEE EXTENSION | 275
WLEX | WHITELEE EXTENSION | 33
WLER | WHITELEE REPOWERING | 275
WLER | WHITELEE REPOWERING | 33
WNUK | WHITENEUK | 132
WHLL | WHITESIDE HILL | 33
WIYH | WINDYHILL | 400
WIYH | WINDYHILL | 275
WIYH | WINDYHILL | 132
WIYH | WINDYHILL | 33
WISH | WISHAW | 400
WISH | WISHAW | 275
WISH | WISHAW | 132
WISH | WISHAW | 33
WYSE | WYSEBY HILL | 400
WYSE | WYSEBY HILL | 400

## B-1-1c
B-1-1c - NGET Index of Substation Codes
Site Code | Site Name | Voltage (kV)
ABTH | ABERTHAW | 275
ABTH | ABERTHAW | 132
ABHA | ABERTHAW | 400
ABHA | ABHAM | 132
ALDW | ALDWARKE | 275
ALDW | ALDWARKE | 33
ALST | ALPHA STEEL | 33
ALVE | ALVERDISCOTT | 400
ALVE | ALVERDISCOTT | 132
AMEM | AMERSHAM MAIN | 400
AMEM | AMERSHAM MAIN | 132
AXMI | AXMINSTER | 400
AXMI | AXMINSTER | 132
BACT | BACTON | 400
BAGB | BAGLAN BAY | 275
BARK | BARKING | 400
BARK | BARKING | 275
BARK | BARKING | 132
BARP | BARKING POWER | 275
BARW | BARKING WEST | 33
BEDD | BEDDINGTON | 400
BEDD | BEDDINGTON | 275
BEDD | BEDDINGTON | 132
BEDT | BEDDINGTON TEE | 132
BENR | BENGEWORTH ROAD | 400
BENR | BENGEWORTH ROAD | 132
BESW | BERKSWELL | 275
BESW | BERKSWELL | 132
BICF | BICKER FEN | 400
BICF | BICKER FEN | 132
BIGG | BIGGLESWADE | 400
BIGG | BIGGLESWADE | 132
BIRK | BIRKENHEAD | 275
BIRK | BIRKENHEAD | 132
BISW | BISHOPS WOOD | 275
BISW | BISHOPS WOOD | 132
BLYT | BLYTH | 400
BLYT | BLYTH | 275
BLYT | BLYTH | 132
BLYT | BLYTH | 66
BODE | BODELWYDDAN | 400
BOLN | BOLNEY | 400
BOLN | BOLNEY | 132
BOTW | BOTLEY WOOD | 400
BOTW | BOTLEY WOOD | 132
BRAW | BRADFORD WEST | 400
BRAW | BRADFORD WEST | 275
BRAW | BRADFORD WEST | 132
BRAI | BRAINTREE | 400
BRAI | BRAINTREE | 132
BRFO | BRAMFORD | 400
BRFO | BRAMFORD | 132
BRLE | BRAMLEY | 400
BRLE | BRAMLEY | 132
BRED | BREDBURY | 275
BRED | BREDBURY | 132
BRWA | BRIDGWATER | 400
BRWA | BRIDGWATER | 275
BRWA | BRIDGWATER | 132
BRIM | BRIMSDOWN | 400
BRIM | BRIMSDOWN | 275
BRIM | BRIMSDOWN | 132
BRIN | BRINSWORTH | 400
BRIN | BRINSWORTH | 275
BULL | BULLS LODGE | 400
BURW | BURWELL MAIN | 400
BURW | BURWELL MAIN | 132
BUSH | BUSHBURY | 275
BUSH | BUSHBURY | 132
BUST | BUSTLEHOLME | 400
BUST | BUSTLEHOLME | 275
BUST | BUSTLEHOLME | 132
CAML | CAMBLESFORTH | 66
CAMA | CAMBRIDGE ARMS | 132
CANT | CANTERBURY NORTH | 400
CANT | CANTERBURY NORTH | 132
CAPE | CAPENHURST | 400
CAPE | CAPENHURST | 275
CAPE | CAPENHURST | 132
CARE | CARDIFF EAST | 275
CARE | CARDIFF EAST | 132
CARL | CARLISLE | 400
CARR | CARRINGTON | 400
CARR | CARRINGTON | 275
CARR | CARRINGTON | 132
CELL | CELLARHEAD | 400
CELL | CELLARHEAD | 132
CHUE | CHAFFORD HUNDRED EAST | 400
CHSI | CHESSINGTON | 275
CHSI | CHESSINGTON | 132
CHTE | CHESTERFIELD | 400
CHTE | CHESTERFIELD | 275
CHTE | CHESTERFIELD | 132
CHIC | CHICKERELL | 400
CHIC | CHICKERELL | 132
CHIL | CHILLING | 400
CILF | CILFYNYDD | 400
CILF | CILFYNYDD | 275
CITR | CITY ROAD | 400
CITR | CITY ROAD | 132
CLEH | CLEVE HILL | 400
CONQ | CONNAHS QUAY | 400
CONQ | CONNAHS QUAY | 132
COSO | CORYTON SOUTH | 400
COTT | COTTAM | 400
COVE | COVENTRY | 275
COVE | COVENTRY | 132
COWT | COWBRIDGE TEE | 275
COWL | COWLEY | 400
COWL | COWLEY | 132
CREB | CREYKE BECK | 400
CREB | CREYKE BECK | 275
CREB | CREYKE BECK | 132
CRBB | CREYKE BECK B | 400
CULJ | CULHAM JET | 400
CULJ | CULHAM JET | 33
DAIN | DAINES | 400
DAMC | DAMHEAD CREEK | 400
DIDC | DIDCOT | 400
DINO | DINORWIG | 400
DISS | DISS | 400
DRAK | DRAKELOW | 400
DRAK | DRAKELOW | 275
DRAK | DRAKELOW | 132
DRAX | DRAX | 400
DRAX | DRAX | 132
DUNG | DUNGENESS | 400
DUNG | DUNGENESS | 275
EALI | EALING | 275
EALI | EALING | 66
EACS | EAST ANGLIA COASTAL SUBSTATION | 400
ECLA | EAST CLAYDON | 400
ECLA | EAST CLAYDON | 132
EASO | EATON SOCON | 400
EASO | EATON SOCON | 132
EGGB | EGGBOROUGH | 400
ELLA | ELLAND | 275
ELLA | ELLAND | 132
ELST | ELSTREE | 400
ELST | ELSTREE | 275
ELST | ELSTREE | 132
ELST | ELSTREE | 132
ENDE | ENDERBY | 400
ENDE | ENDERBY | 132
EXET | EXETER | 400
EXET | EXETER | 132
FAWL | FAWLEY | 400
FAWL | FAWLEY | 132
FECK | FECKENHAM | 400
FECK | FECKENHAM | 275
FECK | FECKENHAM | 66
FENW | FENWICK TEE | 400
FERR | FERRYBRIDGE | 400
FERR | FERRYBRIDGE | 275
FERR | FERRYBRIDGE | 132
FERR | FERRYBRIDGE | 66
FFES | FFESTINIOG | 275
FIDF | FIDDLERS FERRY | 275
FIDF | FIDDLERS FERRY | 132
FLEE | FLEET | 400
FLEE | FLEET | 132
FLIB | FLINTSHIRE BRIDGE | 400
FOUX | FOUR CROSSES | 400
FOUX | FOUR CROSSES | 132
FOUR | FOURSTONES | 275
FOUR | FOURSTONES | 33
FOUR | FOURSTONES | 20.5
FRIS | FRISTON | 400
FRIN | FRISTON NORTH | 400
FROD | FRODSHAM | 400
FROD | FRODSHAM | 275
FROD | FRODSHAM | 132
GART | GARTH CABLE COMPOUND | 400
GRAI | GRAIN | 400
GRAI | GRAIN | 132
WALE | GRAIN WEST | 400
GRAN | GRANGE | 66
GRTO | GRANGETOWN | 66
GREN | GRENDON | 400
GREN | GRENDON | 132
GRST | GREYSTONES | 275
GRST | GREYSTONES | 66
GRIW | GRIMSBY WEST | 400
GRIW | GRIMSBY WEST | 132
GWYD | GWYDDELWERN | 400
GWYN | GWYNEDD | 400
HACK | HACKNEY | 400
HACK | HACKNEY | 275
HACK | HACKNEY | 132
HACK | HACKNEY | 66
HAMB | HAMBLETON | 400
HAMH | HAMS HALL | 400
HAMH | HAMS HALL | 275
HAMH | HAMS HALL | 132
HARK | HARKER | 400
HARK | HARKER | 275
HARK | HARKER | 132
HAKB | HARKER BOUNDARY | 400
HARG | HARKER GIS | 400
HARG | HARKER GIS | 275
HARG | HARKER GIS | 132
HATL | HARTLEPOOL | 275
HARM | HARTMOOR | 275
HARM | HARTMOOR | 66
HAWP | HAWTHORN PIT | 400
HAWP | HAWTHORN PIT | 275
HAWP | HAWTHORN PIT | 66
HEDO | HEDON (GIS) | 275
HEND | HENDON | 132
HEYS | HEYSHAM | 400
HEYS | HEYSHAM | 132
HIGM | HIGH MARNHAM | 400
HIGM | HIGH MARNHAM | 275
HIMB | HIGH MARNHAM SUBSTATION-B | 400
HIBU | HIGHBURY | 400
HINP | HINKLEY POINT | 400
HINP | HINKLEY POINT | 275
HUMR | HUMBER REFINERY | 400
HUMR | HUMBER REFINERY | 33
HURS | HURST | 275
HURS | HURST | 132
HUTT | HUTTON | 400
HUTT | HUTTON | 132
HUTT | HUTTON | 25
IMPP | IMPERIAL PARK | 400
IMPP | IMPERIAL PARK | 33
INCE | INCE | 132
INDQ | INDIAN QUEENS | 400
INDQ | INDIAN QUEENS | 132
INDQ | INDIAN QUEENS | 33
IROA | IRON ACTON | 275
IROA | IRON ACTON | 132
IRON | IRONBRIDGE | 400
IRON | IRONBRIDGE | 132
ISLI | ISLINGTON | 132
IVER | IVER | 400
IVER | IVER | 275
IVER | IVER | 132
IVER | IVER | 66
JORD | JORDANTHORPE | 275
JORD | JORDANTHORPE | 33
KEAD | KEADBY | 400
KEAD | KEADBY | 132
KEAP | KEADBY POWER | 400
KEAR | KEARSLEY | 400
KEAR | KEARSLEY | 275
KEAR | KEARSLEY | 132
KEAR | KEARSLEY | 33
KEMS | KEMSLEY | 400
KEMS | KEMSLEY | 132
KENG | KENSAL GREEN | 400
KILL | KILLINGHOLME | 400
KLYN | KINGS LYNN | 400
KINO | KINGSNORTH | 400
KINO | KINGSNORTH | 132
KIBY | KIRKBY | 275
KIBY | KIRKBY | 132
KIRK | KIRKSTALL | 275
KIRK | KIRKSTALL | 132
KITW | KITWELL | 275
KITW | KITWELL | 132
KNAR | KNARESBOROUGH | 275
KNAR | KNARESBOROUGH | 132
LACK | LACKENBY | 400
LACK | LACKENBY | 275
LACK | LACKENBY | 66
LALE | LALEHAM | 275
LALE | LALEHAM | 132
LALE | LALEHAM | 33
LAND | LANDULPH | 400
LAND | LANDULPH | 132
LAGA | LANGAGE | 400
LEMR | LEA MARSTON | 132
LEGA | LEGACY | 400
LEGA | LEGACY | 132
LEIB | LEIGHTON BUZZARD | 400
LEIS | LEISTON | 400
LEIS | LEISTON | 132
LCNA | LINCOLNSHIRE COASTAL NODE A | 400
LCNB | LINCOLNSHIRE COASTAL NODE B | 400
LISD | LISTER DRIVE | 275
LISD | LISTER DRIVE | 132
LITB | LITTLE BARFORD | 400
LITB | LITTLE BARFORD | 132
LHOR | LITTLE HORSTED | 400
LHOR | LITTLE HORSTED | 132
LITT | LITTLEBROOK | 400
LITT | LITTLEBROOK | 275
LITT | LITTLEBROOK | 132
LODR | LODGE ROAD | 66
LOFI | LONGFIELD | 400
LOVE | LOVEDEAN | 400
LOVE | LOVEDEAN | 132
LOFR | LOWER FRANKTON | 400
LOFR | LOWER FRANKTON | 132
LOFT | LOWER FRANKTON TEE | 400
MABL | MABLETHORPE | 400
MACC | MACCLESFIELD | 400
MACC | MACCLESFIELD | 275
MACC | MACCLESFIELD | 33
MANN | MANNINGTON | 400
MANN | MANNINGTON | 132
MAWO | MARCHWOOD | 400
MAGA | MARGAM | 275
MARH | MARKET HARBOROUGH | 400
MARV | MARSTON VALE | 400
MEDB | MEDBURN TEE B | 400
MEDW | MEDWAY | 400
MELK | MELKSHAM | 400
MELK | MELKSHAM | 275
MELK | MELKSHAM | 132
MIDL | MIDDLETON | 400
MILH | MILL HILL | 275
MILH | MILL HILL | 132
MILP | MILTON PARK | 33
MITY | MINETY | 400
MITY | MINETY | 132
MITY | MINETY | 33
MONF | MONK FRYSTON | 400
MONF | MONK FRYSTON | 275
MFSN | MONK FRYSTON NEW | 275
MFSN | MONK FRYSTON NEW | 400
NECH | NECHELLS | 275
NECH | NECHELLS | 132
NECT | NECTON | 400
NEEP | NEEPSEND | 400
NEEP | NEEPSEND | 275
NEEP | NEEPSEND | 33
NEWX | NEW CROSS | 400
NEWX | NEW CROSS | 275
NEWX | NEW CROSS | 132
NEWX | NEW CROSS | 66
NERY | NEW RYHALL | 400
NINF | NINFIELD | 400
NINF | NINFIELD | 132
NHYD | NORTH HYDE | 275
NHYD | NORTH HYDE | 66
NFLE | NORTHFLEET EAST | 400
NFLE | NORTHFLEET EAST | 132
NORT | NORTON | 400
NORT | NORTON | 275
NORT | NORTON | 132
NORL | NORTON LEES | 275
NORL | NORTON LEES | 33
NORW | NORWICH | 132
NORM | NORWICH MAIN | 400
NORM | NORWICH MAIN | 132
NOTR | NORWICH TROWSE | 132
NURS | NURSLING | 400
NURS | NURSLING | 132
OCKH | OCKER HILL | 275
OCKH | OCKER HILL | 132
OFFE | OFFERTON | 275
OFFE | OFFERTON | 33
OLDB | OLDBURY | 400
OLDB | OLDBURY | 275
OLDB | OLDBURY | 132
OLDS | OLDBURY ON SEVERN | 132
OSBA | OSBALDWICK | 400
OSBA | OSBALDWICK | 132
OBST | OSBALDWICK TEE | 400
PADI | PADIHAM | 400
PADI | PADIHAM | 132
PAFB | PATFORD BRIDGE | 400
PELH | PELHAM | 400
PELH | PELHAM | 132
PEMB | PEMBROKE | 400
PEMB | PEMBROKE | 132
PENI | PENISARWAUN | 400
PENN | PENN | 400
PENN | PENN | 275
PENN | PENN | 132
PERH | PENRHOS | 132
PENT | PENTIR | 400
PENT | PENTIR | 132
PEWO | PENWORTHAM | 400
PEWO | PENWORTHAM | 275
PENE | PENWORTHAM EAST | 132
PENW | PENWORTHAM WEST | 132
PITS | PITSMOOR | 275
PITS | PITSMOOR | 33
POAB | PONT ABRAHAM | 400
POPP | POPPLETON | 275
POPP | POPPLETON | 33
PORH | PORT HAM | 132
PUDM | PUDDING MILL LANE | 400
PYLE | PYLE | 275
PYLE | PYLE | 132
QUER | QUERNMOOR | 400
RAIN | RAINHILL | 275
RAIN | RAINHILL | 132
RASS | RASSAU | 400
RASS | RASSAU | 132
RATS | RATCLIFFE-ON-SOAR | 400
RATS | RATCLIFFE-ON-SOAR | 275
RATS | RATCLIFFE-ON-SOAR | 132
RAYL | RAYLEIGH | 400
RAYM | RAYLEIGH MAIN | 132
REBR | REDBRIDGE | 275
REBR | REDBRIDGE | 33
RHIG | RHIGOS | 400
RICH | RICHBOROUGH | 400
RICH | RICHBOROUGH | 132
RICB | RICHBOROUGH B | 400
ROCH | ROCHDALE | 400
ROCH | ROCHDALE | 275
ROCH | ROCHDALE | 132
ROCK | ROCKSAVAGE | 400
ROCK | ROCKSAVAGE | 132
ROWD | ROWDOWN | 400
RUGE | RUGELEY | 400
RUGE | RUGELEY | 132
RYEH | RYE HOUSE | 400
RYEH | RYE HOUSE | 132
RYHA | RYHALL | 400
SAEN | SALTEND NORTH | 275
SAEN | SALTEND NORTH | 132
SAES | SALTEND SOUTH | 275
SALH | SALTHOLME | 400
SALH | SALTHOLME | 275
SALH | SALTHOLME | 132
SAFO | SANDFORD | 400
SAFO | SANDFORD | 132
SEAB | SEABANK | 400
SEAB | SEABANK | 132
SELL | SELLINDGE | 400
SELL | SELLINDGE | 132
SHEE | SHEERNESS | 132
SHEC | SHEFFIELD CITY | 275
SHEC | SHEFFIELD CITY | 33
SHRE | SHREWSBURY | 400
SHRE | SHREWSBURY | 132
SHUR | SHURTON | 400
SING | SINGLEWELL | 400
SIZE | SIZEWELL | 400
SIZE | SIZEWELL | 132
SKLG | SKELTON GRANGE | 275
SKLG | SKELTON GRANGE | 132
SHBA | SOUTH HUMBER BANK | 400
SMAN | SOUTH MANCHESTER | 275
SMAN | SOUTH MANCHESTER | 132
SSHI | SOUTH SHIELDS | 275
SSHI | SOUTH SHIELDS | 33
SPLN | SPALDING NORTH | 400
SPEN | SPENNYMOOR | 400
SPEN | SPENNYMOOR | 132
SASA | ST ASAPHS | 132
SJOW | ST JOHNS WOOD | 400
SJOW | ST JOHNS WOOD | 275
SJOW | ST JOHNS WOOD | 132
STAL | STALYBRIDGE | 400
STAL | STALYBRIDGE | 275
STAL | STALYBRIDGE | 132
STAH | STANAH | 400
STAH | STANAH | 132
STAY | STAYTHORPE | 400
STYC | STAYTHORPE C | 132
STEN | STELLA NORTH | 132
STES | STELLA SOUTH | 132
STEW | STELLA WEST | 400
STEW | STELLA WEST | 275
STWB | STELLA WEST BORDER 400KV | 400
STSB | STOCKSBRIDGE | 400
STOB | STOKE BARDOLPH | 400
STOB | STOKE BARDOLPH | 132
SUND | SUNDON | 400
SUND | SUNDON | 132
SUND | SUNDON | 33
SUTB | SUTTON BRIDGE | 400
SWAN | SWANSEA NORTH | 400
SWAN | SWANSEA NORTH | 275
SWAN | SWANSEA NORTH | 132
TADT | TADCASTER TEE | 275
TAUN | TAUNTON | 400
TAUN | TAUNTON | 132
TEMP | TEMPLEBOROUGH | 275
TEMP | TEMPLEBOROUGH | 33
THTO | THORNTON | 400
THOM | THORPE MARSH | 400
THOM | THORPE MARSH | 275
THOM | THORPE MARSH | 66
THUR | THURCROFT | 275
THUR | THURCROFT | 66
TILB | TILBURY | 400
TILB | TILBURY | 275
TILB | TILBURY | 132
TILN | TILBURY NORTH | 400
TINP | TINSLEY PARK | 275
TINP | TINSLEY PARK | 33
TODP | TOD POINT | 275
TODP | TOD POINT | 66
TOTT | TOTTENHAM | 275
TOTT | TOTTENHAM | 132
TRAW | TRAWSFYNYDD | 400
TRAW | TRAWSFYNYDD | 275
TRAW | TRAWSFYNYDD | 132
TREM | TREMORFA | 275
TREM | TREMORFA | 33
TREU | TREUDDYN | 400
TWIN | TWINSTEAD | 400
TWIN | TWINSTEAD | 132
TYNE | TYNEMOUTH | 275
TYNE | TYNEMOUTH | 132
TYNE | TYNEMOUTH | 11
TYNE | TYNEMOUTH | 11
UPPB | UPPER BOAT | 275
UPPB | UPPER BOAT | 132
UPPB | UPPER BOAT | 33
USKM | USKMOUTH | 275
USKM | USKMOUTH | 132
WALH | WALHAM | 400
WALP | WALPOLE | 400
WALP | WALPOLE | 132
WALX | WALTHAM CROSS | 400
WALX | WALTHAM CROSS | 275
WARL | WARLEY | 275
WARL | WARLEY | 132
WASF | WASHWAY FARM | 275
WASF | WASHWAY FARM | 132
WATS | WATFORD SOUTH | 275
WATS | WATFORD SOUTH | 132
WEAV | WEAVER JUNCTION | 25
WBOL | WEST BOLDON | 275
WBOL | WEST BOLDON | 66
WBUR | WEST BURTON | 400
WBUR | WEST BURTON | 132
WHAM | WEST HAM | 400
WHAM | WEST HAM | 132
WMEL | WEST MELTON | 275
WMEL | WEST MELTON | 132
WTHU | WEST THURROCK | 400
WTHU | WEST THURROCK | 33
WWEY | WEST WEYBRIDGE | 400
WWEY | WEST WEYBRIDGE | 275
WWEY | WEST WEYBRIDGE | 132
WEMA | WESTON MARSH | 400
WHGA | WHITEGATE | 275
WHGA | WHITEGATE | 132
WHSO | WHITSON | 400
WHSO | WHITSON | 275
WHSO | WHITSON | 33
WIEN | WILLENHALL | 275
WIEN | WILLENHALL | 132
WISD | WILLESDEN | 400
WISD | WILLESDEN | 275
WISD | WILLESDEN | 132
WISD | WILLESDEN | 66
WILL | WILLINGTON | 275
WILL | WILLINGTON | 132
WILE | WILLINGTON EAST | 400
WILT | WILTON | 275
WIMB | WIMBLEDON | 400
WIMB | WIMBLEDON | 275
WIMB | WIMBLEDON | 132
WIBA | WINCOBANK | 275
WIBA | WINCOBANK | 33
WYLF | WYLFA | 400
WYLF | WYLFA | 132
WYLS | WYLFA SOUTH | 400
WYMO | WYMONDLEY | 400
WYMO | WYMONDLEY | 132
YAXL | YAXLEY | 400
OVER | YORK NORTH | 275
YORK | YORK NORTH | 400

## B-1-1d
B-1-1d - OFTO Index of Substation Codes
Site Code | Site Name | Voltage (kV)
BASO | BOREAS ONSHORE | 400
BASW | BOREAS OFFSHORE | 400
BBWO | BURBO BANK EXTENSION ONSHORE | 400
BBWO | BURBO BANK EXTENSION ONSHORE | 220
BBWW | BURBO BANK EXTENSION OFFSHORE | 220
BBWW | BURBO BANK EXTENSION OFFSHORE | 34
BEAT | BEATRICE ONSHORE | 400
BEAT | BEATRICE ONSHORE | 220
BEIW | BEATRICE OFFSHORE | 220
BEIW | BEATRICE OFFSHORE | 33
BOSO | BARROW ONSHORE | 132
BOSW | BARROW OFFSHORE | 132
BOSW | BARROW OFFSHORE | 33
DBAO | DOGGER BANK A ONSHORE | 400
DBAW | DOGGER BANK A OFFSHORE | 220
DBAW | DOGGER BANK A OFFSHORE | 33
DBBO | DOGGER BANK B ONSHORE | 400
DBBW | DOGGER BANK B OFFSHORE | 220
DBBW | DOGGER BANK B OFFSHORE | 33
DBCO | DOGGER BANK C ONSHORE | 400
DBCW | DOGGER BANK C OFFSHORE | 220
DBCW | DOGGER BANK C OFFSHORE | 66
DUDO | DUDGEON ONSHORE | 132
DUDW | DUDGEON OFFSHORE | 132
DUDW | DUDGEON OFFSHORE | 33
EAAW | EAST ANGLIA ONE OFFSHORE | 220
EAAW | EAST ANGLIA ONE OFFSHORE | 66
EABO | EAST ANGLIA TWO ONSHORE | 400
EABO | EAST ANGLIA TWO ONSHORE | 275
EABW | EAST ANGLIA TWO OFFSHORE | 275
EABW | EAST ANGLIA TWO OFFSHORE | 66
EACO | EAST ANGLIA THREE ONSHORE | 400
EACW | EAST ANGLIA THREE OFFHORE | 400
EACW | EAST ANGLIA THREE OFFHORE | 66
EANO | EAST ANGLIA ONE NORTH ONSHORE | 400
EANO | EAST ANGLIA ONE NORTH ONSHORE | 220
EANW | EAST ANGLIA ONE NORTH OFFSHORE | 220
EANW | EAST ANGLIA ONE NORTH OFFSHORE | 66
FOFO | FIRTH OF FORTH ONSHORE | 275
FOFW | FIRTH OF FORTH OFFSHORE | 275
FOFW | FIRTH OF FORTH OFFSHORE | 66
GALO | GALLOPER ONSHORE | 132
GANW | GALLOPER NORTH OFFSHORE | 132
GANW | GALLOPER NORTH OFFSHORE | 33
GGON | GREATER GABBARD ONSHORE | 132
GREG | GREATER GABBARD OFFSHORE | 132
GREG | GREATER GABBARD OFFSHORE | 33
GUNS | GUNFLEET SANDS OFFSHORE | 132
GUNS | GUNFLEET SANDS OFFSHORE | 33
GWAW | GWYNT-Y-MOR OFFSHORE A | 132
GWAW | GWYNT-Y-MOR OFFSHORE A | 33
GWBW | GWYNT-Y-MOR OFFSHORE B | 132
GWBW | GWYNT-Y-MOR OFFSHORE B | 33
GWYO | GWYNT-Y-MOR ONSHORE | 132
HOWA | HORNSEA ONE ONSHORE | 400
HOWA | HORNSEA ONE ONSHORE | 220
HOWB | HORNSEA TWO ONSHORE | 400
HOWB | HORNSEA TWO ONSHORE | 220
HOWC | HORNSEA THREE ONSHORE | 400
HOWD | HORNSEA FOUR ONSHORE | 400
HOWD | HORNSEA FOUR ONSHORE | 220
HOWR | HORNSEA REACTOR PLATFORM | 220
HOWW | HORNSEA OFFSHORE | 400
HOWW | HORNSEA OFFSHORE | 220
HOWW | HORNSEA OFFSHORE | 66
HOWW | HORNSEA OFFSHORE | 34
HUMO | HUMBER GATEWAY ONSHORE | 275
HUMO | HUMBER GATEWAY ONSHORE | 132
HUMO | HUMBER GATEWAY ONSHORE | 33
HUMW | HUMBER GATEWAY OFFSHORE | 132
HUMW | HUMBER GATEWAY OFFSHORE | 33
INCO | INCH CAPE ONSHORE | 275
INCO | INCH CAPE ONSHORE | 220
INCW | INCH CAPE OFFSHORE | 275
INCW | INCH CAPE OFFSHORE | 66
LINO | LINCS ONSHORE | 400
LINO | LINCS ONSHORE | 132
LINS | LINCS OFFSHORE | 132
LINS | LINCS OFFSHORE | 33
LOAW | LONDON ARRAY OFFSHORE WIND FARM - PLATFORM 1 | 150
LOAW | LONDON ARRAY OFFSHORE WIND FARM - PLATFORM 1 | 33
LONO | LONDON ARRAY ONSHORE | 400
LONO | LONDON ARRAY ONSHORE | 150
LOYW | LONDON ARRAY OFFSHORE WIND FARM - PLATFORM 2 | 150
LOYW | LONDON ARRAY OFFSHORE WIND FARM - PLATFORM 2 | 33
MORF | MORAY EAST ONSHORE | 275
MORO | MORAY EAST ONSHORE | 220
MOWE | MORAY EAST OFFSHORE | 220
MOWE | MORAY EAST OFFSHORE | 66
MOWO | MORAY WEST ONSHORE | 400
MOWO | MORAY WEST ONSHORE | 220
MOWW | MORAY WEST OFFSHORE | 220
MOWW | MORAY WEST OFFSHORE | 66
NNGO | NEART NA GAOITHE ONSHORE | 400
NNGO | NEART NA GAOITHE ONSHORE | 220
NNGW | NEART NA GAOITHE OFFSHORE | 220
NNGW | NEART NA GAOITHE OFFSHORE | 66
ORMO | ORMONDE ONSHORE | 132
ORMO | ORMONDE ONSHORE | 33
ORMW | ORMONDE OFFSHORE | 132
ORMW | ORMONDE OFFSHORE | 33
RACO | RACEBANK ONSHORE | 400
RACO | RACEBANK ONSHORE | 220
RACW | RACEBANK OFFSHORE | 220
RACW | RACEBANK OFFSHORE | 33
RAMW | RAMPION OFFSHORE | 150
RAMW | RAMPION OFFSHORE | 33
RBBO | RACEBANK EXTENSION ONSHORE | 400
RBBO | RACEBANK EXTENSION ONSHORE | 220
RBBW | RACEBANK EXTENSION OFFSHORE | 220
RBBW | RACEBANK EXTENSION OFFSHORE | 66
RORE | ROBIN RIGG EAST ONSHORE | 132
RORE | ROBIN RIGG EAST ONSHORE | 33
RORW | ROBIN RIGG WEST ONSHORE | 132
RORW | ROBIN RIGG WEST ONSHORE | 33
RREW | ROBIN RIGG EAST OFFSHORE | 132
RRWW | ROBIN RIGG WEST OFFSHORE | 132
SGRO | SEAGREEN ONE 220KV ONSHORE | 220
SGRW | SEAGREEN ONE OFFSHORE | 220
SGRW | SEAGREEN ONE OFFSHORE | 66
SGRX | SEAGREEN ONE 275KV ONSHORE | 275
SOFO | SOFIA ONSHORE | 400
SOFW | SOFIA OFFSHORE | 400
SOFW | SOFIA OFFSHORE | 66
SSAW | SHERRINGHAM SHOAL OFFSHORE PLATFORM 1 | 132
SSAW | SHERRINGHAM SHOAL OFFSHORE PLATFORM 1 | 33
SSBW | SHERRINGHAM SHOAL OFFSHORE PLATFORM 2 | 132
SSBW | SHERRINGHAM SHOAL OFFSHORE PLATFORM 2 | 33
THAW | THANET WIND ONSHORE | 132
THOW | THANET WIND OFFSHORE | 132
THOW | THANET WIND OFFSHORE | 33
TKNE | TRITON KNOLL EAST OFFSHORE | 220
TKNE | TRITON KNOLL EAST OFFSHORE | 66
TKNO | TRITON KNOLL ONSHORE | 400
TKNO | TRITON KNOLL ONSHORE | 220
TKNW | TRITON KNOLL WEST OFFSHORE | 220
TKNW | TRITON KNOLL WEST OFFSHORE | 66
TWNE | TWINEHAM ONSHORE | 400
TWNE | TWINEHAM ONSHORE | 150
VGEO | VANGUARD EAST ONSHORE | 400
VGEW | VANGUARD EAST OFFSHORE | 400
VGWO | VANGUARD WEST ONSHORE | 400
VGWW | VANGUARD WEST OFFSHORE | 400
WAAO | WALNEY 1 ONSHORE | 132
WAAW | WALNEY 1 OFFSHORE | 132
WAAW | WALNEY 1 OFFSHORE | 33
WABO | WALNEY 2 ONSHORE | 132
WABW | WALNEY 2 OFFSHORE | 132
WABW | WALNEY 2 OFFSHORE | 33
WACW | WALNEY 3 OFFSHORE | 220
WACW | WALNEY 3 OFFSHORE | 34
WADW | WALNEY 4 OFFSHORE | 220
WADW | WALNEY 4 OFFSHORE | 34
WDSO | WEST OF DUDDON SANDS ONSHORE | 400
WDSO | WEST OF DUDDON SANDS ONSHORE | 155
WDSW | WEST OF DUDDON SANDS OFFSHORE | 155
WDSW | WEST OF DUDDON SANDS OFFSHORE | 34
WERO | WESTERMOST ROUGH OFFSHORE | 150
WERO | WESTERMOST ROUGH ONSHORE | 275
WERW | WESTERMOST ROUGH OFFSHORE | 150
WERW | WESTERMOST ROUGH OFFSHORE | 34
WOWE | WALNEY EXTENSION | 400
WOWE | WALNEY EXTENSION | 220

## B-2-1a
B-2-1a - SHE Transmission Circuits for 2024/25
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
ABBA1- | DYCE1J | 0 | 7.8 | Cable | 0.1092 | 1.2324 | 10.14 | 173 | 158 | 158 | 158
ABNE1Q | ABNE1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ABNE1Q | CHAR1- | 24.5 | 0 | OHL | 2.49 | 5.66 | 1.22 | 132 | 123 | 106 | 123
ABNE1R | AMUL1G | 28.099 | 0.001 | Composite | 2.8706 | 6.5818 | 1.397 | 132 | 123 | 106 | 123
AIGA1Q | KIOR1Q | 2.797 | 0.123 | Composite | 0.264 | 0.594 | 0.66 | 126 | 117 | 101 | 117
ALNE1Q | FYRI1J | 0 | 2.1 | Cable | 0.06 | 0.202 | 2.547 | 156 | 142 | 142 | 142
ALNE1R | FYRI1K | 0 | 2.1 | Cable | 0.06 | 0.202 | 2.547 | 156 | 142 | 142 | 142
ALYT2A | ALYT2B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ALYT2A | FETT2P | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2A | KINB2J | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2A | TEAL2J | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
ALYT2B | FETT2Q | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2B | KINB2K | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2B | TEAL2K | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030
AMUL1E | AMUL1F | 0 | 8.62 | Cable | 0.2518 | 0.8041 | 10.215 | 153 | 129 | 129 | 129
AMUL1E | BUMU1R | 17.8 | 0 | OHL | 1.8184 | 4.1692 | 0.885 | 132 | 123 | 106 | 123
AMUL1F | GRIF1S | 6.85 | 0 | OHL | 0.7002 | 1.6054 | 0.341 | 132 | 123 | 106 | 123
AMUL1G | AMUL1H | 0 | 8.62 | Cable | 0.2518 | 0.8041 | 10.215 | 153 | 129 | 129 | 129
AMUL1H | GRIF1T | 6.85 | 0 | OHL | 0.7002 | 1.6054 | 0.341 | 132 | 123 | 106 | 123
ANSU1- | INVE1K | 11.35 | 0 | OHL | 0.1816 | 2.009 | 0.738 | 739 | 710 | 662 | 710
ANSU1- | PORA1R | 24.95 | 0 | OHL | 0.3992 | 4.4162 | 1.622 | 739 | 710 | 662 | 710
ARBR1Q | DENS1Q | 14.5 | 0 | OHL | 1.3195 | 3.364 | 0.725 | 132 | 123 | 106 | 123
ARBR1R | DENS1R | 14.5 | 0 | OHL | 1.3195 | 3.364 | 0.725 | 132 | 123 | 106 | 123
ARDK1- | INVE1J | 0 | 9 | Cable | 0.92 | 2.1 | 0.44 | 132 | 123 | 106 | 123
ARDK1- | SLOY1T | 0 | 10 | OHL | 1.02 | 2.33 | 0.49 | 132 | 123 | 106 | 123
ARMO1J | DUGR1Q | 14 | 0 | OHL | 2.38 | 3.94 | 0.93 | 99 | 92 | 79 | 92
BEAT4- | BLHI4- | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BEAU1J | BEAU1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BEAU1J | BEAU1R | 0 | 2.4 | Cable | 0.0315 | 0.197 | 3.941 | 265 | 263 | 263 | 263
BEAU1J | BEAU1T | 0 | 0.22 | Cable | 0.01 | 0.0147 | 0.268 | 141 | 136 | 136 | 136
BEAU1J | CULL1Q | 14 | 0 | OHL | 1.43 | 3.28 | 0.69 | 126 | 117 | 101 | 117
BEAU1J | DUCC1J | 0 | 3.1 | Cable | 0.0219 | 0.1198 | 10.47 | 444 | 403 | 403 | 403
BEAU1K | BEAU1N | 0 | 0.25 | Cable | 0.01 | 0.0167 | 0.305 | 141 | 136 | 136 | 136
BEAU1K | BEAU1S | 0 | 2.4 | Cable | 0.0315 | 0.197 | 3.941 | 265 | 263 | 263 | 263
BEAU1K | DUCC1K | 0 | 3.1 | Cable | 0.0219 | 0.1198 | 10.47 | 444 | 403 | 403 | 403
BEAU1K | KIOR1Q | 1.24 | 0.06 | Composite | 0.13 | 0.29 | 0.06 | 126 | 117 | 101 | 117
BEAU1L | BEAU1P | 0 | 1.74 | Cable | 0.0634 | 0.1599 | 2.062 | 152 | 140 | 140 | 140
BEAU1L | MOTA1R | 29.67 | 0 | OHL | 3.0145 | 6.9027 | 1.469 | 126 | 117 | 101 | 117
BEAU1M | BEAU1Q | 0 | 1.74 | Cable | 0.0634 | 0.1599 | 2.062 | 152 | 140 | 140 | 140
BEAU1M | MOTA1Q | 29.67 | 0 | OHL | 3.0145 | 6.9027 | 1.469 | 132 | 123 | 106 | 123
BEAU1N | KNOC1J | 17.1 | 0 | OHL | 1.5561 | 3.9843 | 0.855 | 132 | 123 | 106 | 123
BEAU1R | INNE1Q | 13.4 | 0 | OHL | 0.6834 | 3.0016 | 0.697 | 241 | 230 | 210 | 230
BEAU1S | INNE1R | 13.4 | 0 | OHL | 0.6834 | 3.0016 | 0.697 | 241 | 230 | 210 | 230
BEAU1T | KNOC1J | 17.1 | 0 | OHL | 1.5561 | 3.9843 | 0.855 | 132 | 123 | 106 | 123
BEAU2J | BEAU2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BEAU2J | FASN2- | 24.288 | 1.012 | Composite | 0.069 | 1.025 | 7.23 | 1910 | 1830 | 1710 | 1830
BEAU2J | FYRI2J | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 702 | 665 | 599 | 665
BEAU2J | KNOC2L | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 935 | 880 | 790 | 880
BEAU2K | FYRI2K | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 702 | 665 | 599 | 665
BEAU2K | KNOC2M | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 935 | 880 | 790 | 880
BEAU4- | FAUG4J | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2780 | 2670 | 2480 | 2670
BEIN11 | CEAN1Q | 0.87 | 0 | OHL | 0.099 | 0.205 | 0.042 | 263 | 257 | 248 | 257
BEIN11 | MILW1S | 2.8 | 0 | OHL | 0.319 | 0.66 | 0.135 | 263 | 257 | 248 | 257
BERB2Q | BLHI2J | 46.26 | 0 | OHL | 0.2619 | 1.9044 | 12.613 | 935 | 880 | 790 | 880
BERB2Q | KNOC2J | 46.98 | 0 | OHL | 0.266 | 1.934 | 12.809 | 935 | 880 | 790 | 880
BHLA11 | GLEN1Q | 0 | 7.8 | Cable | 0.1425 | 0.6104 | 28.363 | 208 | 187 | 187 | 187
BIHI1Q | CHAR1R | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229 | 211 | 183 | 211
BIHI1Q | COUA1Q | 14.6 | 0 | OHL | 0.7446 | 3.2704 | 0.753 | 241 | 230 | 210 | 230
BIHI1Q | TEAL1- | 5.6 | 0 | OHL | 0.239 | 1.199 | 0.29 | 229 | 211 | 183 | 211
BIHI1R | CHAR1- | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229 | 211 | 183 | 211
BIHI1R | COUA1R | 14.6 | 0 | OHL | 0.7446 | 3.2704 | 0.753 | 241 | 230 | 210 | 230
BIHI1R | TEAL1- | 5.6 | 0 | OHL | 0.239 | 1.199 | 0.29 | 229 | 211 | 183 | 211
BLHI1J | BLHI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI1J | DORE11 | 23.45 | 0 | OHL | 1.171 | 5.295 | 1.286 | 241 | 230 | 210 | 230
BLHI1J | KEIT1K | 0 | 3.26 | Cable | 0.0429 | 0.2582 | 4.733 | 176 | 176 | 176 | 176
BLHI1K | DORE12 | 23.45 | 0 | OHL | 1.171 | 5.297 | 1.318 | 241 | 230 | 210 | 230
BLHI1K | KEIT1J | 0 | 3.26 | Cable | 0.0429 | 0.2582 | 4.733 | 176 | 176 | 176 | 176
BLHI2J | BLHI2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI2J | KEIT2Q | 0 | 2.41 | Cable | 0.01 | 0.044 | 13.793 | 580 | 546 | 546 | 546
BLHI2J | KINT2K | 50.85 | 0 | OHL | 0.298 | 2.08 | 14.14 | 935 | 880 | 790 | 880
BLHI2K | CAIN2- | 9.77 | 0 | OHL | 0.0573 | 0.3997 | 2.717 | 935 | 880 | 790 | 880
BLHI2K | DAAS2- | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880
BLHI2K | KEIT2R | 0 | 2.49 | Cable | 0.01 | 0.0456 | 14.286 | 580 | 546 | 546 | 546
BLHI4- | BLHI4R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 1272 | 1272 | 1272 | 1272
BLHI4- | MOWO4- | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI4- | ROTI4J | 35.4 | 0 | OHL | 0.0708 | 0.6832 | 20.826 | 2000 | 1920 | 1790 | 1920
BLHI4- | ROTI4K | 35.4 | 0 | OHL | 0.0708 | 0.6832 | 20.826 | 2000 | 1920 | 1790 | 1920
BOAG1L | BOAG1Q | 0 | 5.7 | Cable | 0.0362 | 0.8819 | 7.98 | 227 | 209 | 209 | 209
BOAG1L | TOMT1L | 19.19 | 0 | OHL | 2.1877 | 4.3562 | 0.96 | 215 | 211 | 203 | 211
BOAG1M | BOAG1R | 0 | 5.7 | Cable | 0.0362 | 0.8819 | 7.98 | 227 | 209 | 209 | 209
BOAG1M | TOMT1M | 19.19 | 0 | OHL | 2.1877 | 4.3562 | 0.96 | 215 | 211 | 203 | 211
BOAG1P | BOAG1Q | 0 | 8.4 | Cable | 0.0558 | 1.271 | 11.48 | 227 | 209 | 209 | 209
BOAG1P | GLFA1- | 0 | 24.82 | Cable | 2.5189 | 5.7753 | 1.228 | 126 | 117 | 101 | 117
BONB2J | BRCW2K | 10.1 | 0 | OHL | 0.028 | 0.409 | 2.886 | 1910 | 1830 | 1710 | 1830
BONB4- | TUMM4- | 72.9 | 0 | OHL | 0.094 | 1.396 | 44.078 | 2780 | 2670 | 2480 | 2670
BRCW2J | BRCW2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BRCW2J | KINA2K | 59.8 | 0 | OHL | 0.1638 | 2.4224 | 17.089 | 1910 | 1830 | 1710 | 1830
BREC1Q | BREC1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BREC1Q | BRID1Q | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104
BREC1Q | FIDD1B | 30.4 | 0 | OHL | 3.13 | 6.52 | 2.66 | 112 | 104 | 90 | 104
BREC1R | BRID1R | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104
BREC1R | DENS1Q | 26.1 | 0 | OHL | 3.08 | 6.33 | 1.29 | 112 | 104 | 90 | 104
BROA1Q | EDIN1- | 44.9 | 0 | OHL | 6.014 | 9.963 | 2.332 | 99 | 92 | 79 | 92
BROA1Q | QUOI1Q | 63.4 | 0 | OHL | 8.99 | 14.87 | 3.11 | 99 | 92 | 79 | 92
BROR1- | BROR1Q | 1.1 | 0 | OHL | 0.1004 | 0.2561 | 0.0546 | 126 | 117 | 101 | 117
BROR1Q | DUBE1Q | 38.58 | 0 | OHL | 3.522 | 8.9813 | 1.914 | 126 | 117 | 101 | 117
BROR1Q | LOCB1T | 25.88 | 0 | OHL | 2.3626 | 6.0248 | 1.2842 | 126 | 117 | 101 | 117
BUMU1Q | BUMU1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BUMU1Q | CHAR1- | 0 | 42.2 | Cable | 4.29 | 9.76 | 2.1 | 132 | 123 | 106 | 123
CAAD1Q | CRSS1J | 13.08 | 0 | OHL | 0.3091 | 2.7749 | 0.721 | 448 | 430 | 398 | 430
CAAD1R | CRSS1K | 13.08 | 0 | OHL | 0.3091 | 2.7749 | 0.721 | 448 | 430 | 398 | 430
CAIN2- | KINT2J | 41.08 | 0 | OHL | 0.2407 | 1.6803 | 11.423 | 935 | 880 | 790 | 880
CASS1Q | DLCH1A | 28 | 0 | OHL | 2.562 | 6.09 | 1.2 | 111 | 103 | 89 | 103
CHAR1- | CHAR1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 229 | 211 | 183 | 211
CHAR1- | CHAR1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CHAR1- | CHAR1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CHAR1S | GLAG1Q | 0.935 | 1.375 | Composite | 0.1697 | 0.3805 | 1.708 | 126 | 117 | 101 | 117
CHAR1S | LYND1Q | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117
CHAR1T | GLAG1R | 0.935 | 1.375 | Composite | 0.1697 | 0.3805 | 1.708 | 126 | 117 | 101 | 117
CHAR1T | LYND1R | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117
CLAC1Q | INVE1J | 8.4 | 0 | OHL | 0.85 | 1.95 | 0.41 | 126 | 117 | 101 | 117
CLAC1Q | SLOY1F | 13.05 | 0 | OHL | 1.1875 | 3.0406 | 0.653 | 132 | 123 | 106 | 123
CLAY1Q | REDM1Q | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 100 | 100 | 100
CLAY1Q | WIOW1Q | 0 | 2.1 | Cable | 0.0474 | 0.1253 | 2.897 | 155 | 129 | 129 | 129
CLAY1R | REDM1R | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 100 | 100 | 100
CLAY1R | WIOW1R | 0 | 2.1 | Cable | 0.0474 | 0.1253 | 2.897 | 155 | 129 | 129 | 129
CLUN1Q | CLUN1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CLUN1R | CLUN1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
CLUN1S | COUA1Q | 38.1 | 0 | OHL | 1.9301 | 8.5468 | 1.966 | 241 | 230 | 210 | 230
CLUN1S | ERRO1K | 15.4 | 0 | OHL | 1.406 | 3.58 | 0.764 | 126 | 117 | 101 | 117
CLUN1T | COUA1R | 38.1 | 0 | OHL | 1.9301 | 8.5468 | 1.966 | 241 | 230 | 210 | 230
CLUN1T | ERRO1J | 15.4 | 0 | OHL | 1.406 | 3.58 | 0.764 | 126 | 117 | 101 | 117
COGA1- | COGA1C | 13.9 | 0 | OHL | 0.7002 | 2.8782 | 0.778 | 241 | 230 | 210 | 230
COGA1C | FARI1J | 0 | 4.11 | Cable | 0.065 | 0.334 | 6.245 | 210 | 196 | 196 | 196
CONN1C | CONN1J | 0 | 0.76 | Cable | 0.0161 | 0.0631 | 1.035 | 200 | 178 | 178 | 178
CONN1C | STRW1A | 12 | 0 | OHL | 0.605 | 2.485 | 0.672 | 241 | 230 | 210 | 230
CONN2J | DOUN2- | 10.34 | 0 | OHL | 0.0621 | 0.5689 | 2.193 | 702 | 665 | 599 | 665
CONN2J | LOCB2J | 76.071 | 0.269 | Composite | 0.458 | 4.1987 | 16.184 | 702 | 665 | 599 | 665
CORI1J | CORI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CORI1J | CORI1P | 0 | 0.71 | Cable | 0.0216 | 0.0662 | 0.84 | 126 | 116 | 116 | 116
CORI1J | LUIC1Q | 10.43 | 0 | OHL | 0.2443 | 2.2748 | 0.551 | 464 | 446 | 414 | 446
CORI1K | CORI1Q | 0 | 0.63 | Cable | 0.0191 | 0.0586 | 0.742 | 126 | 116 | 116 | 116
CORI1K | LUIC1R | 10.35 | 0 | OHL | 0.2425 | 2.2577 | 0.547 | 464 | 446 | 414 | 446
CORI1P | MOSS1S | 1.45 | 0 | OHL | 0.074 | 0.3248 | 0.075 | 224 | 211 | 189 | 211
CORI1Q | MOSS1T | 1.45 | 0 | OHL | 0.074 | 0.3248 | 0.075 | 224 | 211 | 189 | 211
CRAI1- | CRAI1P | 0 | 1.1 | Cable | 0.0309 | 0.0973 | 1.456 | 149 | 137 | 137 | 137
CRAI1- | CRAI1Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 145 | 131 | 116 | 131
CRAI1- | CRAI1R | 0 | 1.1 | Cable | 0.0309 | 0.0973 | 1.456 | 149 | 137 | 137 | 137
CRAI1- | FOGG1Q | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 132 | 123 | 106 | 123
CRAI1- | FOGG1R | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 132 | 123 | 106 | 123
CRAI1- | REDM1R | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146
CRAI1- | WOHI1Q | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120
CRAI1- | WOHI1R | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120
CRAI1P | KINT1P | 17.5 | 0 | OHL | 0.8925 | 3.92 | 0.903 | 241 | 230 | 210 | 230
CRAI1Q | REDM1Q | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146
CRAI1R | KINT1R | 17.5 | 0 | OHL | 0.8925 | 3.92 | 0.903 | 241 | 230 | 210 | 230
CRAR1R | INVE1J | 22.58 | 0 | OHL | 0.3613 | 3.9967 | 1.468 | 739 | 710 | 662 | 710
CRAR1R | PORA1S | 13.72 | 0 | OHL | 0.2195 | 2.4284 | 0.892 | 739 | 710 | 662 | 710
CREA1- | CREA1B | 4 | 0 | OHL | 0.2 | 0.828 | 0.224 | 203 | 193 | 176 | 193
CREA1A | CREA1B | 0 | 1.4 | Cable | 0.0149 | 0.0892 | 2.161 | 306 | 253 | 253 | 253
CREA1A | DLCH1B | 16.6 | 0 | OHL | 0.83 | 3.4362 | 0.93 | 203 | 193 | 176 | 193
CRSS1J | CRSS1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRSS1Q | PORA1R | 44.7 | 0 | OHL | 0.7152 | 7.9119 | 2.905 | 739 | 710 | 662 | 710
CRSS1R | PORA1S | 44.7 | 0 | OHL | 0.7152 | 7.9119 | 2.905 | 739 | 710 | 662 | 710
CRSS2A | CRSS2C | 0 | 1.61 | Cable | 0.0178 | 0.0531 | 4.45 | 240 | 240 | 240 | 240
CRSS2B | CRSS2D | 0 | 1.66 | Cable | 0.0178 | 0.056 | 4.57 | 240 | 240 | 240 | 240
CRSS2C | HUNN2C | 0 | 38.1 | Cable | 0.6045 | 1.1463 | 76.848 | 240 | 240 | 240 | 240
CRSS2D | HUNN2D | 0 | 38.5 | Cable | 0.6157 | 1.1674 | 78.263 | 240 | 240 | 240 | 240
CULL1Q | DEAN1Q | 9 | 0 | OHL | 0.93 | 2.12 | 0.45 | 126 | 117 | 101 | 117
DAAS2- | KNOC2K | 60.22 | 0 | OHL | 0.341 | 2.479 | 16.419 | 935 | 880 | 790 | 880
DENS1Q | TEAL1- | 8.7 | 0 | OHL | 0.3393 | 1.9053 | 0.461 | 183 | 160 | 149 | 160
DENS1R | TEAL1- | 8.7 | 0 | OHL | 0.3393 | 1.9053 | 0.461 | 183 | 160 | 149 | 160
DLCH1A | DLCH1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
DLCH1A | LAIR1- | 0 | 4.52 | Cable | 0.458 | 1.089 | 0.215 | 111 | 103 | 89 | 103
DLCH1A | LAIR1- | 0 | 4.52 | Cable | 0.458 | 1.089 | 0.215 | 111 | 103 | 89 | 103
DLCH1A | LOCB1L | 17 | 0 | OHL | 0.3992 | 3.7085 | 0.898 | 464 | 446 | 414 | 446
DLCH1B | LOCB1M | 17 | 0 | OHL | 0.3992 | 3.7085 | 0.898 | 464 | 446 | 414 | 446
DOUN2- | GORW2- | 58.1 | 0 | OHL | 0.3486 | 3.196 | 12.32 | 702 | 665 | 599 | 665
DOUN2- | THUS2J | 15.4 | 0 | OHL | 0.077 | 0.847 | 3.28 | 965 | 925 | 865 | 925
DOUN2- | THUS2K | 15.4 | 0 | OHL | 0.077 | 0.847 | 3.28 | 965 | 925 | 865 | 925
DUBE1Q | MYBS1R | 20.84 | 0 | OHL | 1.9025 | 4.8515 | 1.034 | 126 | 117 | 101 | 117
DUCC1J | ORRI1S | 10.76 | 0 | OHL | 0.2526 | 2.3466 | 0.568 | 464 | 446 | 414 | 446
DUCC1K | ORRI1T | 10.76 | 0 | OHL | 0.2526 | 2.3466 | 0.568 | 464 | 446 | 414 | 446
DUDH1Q | GLAG1Q | 0 | 1.95 | Cable | 0.0585 | 0.1151 | 2.73 | 124 | 114 | 114 | 114
DUDH1Q | MILC1R | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113
DUDH1R | GLAG1R | 0 | 1.95 | Cable | 0.0585 | 0.1151 | 2.73 | 124 | 114 | 114 | 114
DUDH1R | MILC1V | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113
DUGR1Q | EDIN1- | 9 | 0 | OHL | 1.206 | 1.997 | 0.468 | 99 | 92 | 79 | 92
DUNM1- | DUNM1T | 2.76 | 0 | OHL | 0.1391 | 0.5715 | 0.155 | 203 | 193 | 176 | 193
DUNM1- | DUNM1T | 2.76 | 0 | OHL | 0.1391 | 0.5715 | 0.155 | 203 | 193 | 176 | 193
DUNM1C | DUNM1T | 3.24 | 0 | OHL | 0.1632 | 0.6709 | 0.181 | 203 | 193 | 176 | 193
DUNM1C | DUNM1T | 3.24 | 0 | OHL | 0.1632 | 0.6709 | 0.181 | 203 | 193 | 176 | 193
DUNM1C | FARI1K | 0 | 4.07 | Cable | 0.064 | 0.28 | 6.175 | 210 | 196 | 196 | 196
DUNO1Q | WHTB1S | 18.1 | 0 | OHL | 2.5159 | 4.0363 | 0.887 | 99 | 92 | 79 | 92
DUNO1R | WHTB1T | 18.1 | 0 | OHL | 2.5159 | 4.0363 | 0.887 | 99 | 92 | 79 | 92
DYCE1J | DYCE1Q | 1.93 | 0 | OHL | 0.0978 | 0.4332 | 0.33 | 241 | 230 | 210 | 230
DYCE1Q | DYCE1T | 0 | 1.3 | Cable | 0.0455 | 0.0543 | 2.428 | 150 | 143 | 143 | 143
DYCE1R | DYCE1U | 0 | 1.3 | Cable | 0.0455 | 0.0543 | 2.428 | 150 | 143 | 143 | 143
DYCE1T | KINT1T | 10.17 | 0 | OHL | 0.5187 | 2.2781 | 0.525 | 241 | 230 | 210 | 230
DYCE1U | KINT1U | 10.17 | 0 | OHL | 0.6335 | 2.2972 | 0.519 | 145 | 131 | 116 | 131
ELGI1L | ELGI1Q | 0 | 1.8 | Cable | 0.0236 | 0.1477 | 2.956 | 251 | 252 | 252 | 252
ELGI1L | NAIR1Q | 33.9 | 0 | OHL | 1.7289 | 7.5936 | 1.763 | 241 | 230 | 210 | 230
ELGI1M | ELGI1R | 0 | 1.8 | Cable | 0.0236 | 0.1477 | 2.956 | 251 | 252 | 252 | 252
ELGI1M | NAIR1R | 33.9 | 0 | OHL | 1.7289 | 7.5936 | 1.763 | 241 | 230 | 210 | 230
ELGI1Q | KEIT1- | 27.4 | 0 | OHL | 1.3974 | 6.1376 | 1.425 | 241 | 230 | 210 | 230
ELGI1R | KEIT1- | 27.4 | 0 | OHL | 1.3974 | 6.1376 | 1.425 | 241 | 230 | 210 | 230
ERRO1A | ERRO1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 240 | 240 | 240 | 240
ERRO1A | TUMM1J | 0 | 1.33 | Cable | 0.014 | 0.098 | 2.572 | 300 | 280 | 280 | 280
ERRO1B | ERRO1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 240 | 240 | 240 | 240
ERRO1B | TUMM1K | 0 | 1.3 | Cable | 0.013 | 0.095 | 2.51 | 300 | 280 | 280 | 280
ERRO1J | ERRO1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ERRO1J | ERRO1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ERRO1J | TUMB1R | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117
ERRO1J | WHIB1A | 4.87 | 0 | OHL | 0.4973 | 1.1403 | 0.242 | 132 | 123 | 106 | 123
ERRO1K | TUMB1Q | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117
ERRO1K | WHIB1B | 4.87 | 0 | OHL | 0.4973 | 1.1403 | 0.242 | 132 | 123 | 106 | 123
ERRO1T | KIIN1- | 36.9 | 0 | OHL | 3.75 | 8.58 | 1.82 | 132 | 123 | 106 | 123
FAAR1Q | TOMT1K | 7.2 | 0 | OHL | 0.6544 | 1.6631 | 0.361 | 132 | 123 | 106 | 123
FAAR1R | TOMT1J | 7.2 | 0 | OHL | 0.6544 | 1.6631 | 0.361 | 132 | 123 | 106 | 123
FARI2J | FOYE2- | 8.4 | 0 | OHL | 0.0479 | 0.3363 | 2.358 | 935 | 880 | 790 | 880
FARI2J | KNOC2J | 14.9 | 0 | OHL | 0.0851 | 0.5967 | 4.182 | 935 | 880 | 790 | 880
FARI2K | FOYE2- | 8.4 | 0 | OHL | 0.0479 | 0.3363 | 2.358 | 935 | 880 | 790 | 880
FARI2K | KNOC2K | 14.9 | 0 | OHL | 0.0851 | 0.5967 | 4.182 | 935 | 880 | 790 | 880
FASN2- | FAUG2J | 24.384 | 1.016 | Composite | 0.069 | 1.029 | 7.259 | 1910 | 1830 | 1710 | 1830
FAUG1- | FAUG1M | 0 | 0.25 | Cable | 0.0028 | 0.0145 | 0.45 | 319 | 295 | 295 | 295
FAUG1- | FAUG1N | 0 | 0.17 | Cable | 0.0018 | 0.0097 | 0.302 | 319 | 297 | 297 | 297
FAUG1- | FAUG1P | 0 | 0.54 | Cable | 0.0088 | 0.0486 | 0.8014 | 230 | 218 | 218 | 218
FAUG1- | FAUG1Q | 0 | 1 | Cable | 0.01 | 0.012 | 0.002 | 126 | 117 | 101 | 117
FAUG1- | GLDO1G | 0 | 6 | Cable | 0.21 | 0.47 | 5.91 | 127 | 127 | 127 | 127
FAUG1J | FAUG1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FAUG1J | LAGG1Q | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 221 | 216 | 208 | 216
FAUG1K | LAGG1R | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 221 | 216 | 208 | 216
FAUG1M | LOCL1Q | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG1N | LOCL1R | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG1P | QUOI1Q | 28.2 | 0 | OHL | 1.41 | 5.8391 | 1.5759 | 241 | 230 | 210 | 230
FAUG2J | FAUG2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FAUG2K | TUMM2J | 77.2 | 0 | OHL | 0.211 | 3.128 | 22.063 | 1910 | 1830 | 1710 | 1830
FAUG4J | FAUG4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FAUG4J | MELG4J | 24.01 | 0 | OHL | 0.0311 | 0.4597 | 14.517 | 2780 | 2670 | 2480 | 2670
FERO1- | FERO1S | 5.1 | 0 | OHL | 0.7089 | 1.0659 | 0.265 | 99 | 92 | 79 | 92
FERO1S | INVE1J | 15.21 | 0 | OHL | 2.157 | 3.571 | 0.744 | 99 | 92 | 79 | 92
FERO1S | TAYN1R | 7.49 | 0 | OHL | 1.063 | 1.759 | 0.366 | 99 | 92 | 79 | 92
FETT2P | FETT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT2P | KINT2K | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
FETT2Q | FETT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT2Q | KINT2K | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
FIDD1A | FIDD1Q | 0 | 0.55 | Cable | 0.0192 | 0.02 | 1.03 | 180 | 180 | 171 | 180
FIDD1A | FOGG1R | 25 | 0 | OHL | 2.96 | 6.06 | 1.22 | 112 | 104 | 90 | 104
FIDD1B | FIDD1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FIDD1Q | FIDD1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FINL1Q | KIIN1- | 2.1 | 0 | OHL | 0.21 | 0.5 | 0.1 | 126 | 117 | 101 | 117
FOGG1Q | KINT1- | 15.6 | 0 | OHL | 1.826 | 3.742 | 0.752 | 112 | 104 | 90 | 104
FOGG1Q | TARL1Q | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123
FOGG1R | TARL1R | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123
FOYE2- | FOYE2J | 0 | 1 | Cable | 0.01 | 0.024 | 6.22 | 400 | 400 | 400 | 400
FRAS1Q | LUMB1Q | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 126 | 117 | 101 | 117
FRAS1R | LUMB1R | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 126 | 117 | 101 | 117
FWIL1Q | LOCL1Q | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1R | LOCL1R | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1R | LUND1- | 9.3 | 0 | OHL | 0.849 | 2.16 | 0.463 | 136 | 129 | 118 | 129
FYRI1J | FYRI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FYRI2J | LOCB2K | 35.93 | 0 | OHL | 0.2156 | 1.9762 | 7.617 | 702 | 665 | 599 | 665
FYRI2K | LOCB2J | 35.93 | 0 | OHL | 0.2156 | 1.9762 | 7.617 | 702 | 665 | 599 | 665
GARB1Q | SLOY1K | 14.9 | 0 | OHL | 1.45 | 3.31 | 0.7 | 132 | 123 | 106 | 123
GARB1R | SLOY1J | 14.185 | 0.715 | Composite | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
GARB1S | SLOY1J | 14.9 | 0 | OHL | 1.45 | 3.31 | 0.7 | 132 | 123 | 106 | 123
GARB1T | SLOY1K | 14.185 | 0.715 | Composite | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
GARB1T | SLOY1K | 14.185 | 0.715 | Composite | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123
GLEN1Q | LAGG1Q | 4.8 | 0 | OHL | 0.546 | 1.132 | 0.232 | 263 | 257 | 248 | 257
GLFA1- | KEIT1- | 29.6 | 0 | OHL | 3.0087 | 6.8969 | 1.466 | 126 | 117 | 101 | 117
GLKO1- | TOMT1K | 0 | 3 | Cable | 0.417 | 0.627 | 0.156 | 83 | 77 | 67 | 77
GLRB2- | TEAL2K | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030
GORW2- | STRB2- | 10.3 | 0 | OHL | 0.0618 | 0.5665 | 2.184 | 702 | 665 | 599 | 665
GRIF1S | WHIB1H | 14.17 | 0 | OHL | 1.4476 | 3.3191 | 0.704 | 132 | 123 | 106 | 123
GRIF1T | WHIB1G | 14.17 | 0 | OHL | 1.4476 | 3.3191 | 0.704 | 132 | 123 | 106 | 123
GRUB1Q | MOSS1S | 2.73 | 0 | OHL | 0.1392 | 0.6115 | 0.142 | 224 | 211 | 189 | 211
GRUB1R | MOSS1T | 2.73 | 0 | OHL | 0.1392 | 0.6115 | 0.142 | 224 | 211 | 189 | 211
INGA1Q | LOCL1Q | 2.4 | 0 | OHL | 0.2184 | 0.5592 | 0.12 | 111 | 103 | 89 | 103
INNE1J | INNE1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
INNE1J | KNOC1J | 0 | 4.57 | Cable | 0.1051 | 0.3818 | 6.326 | 155 | 150 | 150 | 150
INNE1K | INNE1L | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
INNE1L | KNOC1J | 0 | 4.48 | Cable | 0.1042 | 0.3784 | 6.27 | 155 | 150 | 150 | 150
INNE1Q | SLKB1J | 1.97 | 0 | OHL | 0.1005 | 0.4413 | 0.102 | 241 | 230 | 210 | 230
INNE1R | SLKB1K | 1.97 | 0 | OHL | 0.1005 | 0.4413 | 0.102 | 241 | 230 | 210 | 230
INRU1Q | PEHE1- | 6.8 | 0 | OHL | 0.69 | 1.57 | 0.33 | 150 | 142 | 128 | 142
INRU1Q | PEHG1Q | 1.8 | 0 | OHL | 0.0918 | 0.4032 | 0.094 | 241 | 230 | 210 | 230
INRU1Q | SFER1L | 6.1 | 0 | OHL | 0.3111 | 1.3664 | 0.317 | 241 | 230 | 210 | 230
INRU1R | PEHE1- | 6.8 | 0 | OHL | 0.69 | 1.57 | 0.33 | 126 | 117 | 101 | 117
INRU1R | PEHG1R | 1.8 | 0 | OHL | 0.0918 | 0.4032 | 0.094 | 241 | 230 | 210 | 230
INRU1R | SFER1M | 6.1 | 0 | OHL | 0.3111 | 1.3664 | 0.317 | 241 | 230 | 210 | 230
INRU1S | PEHE1- | 0 | 3 | Cable | 0.0687 | 0.2536 | 4.105 | 186 | 186 | 186 | 186
INRU1S | SFER1J | 11.3 | 0 | OHL | 0.6 | 2.379 | 0.617 | 195 | 181 | 157 | 181
INVE1J | INVE1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
INVE1K | KILC1Q | 15.1 | 0 | OHL | 2.15 | 3.55 | 0.74 | 99 | 92 | 79 | 92
INVE1K | SLOY1E | 21.3 | 0 | OHL | 1.9383 | 4.9629 | 1.065 | 126 | 117 | 101 | 117
INVR1- | INVR1A | 6.18 | 0 | OHL | 0.6294 | 1.4386 | 0.305 | 132 | 126 | 106 | 126
INVR1- | INVR1B | 6.18 | 0 | OHL | 0.6294 | 1.4386 | 0.305 | 132 | 126 | 106 | 126
INVR1- | SLOY1K | 11.22 | 0 | OHL | 1.14 | 2.614 | 0.55 | 132 | 126 | 106 | 126
INVR1- | SLOY1T | 5.82 | 0 | OHL | 0.59 | 1.356 | 0.285 | 132 | 126 | 106 | 126
INVR1A | INVR1C | 0 | 4.4 | Cable | 0.1393 | 0.4267 | 5.615 | 130 | 126 | 126 | 126
INVR1B | INVR1D | 0 | 4.4 | Cable | 0.1396 | 0.4277 | 5.627 | 130 | 126 | 126 | 126
INVR1C | KIIN1- | 23 | 0 | OHL | 2.3423 | 5.3538 | 1.134 | 132 | 126 | 106 | 126
INVR1D | KIIN1- | 23 | 0 | OHL | 2.3423 | 5.3538 | 1.134 | 132 | 126 | 106 | 126
KEIT1J | MACD1Q | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 132 | 123 | 106 | 123
KEIT1K | MACD1R | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 132 | 123 | 106 | 123
KEIT3- | KEIT3A | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KERG1- | KERG1J | 0 | 0.17 | Cable | 0.0019 | 0.0098 | 0.298 | 370 | 370 | 370 | 370
KERG1- | KERG1J | 0 | 0.17 | Cable | 0.0019 | 0.0098 | 0.298 | 370 | 370 | 370 | 370
KERG1J | KERG1K | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KERG1J | KERG1K | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KERG1J | KERG1P | 0 | 0.09 | Cable | 0.0017 | 0.0085 | 0.149 | 234 | 234 | 234 | 234
KERG1J | KERG1Q | 0 | 0.15 | Cable | 0.0027 | 0.0137 | 0.241 | 234 | 234 | 234 | 234
KERG1J | KERG1T | 0 | 0.12 | Cable | 0.0013 | 0.0069 | 0.21 | 220 | 220 | 220 | 220
KERG1K | KERG1R | 0 | 0.08 | Cable | 0.0014 | 0.0072 | 0.127 | 234 | 234 | 234 | 234
KIIN1- | LOCH1- | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 126 | 117 | 101 | 117
KIIN1- | SFIL1Q | 21.6 | 0 | OHL | 2.19 | 5.2 | 1.03 | 126 | 117 | 101 | 117
KILC1Q | NANT1Q | 4.2 | 0 | OHL | 0.59 | 1.03 | 0.19 | 99 | 92 | 79 | 92
KILC1Q | TAYN1Q | 7.6 | 0 | OHL | 1.07 | 1.78 | 0.37 | 99 | 92 | 79 | 92
KILO1- | LUND1- | 15.2 | 0 | OHL | 1.054 | 3.441 | 0.775 | 126 | 117 | 101 | 117
KINA2J | KINA2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINA2J | TUMM2K | 3 | 0 | OHL | 0.0082 | 0.1216 | 0.858 | 1910 | 1830 | 1710 | 1830
KINT1- | KINT1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINT1- | KINT1P | 0 | 0.27 | Cable | 0.01 | 0.0154 | 0.354 | 148 | 140 | 140 | 140
KINT1- | KINT1R | 0 | 0.26 | Cable | 0.01 | 0.0148 | 0.341 | 148 | 140 | 140 | 140
KINT1- | KINT1T | 0 | 0.6 | Cable | 0.0135 | 0.0343 | 0.787 | 165 | 141 | 141 | 141
KINT1- | KINT1U | 0 | 0.6 | Cable | 0.0135 | 0.0343 | 0.787 | 165 | 141 | 141 | 141
KINT2J | KINT2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINT2J | PERS2R | 28.2 | 0 | OHL | 0.14 | 1.23 | 7.42 | 1090 | 1030 | 920 | 1030
KINT2J | TEAL2A | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2K | PEHE2R | 50.4 | 0 | OHL | 0.26 | 2.19 | 13.22 | 1090 | 1030 | 920 | 1030
KINT2K | TEAL2B | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT4J | ROTI4J | 23.2 | 0 | OHL | 0.0464 | 0.4478 | 13.649 | 2000 | 1920 | 1790 | 1920
KINT4K | ROTI4K | 23.2 | 0 | OHL | 0.0464 | 0.4478 | 13.649 | 2000 | 1920 | 1790 | 1920
KNOC2J | KNOC2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KNOC2J | KNOC2L | 0 | 1.47 | Cable | 0.01 | 0.042 | 8.36 | 930 | 900 | 900 | 900
KNOC2J | KNOC2N | 0 | 0.51 | Cable | 0.01 | 0.0157 | 3.005 | 850 | 793 | 793 | 793
KNOC2K | KNOC2M | 0 | 1.29 | Cable | 0.01 | 0.037 | 7.336 | 930 | 900 | 900 | 900
KNOC2K | KNOC2P | 0 | 0.17 | Cable | 0.01 | 0.01 | 1.006 | 850 | 793 | 793 | 793
KNOC2N | TOMT2K | 18.6 | 0 | OHL | 0.093 | 1.023 | 3.962 | 810 | 765 | 685 | 765
KNOC2P | TOMT2J | 18.6 | 0 | OHL | 0.093 | 1.023 | 3.962 | 810 | 765 | 685 | 765
LAGG1R | MILW1S | 5.7 | 0 | OHL | 0.648 | 1.344 | 0.276 | 263 | 257 | 248 | 257
LOCB1J | LOCB1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOCB1J | LOCB1L | 0 | 0.83 | Cable | 0.01 | 0.0635 | 1.489 | 373 | 373 | 373 | 373
LOCB1J | LOCB1S | 0 | 0.79 | Cable | 0.022 | 0.0694 | 1.039 | 149 | 137 | 137 | 137
LOCB1J | LOCB1S | 0 | 0.785 | Cable | 0.022 | 0.0694 | 1.0394 | 149 | 137 | 137 | 137
LOCB1J | LOCB1U | 0 | 0.38 | Cable | 0.0105 | 0.0332 | 0.496 | 149 | 137 | 137 | 137
LOCB1K | LOCB1M | 0 | 0.92 | Cable | 0.01 | 0.0704 | 1.651 | 373 | 373 | 373 | 373
LOCB1K | LOCB1R | 0 | 0.73 | Cable | 0.0204 | 0.0641 | 0.96 | 149 | 137 | 137 | 137
LOCB1K | LOCB1T | 0 | 0.28 | Cable | 0.008 | 0.0252 | 0.377 | 149 | 137 | 137 | 137
LOCB1R | SHIN1- | 8.34 | 0 | OHL | 0.7614 | 1.9415 | 0.414 | 126 | 117 | 101 | 117
LOCB1U | MYBS1Q | 85.3 | 0 | OHL | 7.7872 | 19.8576 | 4.2327 | 126 | 117 | 101 | 117
LOCB2J | LOCB2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOCB2K | STRB2- | 18.9 | 0 | OHL | 0.1134 | 1.0395 | 4.007 | 702 | 665 | 599 | 665
LUIC1Q | ORRI1S | 5.4 | 0 | OHL | 0.1271 | 1.1789 | 0.285 | 464 | 446 | 414 | 446
LUIC1R | ORRI1T | 5.53 | 0 | OHL | 0.1301 | 1.2064 | 0.292 | 464 | 446 | 414 | 446
LUMB1Q | SFER1K | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117
LUMB1Q | STRI1Q | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 126 | 117 | 101 | 117
LUMB1R | SFER1J | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117
LUMB1R | STRI1R | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 126 | 117 | 101 | 117
LUNA1Q | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160
LUNA1R | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160
MELG1J | MELG1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MELG1J | STRL1- | 0 | 10 | Cable | 0.0752 | 0.806 | 18.176 | 317 | 277 | 277 | 277
MELG4J | MELG4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MELG4J | TUMM4- | 53.19 | 0 | OHL | 0.0689 | 1.0183 | 32.161 | 2780 | 2670 | 2480 | 2670
MILC1R | MILC1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MILC1R | MILC1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MILC1S | MILC1V | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MILC1S | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 183 | 160 | 149 | 160
MILC1T | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 183 | 160 | 149 | 160
MILW1Q | MILW1S | 1.3 | 0 | OHL | 0.065 | 0.2691 | 0.073 | 203 | 193 | 176 | 193
MORF4- | NEDE4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
MOSS1Q | MOSS1S | 0.21 | 0 | OHL | 0.0191 | 0.0504 | 0.01 | 132 | 123 | 106 | 123
MOSS1R | MOSS1T | 0.21 | 0 | OHL | 0.0191 | 0.0504 | 0.01 | 132 | 123 | 106 | 123
MOTA1Q | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 132 | 123 | 106 | 123
MOTA1R | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 126 | 117 | 101 | 117
MYBS1Q | SPIT1J | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117
MYBS1R | SPIT1J | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117
MYBS1S | SPIT1M | 5 | 0 | OHL | 0.1182 | 1.0607 | 0.276 | 465 | 445 | 415 | 445
MYBS1T | SPIT1K | 5 | 0 | OHL | 0.1182 | 1.0607 | 0.276 | 465 | 445 | 415 | 445
MYBS3M | MYBS3N | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
NAIR1Q | SLKB1L | 26.33 | 0 | OHL | 1.3428 | 5.8979 | 1.369 | 241 | 230 | 210 | 230
NAIR1R | SLKB1M | 26.33 | 0 | OHL | 1.3428 | 5.8979 | 1.369 | 241 | 230 | 210 | 230
NEDE4J | NEDE4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
NEDE4J | PEHE4J | 30.04 | 0 | OHL | 0.0601 | 0.5798 | 17.673 | 2000 | 1920 | 1790 | 1920
NEDE4J | ROTI4J | 17.3 | 0 | OHL | 0.0346 | 0.3339 | 10.178 | 2000 | 1920 | 1790 | 1920
NEDE4K | PEHE4K | 30.04 | 0 | OHL | 0.0601 | 0.5798 | 17.673 | 2000 | 1920 | 1790 | 1920
NEDE4K | ROTI4K | 17.3 | 0 | OHL | 0.0346 | 0.3339 | 10.178 | 2000 | 1920 | 1790 | 1920
ORRI1Q | ORRI1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
ORRI1R | ORRI1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117
PEHE2- | PEHE2Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHE2- | PEHE2S | 0 | 1 | Cable | 0.01 | 0.033 | 14.21 | 776 | 776 | 776 | 776
PEHE2- | PEHEMEC6 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHE2- | PERS2Q | 47.6 | 0 | OHL | 0.24 | 2.08 | 12.52 | 1090 | 1030 | 920 | 1030
PEHE2J | PEHE2Q | 0 | 0.47 | Cable | 0.01 | 0.01 | 5.009 | 1560 | 1560 | 1560 | 1560
PEHE2R | PEHERSV2 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHE2T | PEHERSV1 | 0 | 1 | Cable | 0.01 | 0.032 | 13.51 | 776 | 776 | 776 | 776
PEHE2U | PEHEMEC5 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313
PEHE2V | PEHEMEC3 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313
PEHE2W | PEHEMEC1 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313
PEHE4J | PEHE4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC1 | PEHEMEC2 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC1 | PEHEMEC6 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC2 | PEHEMEC3 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC2 | PEHERSV2 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC3 | PEHEMEC4 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC4 | PEHEMEC5 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC4 | PEHERSV1 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHEMEC5 | PEHEMEC6 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHERSV1 | PEHE2K | 0 | 0.47 | Cable | 0.01 | 0.01 | 5.0094 | 1560 | 1560 | 1560 | 1560
PERS1Q | PERS1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PERS1Q | WIOW1R | 0 | 3.7 | Cable | 0.084 | 0.221 | 5.104 | 155 | 129 | 129 | 129
PERS1R | WIOW1Q | 0 | 3.7 | Cable | 0.084 | 0.221 | 5.104 | 155 | 129 | 129 | 129
PERS2Q | PERS2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PORA1R | PORA1T | 6.14 | 0 | OHL | 0.8535 | 1.3692 | 0.301 | 99 | 92 | 79 | 92
PORA1S | PORA1U | 6.14 | 0 | OHL | 0.8535 | 1.3692 | 0.301 | 99 | 92 | 79 | 92
PORA1S | PORA1U | 6.14 | 0 | OHL | 0.8535 | 1.3692 | 0.301 | 99 | 92 | 79 | 92
PORA1T | PORA1U | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
QUOI1- | QUOI1Q | 1.6 | 0 | OHL | 0.12 | 0.28 | 0.05 | 150 | 142 | 128 | 142
RANN1Q | TUMB1Q | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117
RANN1R | TUMB1R | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117
ROTI4J | ROTI4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SFEE1A | SFEE1C | 0 | 0.27 | Cable | 0.0077 | 0.0304 | 0.351 | 47 | 47 | 47 | 47
SFEE1A | SFEG1Q | 0.39 | 0 | OHL | 0.0469 | 0.092 | 0.019 | 126 | 117 | 101 | 117
SFEE1A | SFER1L | 1.71 | 0 | OHL | 0.2031 | 0.398 | 0.081 | 126 | 117 | 101 | 117
SFEE1B | SFEE1D | 0 | 0.29 | Cable | 0.0084 | 0.0303 | 0.383 | 47 | 47 | 47 | 47
SFEE1B | SFEG1R | 0.39 | 0 | OHL | 0.0469 | 0.092 | 0.019 | 126 | 117 | 101 | 117
SFEE1B | SFER1M | 1.71 | 0 | OHL | 0.2031 | 0.398 | 0.081 | 126 | 117 | 101 | 117
SFEG1Q | SFEV1S | 0 | 0.4 | Cable | 0.01 | 0.034 | 0.46 | 160 | 135 | 135 | 135
SFEG1R | SFEV1T | 0 | 0.4 | Cable | 0.01 | 0.034 | 0.46 | 160 | 135 | 135 | 135
SFEM1Q | SFER1L | 1.9 | 1.1 | Composite | 0.382 | 0.557 | 1.871 | 132 | 122 | 106 | 122
SFEM1R | SFER1M | 1.9 | 1.1 | Composite | 0.382 | 0.557 | 1.871 | 132 | 122 | 106 | 122
SFER1J | SFER1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SFER1J | SFER1M | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SFER1K | SFER1L | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SFER1L | SFER1M | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100
SFEV1S | SFEV1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100
SGRX2- | TEAL2K | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 9999 | 9999 | 9999 | 9999
SLKB1J | SLKB1L | 0 | 1.5 | Cable | 0.0159 | 0.0956 | 2.316 | 306 | 253 | 253 | 253
SLKB1K | SLKB1M | 0 | 1.5 | Cable | 0.0159 | 0.0956 | 2.316 | 306 | 253 | 253 | 253
SLOY1A | SLOY1K | 0 | 0.92 | Cable | 0.0279 | 0.0856 | 1.126 | 120 | 112 | 112 | 112
SLOY1A | SLOY1M | 0.617 | 0 | OHL | 0.0561 | 0.1438 | 0.0309 | 126 | 117 | 101 | 117
SLOY1B | SLOY1K | 0 | 0.91 | Cable | 0.0277 | 0.0848 | 1.1158 | 120 | 112 | 112 | 112
SLOY1B | SLOY1L | 0.617 | 0 | OHL | 0.0561 | 0.1438 | 0.0309 | 126 | 117 | 101 | 117
SLOY1C | SLOY1J | 0 | 0.835 | Cable | 0.0254 | 0.0778 | 1.0238 | 120 | 112 | 112 | 112
SLOY1C | SLOY1N | 0.627 | 0 | OHL | 0.0571 | 0.1461 | 0.0313 | 126 | 117 | 101 | 117
SLOY1D | SLOY1J | 0 | 0.867 | Cable | 0.0264 | 0.0808 | 1.0631 | 120 | 112 | 112 | 112
SLOY1D | SLOY1P | 0.627 | 0 | OHL | 0.0571 | 0.1461 | 0.0313 | 126 | 117 | 101 | 117
SLOY1E | SLOY1J | 0 | 1.28 | Cable | 0.0389 | 0.1193 | 1.5695 | 140 | 132 | 132 | 132
SLOY1F | SLOY1K | 0 | 1.37 | Cable | 0.0417 | 0.1277 | 1.6798 | 140 | 132 | 132 | 132
SLOY1J | SLOY1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SLOY1J | SLOY1T | 5.4 | 0 | OHL | 0.547 | 1.254 | 0.266 | 132 | 123 | 106 | 123
SPIT2J | SPIT2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SPIT2J | THUS2J | 10.54 | 0 | OHL | 0.0527 | 0.5586 | 2.319 | 965 | 925 | 865 | 925
SPIT2K | SPIT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 960 | 960 | 960 | 960
SPIT2K | THUS2K | 10.54 | 0 | OHL | 0.0527 | 0.5586 | 2.319 | 965 | 925 | 865 | 925
STRW1- | STRW1A | 0 | 0.35 | Cable | 0.01 | 0.0631 | 0.48 | 200 | 178 | 178 | 178
TEAL2A | TEAL2J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TEAL2B | TEAL2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TEAL2J | TEAL2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TEAL2J | WFIB2- | 0 | 38.8 | Cable | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030
THUS1J | THUS1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TOMT1J | TOMT1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
TOMT1J | TOMT1M | 0 | 0.14 | Cable | 0.29 | 1.59 | 18.77 | 261 | 237 | 237 | 237
TOMT1K | TOMT1L | 0 | 0.13 | Cable | 0.27 | 1.5 | 17.6 | 261 | 237 | 237 | 237
TUMM2J | TUMM2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
WHIB1A | WHIB1C | 0 | 2.93 | Cable | 0.0896 | 0.2773 | 3.437 | 153 | 140 | 140 | 140
WHIB1B | WHIB1D | 0 | 2.93 | Cable | 0.0896 | 0.2773 | 3.437 | 153 | 140 | 140 | 140
WHIB1C | WHIB1E | 3.57 | 0 | OHL | 0.3644 | 0.8355 | 0.177 | 132 | 123 | 106 | 123
WHIB1D | WHIB1F | 3.57 | 0 | OHL | 0.3644 | 0.8355 | 0.177 | 132 | 123 | 106 | 123
WHIB1E | WHIB1G | 0 | 0.44 | Cable | 0.0134 | 0.0416 | 0.515 | 153 | 140 | 140 | 140
WHIB1F | WHIB1H | 0 | 0.44 | Cable | 0.0134 | 0.0416 | 0.515 | 153 | 140 | 140 | 140
WIOW1Q | WOHI1Q | 0 | 3.4 | Cable | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147
WIOW1R | WOHI1R | 0 | 3.4 | Cable | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147

## B-2-1b
B-2-1b - SPT Circuits for 2024/25
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
AREC1- | MAHI1- | 7.615 | 1.613 | Composite | 0.4363 | 1.668 | 2.5345 | 214 | 195 | 195 | 195
AREC3- | GLAP3- | 10.79 | 5.931 | Composite | 10.6428 | 36.9228 | 0.6748 | 40 | 38 | 38 | 38
AUCH2- | MAHI2- | 14.5 | 0 | OHL | 0.109 | 0.8301 | 2.9503 | 570 | 570 | 570 | 570
AUCW1- | HADH1- | 0 | 18 | Cable | 1.83 | 3.88 | 0.96 | 140 | 140 | 140 | 140
AUCW1- | MAYB1- | 0 | 0.07 | Cable | 0 | 0.009 | 0.0682 | 140 | 140 | 140 | 140
AYR-2Q | COYW2S | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 1190 | 1190 | 1190 | 1190
AYR-2R | COYW2T | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 955 | 885 | 760 | 885
BAGA1Q | BONN1- | 18.3 | 0 | OHL | 0.716 | 3.8726 | 0.9882 | 171 | 152 | 152 | 152
BAGA1Q | DRCR1Q | 4.71 | 3.39 | Composite | 0.5756 | 1.4393 | 2.8779 | 146 | 146 | 146 | 146
BAGA1R | BONN1- | 18.4 | 0 | OHL | 0.72 | 3.8943 | 0.9935 | 171 | 152 | 152 | 152
BAGA1R | DRCR1R | 4.71 | 3.38 | Composite | 0.5752 | 1.4382 | 2.8701 | 146 | 146 | 146 | 146
BAIN1Q | BONN1- | 7.02 | 0.08 | Composite | 0.2761 | 1.4801 | 0.4755 | 114 | 114 | 114 | 114
BAIN1R | BONN1- | 7.02 | 0.28 | Composite | 0.2797 | 1.4992 | 0.7089 | 114 | 114 | 114 | 114
BERW1Q | ECCL1- | 21.54 | 0.31 | Composite | 1.622 | 4.903 | 1.5274 | 132 | 123 | 106 | 123
BERW1R | ECCL1- | 21.54 | 0.27 | Composite | 1.6213 | 4.8991 | 1.4716 | 132 | 123 | 106 | 123
BLAH1- | DUNH1Q | 1.15 | 0 | OHL | 0.0294 | 0.2043 | 0.0733 | 418 | 386 | 386 | 386
BLAH1- | DUNH1R | 1.15 | 0 | OHL | 0.0294 | 0.2043 | 0.0733 | 466 | 430 | 418 | 430
BLAH1- | GLGL1Q | 12.6 | 0.375 | Composite | 0.4832 | 2.7239 | 1.1395 | 297 | 281 | 258 | 281
BLAH1- | GLGL1R | 12.6 | 0.375 | Composite | 0.4832 | 2.7239 | 1.1395 | 297 | 281 | 258 | 281
BLCW1- | NECU1Q | 36.15 | 0.9 | Composite | 1.2839 | 7.3019 | 3.5807 | 167 | 160 | 148 | 160
BLCW3- | BLKS3- | 0 | 2.801 | Cable | 0.3875 | 1.2246 | 0.6574 | 61.2 | 61.2 | 61.2 | 61.2
BLKL1- | WISH1- | 5.33 | 6.13 | Composite | 0.6542 | 1.8052 | 6.2962 | 161 | 154 | 140 | 154
BLLX1- | LINM1Q | 12.85 | 5.24 | Composite | 1.1339 | 3.1699 | 7.5599 | 132 | 123 | 106 | 123
BONB2J | DENN2- | 19.894 | 0 | OHL | 0.054 | 0.7739 | 5.8126 | 1500 | 1500 | 1500 | 1500
BONB4- | DENN4- | 19.894 | 0 | OHL | 0.0255 | 0.3658 | 12.2976 | 2570 | 2570 | 2508 | 2570
BONN1- | CUMB1Q | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135
BONN1- | CUMB1R | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135
BONN1- | DENN1- | 4.04 | 0.3 | Composite | 0.1878 | 0.4755 | 1.1901 | 240 | 234 | 202 | 234
BONN1- | STIR1S | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 238 | 219 | 191 | 219
BONN1- | STIR1T | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 238 | 219 | 191 | 219
BONN2A | DENN2- | 3.812 | 0.55 | Composite | 0.0183 | 0.1734 | 4.382 | 722 | 647 | 593 | 647
BONN2B | DENN2- | 3.812 | 0.46 | Composite | 0.0181 | 0.1709 | 3.8346 | 722 | 647 | 593 | 647
BRAP1- | ERSK1Q | 3.17 | 5.4 | Composite | 0.4479 | 1.0975 | 12.4447 | 121 | 110 | 106 | 110
BRAP1- | ERSK1R | 3.45 | 6.23 | Composite | 0.4955 | 1.1727 | 12.9637 | 102 | 79 | 79 | 79
BRAP1- | GOVA1R | 0 | 6.13 | Cable | 0.2168 | 0.45 | 11.0073 | 125 | 113 | 110 | 113
BRAP1- | PAIS1R | 4.52 | 2.19 | Composite | 0.1309 | 0.9964 | 3.6706 | 274 | 274 | 274 | 274
BROC1- | BROT1- | 0 | 0.22 | Cable | 0.0044 | 0.0183 | 0.3167 | 224 | 191 | 191 | 191
BROT1- | COAL1- | 0 | 3.2 | Cable | 0.0261 | 0.2614 | 5.959 | 293 | 293 | 293 | 293
BROT1- | LINM1Q | 5.774 | 0 | OHL | 0.1373 | 1.3023 | 0.2972 | 266 | 266 | 266 | 266
BROX1Q | CURR1A | 10.34 | 0 | OHL | 0.8009 | 2.4722 | 0.505 | 132 | 123 | 106 | 123
BROX1R | CURR1B | 10.34 | 0 | OHL | 0.8009 | 2.4722 | 0.505 | 132 | 123 | 106 | 123
BUSB2- | GIFF2Q | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240
BUSB2- | GIFF2R | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240
BUSB2- | NEIL2- | 20.24 | 0 | OHL | 0.0856 | 0.8267 | 5.625 | 1120 | 1060 | 990 | 1060
BUSB2- | STHA2A | 15.14 | 0 | OHL | 0.064 | 0.6181 | 4.2097 | 750 | 690 | 630 | 690
CAFA1Q | KEOO1- | 2.58 | 0 | OHL | 0.2337 | 0.5239 | 0.1455 | 132 | 123 | 106 | 123
CATY1Q | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.3018 | 6.1089 | 122 | 107 | 107 | 107
CATY1R | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.3018 | 6.1089 | 122 | 107 | 107 | 107
CCSS1- | COAL1- | 0 | 6.97 | Cable | 0.10961 | 0.60003 | 11.4841 | 210 | 210 | 210 | 210
CCSS1- | GAWH1Q | 0 | 2.6 | Cable | 0.0409 | 0.2238 | 4.2839 | 210 | 210 | 210 | 210
CCSS3- | CUMH3- | 0 | 2.3 | Cable | 0.3182 | 1.0055 | 0.5398 | 56 | 56 | 56 | 56
CHAP1- | DUMF1- | 26.9 | 0.18 | Composite | 1.0661 | 6.0867 | 1.6344 | 171 | 155 | 155 | 155
CHAP1- | DUMF1- | 26.9 | 0.125 | Composite | 1.065 | 6.0817 | 1.5576 | 171 | 155 | 155 | 155
CHAP1- | ECCF1J | 6.569 | 0.23 | Composite | 0.6009 | 1.515 | 0.651 | 18 | 18 | 18 | 18
CHAP1- | ECCF1K | 6.569 | 0.185 | Composite | 0.6 | 1.5109 | 0.5882 | 21 | 21 | 21 | 21
CHAP1- | GRNA1- | 12.83 | 0.35 | Composite | 1.1811 | 3.0837 | 0.9878 | 132 | 123 | 106 | 123
CHAP1- | GRNA1- | 12.83 | 0.3 | Composite | 1.1797 | 3.0784 | 0.9358 | 132 | 123 | 106 | 123
CHAP1- | HAKB1- | 14.72 | 0 | OHL | 1.535 | 3.472 | 0.754 | 132 | 123 | 106 | 123
CHAS2Q | DALM2Q | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186
CHAS2R | DALM2R | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186
CLYM2- | DALM2Q | 4.21 | 0 | OHL | 0.019 | 0.1713 | 1.1692 | 750 | 690 | 630 | 690
CLYM2- | DALM2R | 4.21 | 0.093 | Composite | 0.0193 | 0.1737 | 1.8402 | 695 | 560 | 500 | 560
CLYM2- | EERH2- | 8.75 | 0 | OHL | 0.0197 | 0.3069 | 2.8023 | 1500 | 1500 | 1500 | 1500
CLYM2- | EKIL2Q | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060
CLYM2- | EKIL2R | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060
CLYM2- | LOAN2- | 54.57 | 0 | OHL | 0.1231 | 1.9141 | 17.477 | 1500 | 1500 | 1500 | 1500
CLYN2Q | ELVA2Q | 0 | 6.2 | Cable | 0.032 | 0.174 | 26.956 | 476 | 415 | 415 | 415
CLYS2R | ELVA2R | 0 | 7.17 | Cable | 0.0445 | 0.1289 | 23.8486 | 291 | 245 | 245 | 245
CLYS3B | CLYS3X | 0 | 0.05 | Cable | 0.0084 | 0.0315 | 0.0106 | 52 | 52 | 52 | 52
COAL1A | KENN1- | 16 | 3.4 | Composite | 1.2963 | 3.7441 | 5.0291 | 140 | 124 | 124 | 124
COAL1A | LINM1R | 5.774 | 3.14 | Composite | 0.2748 | 1.6606 | 2.8754 | 134 | 123 | 123 | 123
COAL1A | MIDM1- | 0 | 13.88 | Cable | 0.3802 | 0.937 | 17.3258 | 153 | 134 | 134 | 134
COAL1B | CCSS1- | 0 | 6.97 | Cable | 0.10961 | 0.60003 | 11.4841 | 210 | 210 | 210 | 210
COAL1B | DONO1- | 0 | 4.48 | Cable | 0.08742 | 0.41139 | 6.2289 | 211 | 190 | 190 | 146
COAL1B | KYPE1- | 0 | 17.09 | Cable | 0.3286 | 1.5387 | 24.4568 | 194 | 180 | 180 | 180
COAL4- | ELVA4- | 26.71 | 0 | OHL | 0.0467 | 0.5062 | 15.9918 | 2210 | 2130 | 1980 | 2130
COAL4- | STHA4B | 21.73 | 0 | OHL | 0.038 | 0.4118 | 13.0101 | 2210 | 2130 | 1980 | 2130
COAT2Q | NEAR2Q | 3.4 | 4.9 | Composite | 0.045 | 0.2476 | 17.1398 | 176 | 156 | 156 | 156
COAT2R | NEAR2R | 3.4 | 4.9 | Composite | 0.045 | 0.2476 | 17.1398 | 176 | 156 | 156 | 156
COCK2- | KAIM2- | 18.29 | 0 | OHL | 0.0779 | 0.756 | 5.0669 | 1120 | 1060 | 990 | 1060
COCK2- | SMEA2- | 9.51 | 0 | OHL | 0.0405 | 0.3931 | 2.6346 | 1120 | 1060 | 990 | 1060
COCK4Q | ECCL4A | 65.9 | 0 | OHL | 0.135 | 1.4191 | 35.4794 | 1120 | 1060 | 990 | 1060
COCK4R | ECCL4B | 65.89 | 0 | OHL | 0.135 | 1.4189 | 35.4739 | 1120 | 1060 | 990 | 1060
COYL1- | COYT1T | 4.37 | 0.27 | Composite | 0.4027 | 1.0118 | 0.5089 | 132 | 123 | 106 | 123
COYL1- | MAYT1T | 9.14 | 0.57 | Composite | 0.8423 | 2.157 | 1.0619 | 132 | 123 | 106 | 123
COYL2- | COYW2S | 1.29 | 0.08 | Composite | 0.0057 | 0.0515 | 0.4645 | 1500 | 1500 | 1500 | 1500
COYL2- | COYW2T | 1.32 | 0 | OHL | 0.0058 | 0.0522 | 0.3778 | 1500 | 1500 | 1500 | 1500
COYL2- | MAHI2- | 49.5 | 0 | OHL | 0.3612 | 2.813 | 10.0797 | 1110 | 1090 | 1060 | 1090
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1490 | 1430 | 1320 | 1430
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1490 | 1430 | 1320 | 1430
COYT1T | KILS1- | 15.215 | 4.815 | Composite | 1.4768 | 3.99 | 7.6706 | 132 | 123 | 106 | 123
COYT1T | MAYB1- | 17.666 | 0.28 | Composite | 1.6159 | 4.1178 | 1.1779 | 132 | 123 | 106 | 123
COYW2S | KILS2- | 13.37 | 0 | OHL | 0.0588 | 0.5269 | 3.8357 | 1500 | 1500 | 1500 | 1500
COYW2T | KILS2- | 13.37 | 0 | OHL | 0.0588 | 0.5269 | 3.8357 | 1500 | 1500 | 1500 | 1500
CRDY3A | EWEH3- | 4.736 | 0.35 | Composite | 3.8899 | 14.1591 | 0.06 | 45 | 39 | 39 | 39
CRDY3B | EWEH3- | 4.775 | 0.35 | Composite | 3.9211 | 14.2732 | 0.0602 | 45 | 39 | 39 | 39
CROO1Q | NEIL1- | 12.56 | 0.22 | Composite | 0.4941 | 2.6834 | 0.984 | 229 | 211 | 183 | 211
CROO1R | NEIL1- | 12.56 | 0.23 | Composite | 0.4943 | 2.6844 | 0.9979 | 229 | 211 | 183 | 211
CRUA2Q | DALL2- | 8.16 | 0.4 | Composite | 0.0346 | 0.3435 | 4.3204 | 283 | 283 | 283 | 283
CRUA2R | DALL2- | 8.16 | 0.4 | Composite | 0.0346 | 0.3435 | 4.3204 | 283 | 283 | 283 | 283
CRYR1A | WESE1- | 0 | 3.989 | Cable | 0.0559 | 0.3473 | 5.1163 | 155 | 155 | 155 | 155
CRYR4- | FALL4- | 13.86 | 0 | OHL | 0.0184 | 0.2733 | 8.179 | 2470 | 2350 | 2150 | 2350
CRYR4- | TORN4- | 9.36 | 1.97 | Composite | 0.0144 | 0.2171 | 44.1355 | 935 | 785 | 785 | 785
CUPA1Q | LEVT1Q | 13.27 | 0 | OHL | 1.2026 | 2.9807 | 0.6715 | 143 | 142 | 128 | 142
CUPA1R | LEVT1R | 13.27 | 0 | OHL | 1.2026 | 2.9807 | 0.6715 | 143 | 142 | 128 | 142
CURR1A | GORG1Q | 1.49 | 5.8 | Composite | 0.261 | 0.9656 | 5.1127 | 111 | 100 | 92 | 100
CURR1A | LING1Q | 8.323 | 5.205 | Composite | 0.7926 | 2.2632 | 6.4813 | 132 | 123 | 106 | 123
CURR1B | GORG1R | 1.49 | 5.78 | Composite | 0.2603 | 0.9634 | 5.0953 | 111 | 100 | 92 | 100
CURR1B | LING1R | 8.323 | 5.335 | Composite | 0.7972 | 2.2773 | 6.5941 | 132 | 123 | 106 | 123
CURR2- | GRMO2- | 42.2 | 0 | OHL | 0.1916 | 1.7399 | 11.6642 | 1090 | 1030 | 925 | 1030
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.0398 | 0.3865 | 2.5902 | 1380 | 1320 | 1230 | 1320
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.0398 | 0.3865 | 2.5902 | 1380 | 1320 | 1230 | 1320
CURR2- | KINC2- | 55.76 | 0 | OHL | 0.2531 | 2.2958 | 15.4272 | 1090 | 1030 | 925 | 1030
CURR2- | SIGH2Q | 1.54 | 1.7 | Composite | 0.0174 | 0.1034 | 6.0397 | 180 | 180 | 180 | 180
CURR2- | SIGH2R | 1.54 | 1.67 | Composite | 0.0172 | 0.1027 | 5.9404 | 180 | 180 | 180 | 180
DALL2- | INVR2- | 22.55 | 0 | OHL | 0.0954 | 0.921 | 6.2707 | 570 | 570 | 570 | 570
DALL2- | WIYH2- | 78.15 | 0 | OHL | 0.3305 | 3.192 | 21.732 | 570 | 570 | 570 | 570
DALM1- | SANX1Q | 0 | 5.16 | Cable | 0.1457 | 0.1955 | 6.7791 | 181 | 164 | 164 | 164
DALM1- | SANX1R | 0 | 5.78 | Cable | 0.1632 | 0.2189 | 7.5936 | 181 | 164 | 164 | 164
DENN2- | LAMB2- | 31.991 | 0 | OHL | 0.1442 | 1.3015 | 8.8844 | 955 | 885 | 760 | 885
DENN2- | LAMB2T | 31.991 | 0 | OHL | 0.1442 | 1.3015 | 8.8844 | 955 | 880 | 760 | 885
DENN2- | LOAN2- | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DENN2- | LOAN2T | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DESA1Q | NECU1- | 6.4 | 4.3 | Composite | 0.5652 | 1.7993 | 6.3388 | 167 | 160 | 147 | 160
DEVM1- | ERSK1Q | 16.5 | 0 | OHL | 1.767 | 3.937 | 0.893 | 132 | 123 | 106 | 123
DEVM1- | SPAV1Q | 7.63 | 0 | OHL | 0.6915 | 1.7146 | 0.386 | 107 | 107 | 101 | 107
DEVM1- | SPAV1R | 7.51 | 0 | OHL | 0.6806 | 1.6869 | 0.38 | 107 | 107 | 101 | 107
DEVM4- | NEIL4R | 28.474 | 0 | OHL | 0.058184 | 0.59672 | 15.8233 | 2000 | 1920 | 1790 | 1920
DEVM4- | WIYH4Q | 28.908 | 0 | OHL | 0.058632 | 0.58884 | 16.3967 | 1120 | 1060 | 990 | 1060
DEVO1- | STIR1T | 5.8 | 5.816 | Composite | 0.3236 | 1.8724 | 7.2413 | 164 | 130 | 130 | 130
DEVO1- | WFIE1B | 31.8 | 0 | OHL | 2.8944 | 7.5329 | 1.5454 | 162 | 154 | 141 | 154
DEWP2Q | WHHO2Q | 0 | 2.48 | Cable | 0.0159 | 0.0559 | 7.7539 | 276 | 240 | 240 | 240
DEWP2R | WHHO2R | 0 | 2.55 | Cable | 0.0164 | 0.0575 | 7.9728 | 276 | 240 | 240 | 240
DONO3A | HAGH3- | 0 | 7.5 | Cable | 1.0376 | 3.279 | 1.7603 | 40 | 38 | 38 | 38
DRUM2Q | WIYH2- | 2.46 | 0.29 | Composite | 0.0113 | 0.1081 | 3.8932 | 120 | 120 | 120 | 120
DRUM2R | WIYH2- | 2.46 | 0 | OHL | 0.0111 | 0.1001 | 0.6832 | 120 | 120 | 120 | 120
DUMF1- | TONG1Q | 43.58 | 0 | OHL | 4.447 | 10.71 | 2.18 | 132 | 123 | 106 | 123
DUNB1Q | DUNB1S | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 232 | 198 | 188 | 198
DUNB1Q | INWI1Q | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 115 | 104 | 104 | 104
DUNB1R | DUNB1T | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 232 | 198 | 188 | 198
DUNB1R | INWI1R | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 115 | 104 | 104 | 104
DUNE1- | GALA1- | 23.64 | 0 | OHL | 2.1456 | 5.5767 | 1.1477 | 164 | 151 | 127 | 151
DUNE1- | SMEA1- | 17.838 | 0.621 | Composite | 1.098 | 3.6602 | 1.7709 | 154 | 131 | 127 | 131
DUNE3- | KEIH3- | 0 | 4.746 | Cable | 5.1628 | 4.7962 | 0.3798 | 21 | 20 | 20 | 20
DUNE3- | POGB3- | 0 | 3.809 | Cable | 4.4533 | 3.8497 | 0.3048 | 21 | 20 | 20 | 20
DUNE3- | TODD3- | 0 | 6.07 | Cable | 2.245 | 5.682 | 0.73 | 42 | 42 | 42 | 42
DUNF1Q | INKE1Q | 7.58 | 0.09 | Composite | 0.6938 | 1.7769 | 0.5496 | 132 | 122 | 106 | 122
DUNF1Q | MOSM1A | 10.46 | 0 | OHL | 0.5557 | 2.2694 | 0.5549 | 215 | 215 | 198 | 215
DUNF1R | INKE1R | 7.58 | 0.09 | Composite | 0.6938 | 1.7769 | 0.5496 | 132 | 122 | 106 | 122
DUNF1R | MOSM1B | 10.46 | 0 | OHL | 0.5557 | 2.2694 | 0.5549 | 215 | 215 | 198 | 215
DUNH1Q | DUNH1S | 0 | 0.336 | Cable | 0.0168 | 0.037 | 0.2759 | 159 | 147 | 147 | 147
DUNH1Q | NECU1- | 13.65 | 0 | OHL | 0.3486 | 2.4244 | 0.8703 | 484 | 458 | 418 | 458
DUNH1R | DUNH1T | 0 | 0.372 | Cable | 0.0186 | 0.0409 | 0.3054 | 159 | 147 | 147 | 147
DUNH1R | NECU1- | 13.65 | 0 | OHL | 0.3486 | 2.4244 | 0.8703 | 484 | 458 | 418 | 458
EAST1Q | GLLE1- | 1.69 | 0 | OHL | 0.1536 | 0.3503 | 0.094 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 31.37 | 0 | OHL | 2.8482 | 7.3807 | 1.5285 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 30.94 | 0 | OHL | 2.8144 | 7.1441 | 1.5364 | 132 | 123 | 106 | 123
ECCL4A | ECCL4C | 0 | 0 | Series Capacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771
ECCL4A | TORN4- | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
ECCL4B | ECCL4D | 0 | 0 | Series Capacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771
ECCL4B | TORN4- | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
ECCL4C | STWB4Q | 7.39 | 0 | OHL | 0.0063 | 0.1209 | 5.1175 | 2770 | 2770 | 2660 | 2770
ECCL4D | STWB4R | 7.39 | 0 | OHL | 0.0063 | 0.1209 | 5.1175 | 2770 | 2770 | 2660 | 2770
EERH2- | LOAN2- | 45.82 | 0 | OHL | 0.1034 | 1.6072 | 14.6747 | 1500 | 1500 | 1500 | 1500
EERH2- | NEAR2Q | 15.34 | 0 | OHL | 0.077 | 0.632 | 4.283 | 950 | 885 | 760 | 885
EKIL2Q | EKIL2S | 5.17 | 0 | OHL | 0.0138 | 0.1834 | 1.6594 | 865 | 825 | 750 | 825
EKIL2Q | STHA2A | 4.79 | 0 | OHL | 0.0216 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965
EKIL2R | EKIL2T | 5.17 | 0.108 | Composite | 0.0141 | 0.186 | 2.1213 | 480 | 405 | 405 | 405
EKIL2R | STHA2B | 4.79 | 0 | OHL | 0.0216 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965
EKIL3A | EKIL3B | 0 | 0 | Series Reactor | 0.5744 | 108.498 | 0 | 30 | 30 | 30 | 30
EKIS2- | NEIL2- | 29.58 | 0 | OHL | 0.1251 | 1.2082 | 8.2207 | 1110 | 1030 | 885 | 1030
EKIS2- | STHA2B | 5.8 | 0 | OHL | 0.0245 | 0.2366 | 1.614 | 1050 | 965 | 880 | 965
EKIS2- | WLEE2- | 0 | 6 | Cable | 0.034 | 0.101 | 25.635 | 378 | 378 | 378 | 378
EKIS2- | WLEX2- | 0 | 16.68 | Cable | 0.088 | 0.346 | 70.948 | 340 | 340 | 340 | 340
ELDE1Q | JOHN1Q | 0 | 4.37 | Cable | 0.1229 | 0.4314 | 4.832 | 149 | 149 | 149 | 149
ELDE1Q | NEIL1- | 3.82 | 0.18 | Composite | 0.1517 | 0.8271 | 0.4569 | 229 | 211 | 183 | 211
ELDE1R | JOHN1R | 0 | 4.37 | Cable | 0.1229 | 0.4314 | 4.832 | 149 | 149 | 149 | 149
ELDE1R | NEIL1- | 3.82 | 0.23 | Composite | 0.1523 | 0.8319 | 0.5267 | 229 | 211 | 183 | 211
ELVA3A | PRST3A | 1.01 | 0 | OHL | 0.8089 | 2.9543 | 0.004 | 49 | 45 | 39 | 45
ELVA4- | GRNA4C | 65.54 | 0 | OHL | 0.1155 | 1.2673 | 38.8356 | 2210 | 2130 | 1980 | 2130
ELVA4- | MOFF4- | 23.5 | 0 | OHL | 0.0414 | 0.4544 | 13.9258 | 2210 | 2130 | 1980 | 2130
ELVA4- | STHA4A | 48.56 | 0 | OHL | 0.085 | 0.9204 | 29.0717 | 2210 | 2130 | 1980 | 2130
ENHI1- | NECU1C | 0 | 4.4 | Cable | 0.1242 | 0.2856 | 5.7805 | 134 | 123 | 123 | 123
ESST1- | PART1Q | 0 | 6.9 | Cable | 0.137 | 0.641 | 9.143 | 210 | 200 | 190 | 200
ESST1- | WIYH1- | 0 | 3.59 | Cable | 0.0711 | 0.3255 | 5.0111 | 233 | 200 | 200 | 200
ESST1Q | PART1R | 0 | 6.84 | Cable | 0.136 | 0.635 | 9.062 | 203 | 190 | 190 | 190
ESST1Q | WIYH1- | 0 | 3.16 | Cable | 0.178 | 0.334 | 7.691 | 203 | 190 | 190 | 190
EWEH1Q | GRNA1- | 15.7 | 0.12 | Composite | 1.1828 | 3.4623 | 0.9844 | 131 | 131 | 131 | 131
FALL4- | SMEA4R | 31.1 | 0 | OHL | 0.0414 | 0.6133 | 18.3526 | 2520 | 2400 | 2190 | 2400
FINN1Q | PART1Q | 0 | 2.813 | Cable | 0.0563 | 0.1582 | 4.0035 | 171 | 152 | 152 | 152
FINN1R | PART1R | 0 | 2.845 | Cable | 0.057 | 0.16 | 4.0491 | 171 | 152 | 152 | 152
GALA1- | HAWI1B | 23.55 | 0 | OHL | 1.211 | 2.684 | 7.57 | 132 | 122 | 106 | 122
GARB1Q | HELE1Q | 15.313 | 0 | OHL | 1.3875 | 3.4126 | 0.7803 | 132 | 123 | 106 | 123
GARB1R | STLE1Q | 26.909 | 0 | OHL | 2.4383 | 5.997 | 1.3713 | 132 | 123 | 106 | 123
GARB1S | GARE1S | 5.03 | 0 | OHL | 0.4558 | 1.1211 | 0.2564 | 132 | 123 | 106 | 123
GARB1T | GARE1T | 5.061 | 0 | OHL | 0.4586 | 1.1279 | 0.2579 | 132 | 123 | 106 | 123
GARE1S | WHTL1S | 1.68 | 0 | OHL | 0.2125 | 0.3513 | 0.0919 | 100 | 94 | 80 | 94
GARE1S | WIYH1- | 35.082 | 0.33 | Composite | 3.1938 | 7.8537 | 2.4208 | 109 | 105 | 101 | 105
GARE1T | WHTL1T | 1.67 | 0 | OHL | 0.2112 | 0.3492 | 0.0913 | 100 | 94 | 80 | 94
GARE1T | WIYH1- | 34.74 | 0.162 | Composite | 3.1552 | 7.7595 | 2.0813 | 109 | 105 | 101 | 105
GAWH3- | HAHA3- | 0 | 5 | Cable | 1.6871 | 4.5198 | 0.5324 | 36 | 34 | 34 | 34
GLGL1Q | SAKN1- | 0 | 9 | Cable | 0.2541 | 0.5842 | 11.0847 | 166 | 166 | 166 | 166
GLGL3- | SNQR3- | 0 | 2.3 | Cable | 0.6364 | 2.0111 | 0.2699 | 30 | 30 | 30 | 30
GLGL3- | WHLL3- | 0 | 1.2 | Cable | 0.332 | 1.5811 | 0.1408 | 30 | 30 | 30 | 30
GLLE1- | KEOO1- | 7.68 | 0 | OHL | 0.6969 | 1.6787 | 0.405 | 132 | 123 | 106 | 123
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.7434 | 7.134 | 1.4605 | 125 | 113 | 102 | 113
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.7434 | 7.134 | 1.4605 | 125 | 113 | 102 | 113
GLLE1- | TONG1- | 33.1 | 0 | OHL | 3.39 | 7.678 | 1.662 | 132 | 123 | 106 | 123
GLLU1Q | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49
GLLU1R | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 57 | 57 | 57 | 57
GLNI1- | MOSM1A | 1.41 | 0.09 | Composite | 0.0651 | 0.2344 | 0.3797 | 265 | 246 | 212 | 246
GLNI1- | MOSM1B | 1.41 | 0.11 | Composite | 0.0654 | 0.2362 | 0.4421 | 265 | 246 | 212 | 246
GLNI1- | REDH1- | 10.547 | 0 | OHL | 0.9555 | 2.3056 | 0.552 | 161 | 154 | 141 | 154
GLNI1- | WFIE1B | 7.11 | 0 | OHL | 0.5359 | 1.6524 | 0.3546 | 264 | 246 | 212 | 246
GLRB2- | GLRO2- | 14.68 | 0 | OHL | 0.0664 | 0.6181 | 3.956 | 1090 | 1030 | 925 | 1030
GLRO2- | WFIE2- | 12.08 | 0 | OHL | 0.0547 | 0.5102 | 3.2488 | 1090 | 1030 | 925 | 1030
GORG1Q | TELR1Q | 0 | 3.74 | Cable | 0.395 | 0.271 | 6.4 | 80 | 75 | 70 | 75
GORG1R | TELR1R | 0 | 3.72 | Cable | 0.395 | 0.271 | 6.4 | 80 | 75 | 70 | 75
GOVA1Q | HAGR1Q | 0 | 4.04 | Cable | 0.2097 | 0.252 | 6.0812 | 70 | 64 | 64 | 64
GOVA1Q | PAIS1Q | 4.52 | 4.03 | Composite | 0.2635 | 1.0894 | 8.2673 | 125 | 113 | 110 | 113
GOVA1R | HAGR1R | 0 | 4.11 | Cable | 0.187 | 0.225 | 3.587 | 69 | 64 | 64 | 64
GRMO2- | KINC2- | 14.96 | 0 | OHL | 0.068 | 0.6184 | 4.1277 | 1050 | 965 | 880 | 965
GRMO3A | GRMO3C | 0 | 1 | Cable | 0.017 | 0.047 | 0.066 | 1000 | 1000 | 1000 | 1000
GRMO3A | GRMO3C | 0 | 1 | Cable | 0.012 | 0.035 | 0.049 | 1000 | 1000 | 1000 | 1000
GRNA1- | HAWI1- | 55.35 | 0 | OHL | 4.2501 | 13.0393 | 2.7334 | 132 | 123 | 106 | 123
GRNA1- | JUNV1- | 4.74 | 0 | OHL | 0.4329 | 1.1257 | 0.2305 | 132 | 123 | 106 | 123
GRNA4- | GRNA4C | 0 | 0 | Series Capacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771
GRNA4- | HAKB4B | 1.97 | 0 | OHL | 0.0035 | 0.0381 | 1.1674 | 2210 | 2130 | 1980 | 2130
HAKB4- | MOFF4C | 43.79 | 0 | OHL | 0.0772 | 0.8467 | 25.9494 | 2210 | 2130 | 1980 | 2130
HARE1- | MOFF1- | 0 | 15.33 | Cable | 0.304 | 0.8622 | 21.563 | 184 | 184 | 184 | 184
HARR3- | KYPE3A | 0 | 0.5 | Cable | 0.0692 | 0.2186 | 0.1174 | 40 | 38 | 38 | 38
HAWI1- | JUNV1- | 50.34 | 0 | OHL | 3.7968 | 11.8507 | 2.4895 | 132 | 123 | 106 | 123
HELE1R | WIYH1- | 24.799 | 0.182 | Composite | 2.2553 | 5.5463 | 1.6125 | 109 | 105 | 101 | 105
HUCS4- | HUNE4- | 0 | 0.665 | Cable | 0.0003 | 0.0089 | 7.3943 | 1444 | 1444 | 1444 | 1444
HUCS4- | HUNE4- | 0 | 0.675 | Cable | 0.0003 | 0.009 | 7.5055 | 1444 | 1444 | 1444 | 1444
HUER1- | HUNF1Q | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 146 | 146 | 146
HUER1- | HUNF1R | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 146 | 146 | 146
HUER1- | JUNA1T | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 175 | 175 | 175
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.0001 | 0.001 | 0.7263 | 2770 | 2770 | 2770 | 2770
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.0001 | 0.001 | 0.7263 | 2770 | 2770 | 2770 | 2770
HUER4- | KILS4- | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930
HUER4- | KILS4T | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930
HUNE4- | HUNN4A | 0 | 0.259 | Cable | 0.0008 | 0.0027 | 1.7445 | 607 | 607 | 607 | 607
HUNE4- | HUNN4B | 0 | 0.177 | Cable | 0.0005 | 0.0019 | 1.1922 | 607 | 607 | 607 | 607
HUNE4- | NEIL4Q | 35.43 | 0 | OHL | 0.0706 | 0.7289 | 20.0655 | 1390 | 1280 | 1110 | 1280
HUNE4- | NEIL4R | 35.43 | 0 | OHL | 0.0706 | 0.7289 | 20.0655 | 1390 | 1280 | 1110 | 1280
HUNF1Q | KILW1R | 12.85 | 3.06 | Composite | 0.6044 | 3.1854 | 6.863 | 146 | 146 | 145 | 146
HUNF1R | SACO1R | 8.572 | 3.04 | Composite | 0.4215 | 2.2374 | 6.6019 | 146 | 146 | 145 | 146
HUNN2A | HUNN2C | 0 | 3.356 | Cable | 0.0212 | 0.1068 | 11.7957 | 240 | 240 | 240 | 240
HUNN2B | HUNN2D | 0 | 3.413 | Cable | 0.0216 | 0.1087 | 11.9781 | 240 | 240 | 240 | 240
INVB2A | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000
INVB2B | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000
INVR2- | WIYH2- | 55.6 | 0 | OHL | 0.2351 | 2.2709 | 15.4613 | 570 | 570 | 570 | 570
INWI1Q | TORN1- | 0 | 1.15 | Cable | 0.038 | 0.061 | 2.365 | 115 | 104 | 104 | 104
INWI1R | TORN1- | 0 | 1.12 | Cable | 0.038 | 0.061 | 2.365 | 115 | 104 | 104 | 104
JUNA1T | KILW1Q | 12.418 | 0 | OHL | 0.4909 | 2.779 | 0.643 | 146 | 146 | 146 | 146
JUNA1T | SACO1Q | 8.14 | 0 | OHL | 0.3086 | 1.8332 | 0.4224 | 151 | 151 | 151 | 151
JUNB1- | JUNV1- | 1 | 0 | OHL | 6e-06 | 5.7e-05 | 0 | 1000 | 1000 | 1000 | 1000
KAIM2- | SMEA2- | 8.78 | 0 | OHL | 0.0374 | 0.3629 | 2.4323 | 1190 | 1190 | 1190 | 1190
KAIM2- | WHHO2Q | 0 | 6.455 | Cable | 0.0415 | 0.1456 | 20.1821 | 276 | 240 | 240 | 240
KAIM2- | WHHO2R | 0 | 6.297 | Cable | 0.0405 | 0.1421 | 19.6881 | 276 | 240 | 240 | 240
KAIM3- | KAIM3A | 0 | 0 | Series Reactor | 0.0625 | 13.5546 | 0 | 120 | 120 | 120 | 120
KAIM3- | KAIM3B | 0 | 0 | Series Reactor | 0.0624 | 13.55 | 0 | 120 | 120 | 120 | 120
KEOO1- | NECU1R | 26.51 | 0 | OHL | 0.8345 | 5.2149 | 1.561 | 132 | 123 | 106 | 123
KIER1Q | WIYH1- | 2.089 | 4.183 | Composite | 0.3881 | 0.9293 | 7.6166 | 100 | 80 | 60 | 80
KIER1R | WIYH1- | 2.089 | 4.095 | Composite | 0.3833 | 0.9197 | 7.4586 | 100 | 80 | 60 | 80
KILB1Q | WIYH1- | 0 | 3.38 | Cable | 0.098 | 0.209 | 4.333 | 139 | 126 | 113 | 126
KILB1R | WIYH1- | 0 | 3.29 | Cable | 0.115 | 0.199 | 8.02 | 139 | 126 | 113 | 126
KILG2- | MAHI2- | 0 | 14 | Cable | 0.0719 | 0.2998 | 53.9497 | 352 | 290 | 290 | 290
KILS1- | MEAD1- | 12.57 | 0 | OHL | 0.874 | 2.581 | 2.166 | 162 | 154 | 141 | 154
KILS2- | KILT2Q | 3.56 | 0.29 | Composite | 0.0175 | 0.154 | 2.0858 | 204 | 177 | 177 | 177
KILS2- | KILT2R | 3.56 | 0.33 | Composite | 0.0178 | 0.1548 | 2.24 | 204 | 177 | 177 | 177
KILS4- | STHA4A | 34.948 | 0 | OHL | 0.0712 | 0.7173 | 19.8386 | 2000 | 1920 | 1790 | 1920
KILS4T | STHA4B | 34.948 | 0 | OHL | 0.0712 | 0.7173 | 19.8386 | 2000 | 1920 | 1790 | 1920
KILW1Q | MEAD1- | 13.8 | 0 | OHL | 0.7331 | 2.9941 | 0.732 | 146 | 146 | 138 | 146
KILW1R | MEAD1- | 13.8 | 0 | OHL | 0.7331 | 2.9941 | 0.732 | 146 | 146 | 138 | 146
KINB2J | KINC2- | 10.71 | 0 | OHL | 0.0482 | 0.4368 | 2.969 | 1090 | 1030 | 925 | 1030
KINB2K | KINC2- | 10.325 | 0.385 | Composite | 0.0467 | 0.4255 | 6.9142 | 1090 | 1030 | 925 | 1030
KINC2- | LOAN2Q | 4.28 | 0 | OHL | 0.0186 | 0.1855 | 1.1454 | 765 | 620 | 620 | 620
KINC2- | LOAN2R | 4.28 | 0 | OHL | 0.0186 | 0.1855 | 1.1454 | 765 | 620 | 620 | 620
LAMB2- | LAMB2T | 0.001 | 0 | OHL | 0 | 0 | 0 | 1120 | 1060 | 990 | 1060
LAMB2- | PORD2Q | 3.94 | 0 | OHL | 0.0182 | 0.1701 | 1.0531 | 955 | 885 | 760 | 885
LAMB2- | PORD2R | 3.94 | 0.177 | Composite | 0.0192 | 0.1721 | 2.1551 | 300 | 300 | 300 | 300
LAMB2- | WIYH2- | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 955 | 955 | 880 | 955
LAMB2T | WIYH2- | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1120 | 1060 | 990 | 1060
LEVE1Q | LEVT1Q | 2.16 | 0 | OHL | 0.1957 | 0.4852 | 0.1093 | 143 | 142 | 128 | 142
LEVE1R | LEVT1R | 2.26 | 0 | OHL | 0.2048 | 0.5083 | 0.1143 | 143 | 142 | 128 | 142
LEVT1Q | REDH1- | 8.61 | 0 | OHL | 0.7803 | 1.9339 | 0.4357 | 143 | 142 | 128 | 142
LEVT1R | WFIE1B | 18.707 | 0 | OHL | 1.588 | 4.18 | 0.9537 | 143 | 142 | 128 | 142
LOAN2- | LOAN2Q | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | LOAN2R | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | LOAN2T | 0.001 | 0 | OHL | 0 | 0 | 0 | 1500 | 1500 | 1500 | 1500
LOAN2- | MOSM2- | 31.496 | 0.174 | Composite | 0.1429 | 1.3311 | 11.6006 | 1090 | 1030 | 925 | 1030
LOAN2T | WFIE2- | 29.209 | 0 | OHL | 0.1316 | 1.2106 | 7.9335 | 1090 | 1030 | 925 | 1030
MAHI3- | TRLO3- | 8.722 | 5.5 | Composite | 12.1114 | 32.1139 | 0.6017 | 40 | 30 | 30 | 30
MAYB1- | MAYT1T | 12.59 | 0.31 | Composite | 1.1567 | 3.0101 | 0.9444 | 132 | 123 | 106 | 123
MEAD1- | MEAD1Q | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100
MEAD1- | MEAD1R | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100
MINN3- | MOFF3A | 0 | 12.34 | Cable | 4.1636 | 17.1281 | 1.314 | 31 | 29 | 29 | 29
MOFF4- | MOFF4C | 0 | 0 | Series Capacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771
MOSH1Q | MOSM1A | 0 | 1.03 | Cable | 0.048 | 0.063 | 2.012 | 132 | 123 | 106 | 123
MOSH1R | MOSM1B | 0 | 0.96 | Cable | 0.044 | 0.057 | 1.826 | 132 | 123 | 106 | 123
MOSM2- | WFIE2- | 8.243 | 0 | OHL | 0.0378 | 0.3641 | 2.1507 | 1090 | 1030 | 925 | 1030
NEAR2Q | WISH2- | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 955 | 885 | 760 | 885
NEAR2R | WISH2- | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 285 | 285 | 285 | 285
NECU1- | SOKY1- | 0 | 4.2 | Cable | 0.0458 | 0.2435 | 7.265 | 242 | 223 | 192 | 223
NEIL1- | NEIL1C | 0 | 0.32 | Cable | 0 | 0.0126 | 0 | 416 | 389 | 389 | 389
NEIL1- | PAIS1Q | 8.29 | 0.29 | Composite | 0.1643 | 1.4877 | 1.704 | 268 | 268 | 268 | 268
NEIL1- | PAIS1R | 8.31 | 0.31 | Composite | 0.1648 | 1.493 | 1.7861 | 268 | 268 | 268 | 268
NEIL2- | NEIL2C | 0 | 0.2 | Cable | 0.0007 | 0.003 | 1.492 | 1140 | 945 | 945 | 945
NEIL2- | NEIL2D | 0 | 0.2 | Cable | 0.0002 | 0.0028 | 2.4328 | 500 | 500 | 500 | 500
NEIL2- | WIYH2R | 25.453 | 0 | OHL | 0.1093 | 1.0873 | 6.9047 | 1120 | 1060 | 990 | 1060
NETH3- | WISH3T | 0 | 0.98 | Cable | 0.1354 | 0.45 | 0.2253 | 37 | 36 | 36 | 36
NOKY1- | NECU1- | 0 | 1.3 | Cable | 0.0084 | 0.0773 | 2.2771 | 261 | 261 | 261 | 261
PAIS1Q | PAIS1S | 1.87 | 0 | OHL | 0.0366 | 0.3302 | 0.1197 | 460 | 425 | 365 | 425
PAIS1R | PAIS1T | 1.87 | 0 | OHL | 0.0366 | 0.3302 | 0.1197 | 460 | 425 | 365 | 425
POOB2Q | SHRU2Q | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270
POOB2Q | SMEA2- | 7.79 | 0.19 | Composite | 0.0335 | 0.3227 | 2.9788 | 360 | 300 | 240 | 300
POOB2R | SHRU2R | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270
POOB2R | SMEA2- | 7.79 | 0.19 | Composite | 0.0335 | 0.3227 | 2.9788 | 360 | 300 | 240 | 300
PORD2Q | WGEO2Q | 0 | 1.83 | Cable | 0.017 | 0.056 | 12.236 | 305 | 198 | 198 | 198
PORD2R | WGEO2R | 0 | 2.15 | Cable | 0.014 | 0.049 | 10.691 | 305 | 198 | 198 | 198
RAVE3S | WISH3S | 0 | 4.1 | Cable | 0.9601 | 1.9766 | 0.01 | 32 | 32 | 32 | 32
RAVE3T | WISH3T | 0 | 4.1 | Cable | 0.9601 | 1.9766 | 0.01 | 32 | 32 | 32 | 32
REDH1- | WFIE1A | 10.097 | 0 | OHL | 0.8077 | 2.2461 | 0.5179 | 157 | 152 | 141 | 152
SMEA4Q | STHA4B | 73.37 | 0 | OHL | 0.1593 | 1.4873 | 41.7375 | 900 | 760 | 760 | 760
SMEA4Q | TORN4- | 54.32 | 1.94 | Composite | 0.0742 | 1.1033 | 70.0791 | 900 | 760 | 760 | 760
SMEA4R | WISH4- | 61.77 | 0 | OHL | 0.1344 | 1.2615 | 34.9418 | 1390 | 1280 | 1110 | 1280
STHA4A | WISH4- | 11.6 | 0 | OHL | 0.0233 | 0.2267 | 6.8043 | 2000 | 1920 | 1790 | 1920
STIR1S | WFIE1A | 37.6 | 5.816 | Composite | 3.218 | 9.4053 | 8.7867 | 162 | 154 | 141 | 154
STLE1R | WIYH1- | 12.892 | 0.291 | Composite | 1.1813 | 2.9041 | 1.2141 | 109 | 105 | 101 | 105
WFIB2- | WFIE2- | 22.48 | 0 | OHL | 0.1014 | 0.933 | 6.1144 | 1090 | 1030 | 925 | 1030
WHTB1S | WHTL1S | 2.05 | 0 | OHL | 0.2593 | 0.4287 | 0.1121 | 100 | 94 | 80 | 94
WHTB1T | WHTL1T | 2.05 | 0 | OHL | 0.2593 | 0.4287 | 0.1121 | 100 | 94 | 80 | 94
WIYH2- | WIYH2R | 0 | 0 | Series Reactor | 0.005 | 1.5 | 0 | 1000 | 1000 | 1000 | 1000

## B-2-1c
B-2-1c - NGET Circuits for 2024/25
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
ABHA4A | EXET41 | 48.785 | 0 | OHL | 0.0778 | 0.9831 | 27.9792 | 2078 | 2078 | 2078 | 2078
ABHA4A | LAGA41 | 26.121 | 0 | OHL | 0.0417 | 0.5027 | 15.6941 | 2423 | 2327 | 2168 | 2327
ABHA4B | EXET41 | 49.051 | 0 | OHL | 0.0783 | 0.9885 | 28.1313 | 2423 | 2327 | 2168 | 2327
ABHA4B | LAGA41 | 26.121 | 0 | OHL | 0.0417 | 0.5027 | 15.6941 | 2423 | 2327 | 2168 | 2327
ABTH21 | COWT2A | 13.318 | 0 | OHL | 0.0503 | 0.5449 | 3.758 | 932 | 879 | 790 | 879
ABTH21 | PYLE21 | 35.388 | 0 | OHL | 0.1819 | 1.4523 | 9.9528 | 932 | 879 | 790 | 879
ABTH21 | TREM21 | 46.451 | 0 | OHL | 0.2267 | 2.1393 | 11.8321 | 682 | 629 | 538 | 629
ABTH21 | UPPB21 | 26.996 | 0 | OHL | 0.1234 | 1.1426 | 7.3237 | 955 | 882 | 762 | 882
ABTH21 | UPPB22 | 27.035 | 0.547 | Composite | 0.1245 | 1.1595 | 13.2801 | 772 | 772 | 595 | 595
ALDW21 | BRIN21 | 17.961 | 0 | OHL | 0.1442 | 0.7628 | 4.8487 | 626 | 591 | 535 | 591
ALDW21 | WMEL21 | 8.96 | 0 | OHL | 0.0409 | 0.3891 | 2.3695 | 955 | 882 | 762 | 882
ALVE4A | INDQ41 | 97.176 | 0 | OHL | 0.2121 | 1.9367 | 56.1415 | 1389 | 1284 | 1108 | 1284
ALVE4A | TAUN41 | 73.293 | 0 | OHL | 0.117 | 1.477 | 42.0344 | 1389 | 1284 | 1108 | 1284
ALVE4B | INDQ41 | 97.294 | 0 | OHL | 0.2123 | 1.9391 | 56.209 | 1389 | 1284 | 1108 | 1284
ALVE4B | TAUN42 | 73.298 | 0 | OHL | 0.117 | 1.4771 | 42.0372 | 1389 | 1284 | 1108 | 1284
AMEM4A | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2009 | 1911 | 1746 | 1911
AMEM4A | IVER4A | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2009 | 1911 | 1746 | 1911
AMEM4B | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2032 | 1933 | 1766 | 1933
AMEM4B | IVER4B | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2032 | 1933 | 1766 | 1933
AXMI41 | CHIC4A | 30.7 | 8.8 | Composite | 0.0379 | 0.6609 | 130.8219 | 2779 | 2568 | 2217 | 2568
AXMI41 | EXET41 | 36.184 | 0 | OHL | 0.0404 | 0.6915 | 21.9115 | 2779 | 2568 | 2217 | 2568
BAGB21 | MAGA21 | 12.629 | 1.389 | Composite | 0.0435 | 0.5216 | 17.0509 | 1204 | 1115 | 1018 | 1115
BAGB21 | SWAN21 | 18.21 | 1.439 | Composite | 0.0625 | 0.7488 | 19.1165 | 1548 | 1548 | 1431 | 1431
BARK21 | REBR22 | 10.879 | 0 | OHL | 0.0411 | 0.4451 | 3.0706 | 1129 | 1081 | 1000 | 1081
BARK22 | REBR21 | 10.854 | 0 | OHL | 0.041 | 0.4441 | 3.0636 | 1205 | 1127 | 1044 | 1127
BARK41 | CHUE4A | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048
BARK41 | CHUE4B | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048
BARK41 | WHAM41 | 9.662 | 0.124 | Composite | 0.0156 | 0.1915 | 10.4541 | 2009 | 1909 | 1710 | 1909
BARK41 | WHAM41 | 9.662 | 0 | OHL | 0.0155 | 0.191 | 5.6429 | 2009 | 1911 | 1746 | 1911
BARK41 | WTHU4A | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911
BARK41 | WTHU4B | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911
BEDD21 | CHSI21 | 17.836 | 0.286 | Composite | 0.068 | 0.7365 | 7.9729 | 944 | 882 | 762 | 835
BEDD21 | WIMB21 | 8.5 | 0.968 | Composite | 0.0409 | 0.3915 | 11.7005 | 859 | 827 | 623 | 694
BEDD22 | CHSI21 | 17.836 | 0.137 | Composite | 0.0677 | 0.7328 | 6.4221 | 762 | 762 | 662 | 662
BEDD23 | WIMB2A | 8.5 | 0.582 | Composite | 0.0398 | 0.3821 | 8.4754 | 995 | 930 | 728 | 806
BEDD4A | ROWD42 | 0 | 10.1 | Cable | 0.0071 | 0.1292 | 121.8435 | 1309 | 1309 | 1309 | 1309
BEDD4B | ROWD41 | 0 | 10.1 | Cable | 0.0069 | 0.1275 | 124.3819 | 1417 | 1417 | 1220 | 1294
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882
BESW21 | FECK21 | 35.814 | 0 | OHL | 0.1425 | 1.5095 | 9.7917 | 955 | 882 | 762 | 882
BESW21 | OCKH21 | 56.939 | 0.731 | Composite | 0.2318 | 2.4208 | 22.7971 | 819 | 819 | 638 | 638
BICF41 | SPLN41 | 20.109 | 0 | OHL | 0.0191 | 0.355 | 13.187 | 3156 | 3032 | 2823 | 3032
BICF41 | WALP41 | 37.775 | 0 | OHL | 0.0335 | 0.6488 | 25.3895 | 3189 | 3063 | 2853 | 3063
BICF41 | WBUR41 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160
BICF41 | WBUR42 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160
BIGG41 | EASO41 | 16.5 | 0 | OHL | 0.0146 | 0.2834 | 11.1085 | 3326 | 2790 | 3320 | 3320
BIGG41 | WYMO41 | 18.772 | 0 | OHL | 0.0166 | 0.3225 | 12.6381 | 3326 | 2790 | 3320 | 3320
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882
BIRK21 | LISD2A | 0 | 12.891 | Cable | 0.0271 | 0.2978 | 125.0427 | 817 | 817 | 739 | 739
BISW21 | FECK21 | 22.83 | 0 | OHL | 0.0938 | 0.9633 | 6.2301 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 24.226 | 0 | OHL | 0.0932 | 1.0024 | 6.7545 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 27.111 | 0 | OHL | 0.1054 | 1.1236 | 7.5448 | 955 | 882 | 762 | 882
BISW21 | PENN21 | 30.172 | 0 | OHL | 0.1233 | 1.2726 | 8.2379 | 1040 | 1031 | 762 | 762
BLYT21 | BLYT22 | 0 | 0 | SSSC | 0 | 1.5868 | 0 | 1360 | 1307 | 1217 | 1307
BLYT21 | BLYT23 | 0 | 0 | SSSC | 0 | 1.5868 | 0 | 1360 | 1307 | 1217 | 1307
BLYT21 | STEW21 | 26.779 | 0 | OHL | 0.1472 | 1.3916 | 5.9965 | 682 | 629 | 538 | 629
BLYT21 | STEW21 | 26.711 | 0 | OHL | 0.1469 | 1.388 | 5.9813 | 682 | 629 | 538 | 629
BLYT21 | TYNE21 | 16.818 | 0 | OHL | 0.0742 | 0.7144 | 4.5642 | 1360 | 1310 | 1220 | 1310
BLYT21 | TYNE2A | 16.866 | 0 | OHL | 0.0744 | 0.7164 | 4.5772 | 1360 | 1310 | 1220 | 1310
BODE41 | GWYN4A | 0 | 0.8 | Cable | 0.0008 | 0.0094 | 7.6404 | 1056 | 1056 | 980 | 980
BODE41 | GWYN4B | 0.5 | 0 | OHL | 0.0005 | 0.0087 | 0.3284 | 2771 | 2695 | 2510 | 2695
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 3102 | 2935 | 2765 | 2935
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 2771 | 2771 | 2765 | 2771
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
BOTW41 | CHIL41 | 7.479 | 0 | OHL | 0.0066 | 0.1285 | 5.027 | 3341 | 3160 | 2971 | 3160
BOTW41 | LOVE41 | 14.672 | 0 | OHL | 0.013 | 0.252 | 9.8617 | 3341 | 3160 | 2971 | 3160
BRAI4A | BRFO41 | 48.267 | 0 | OHL | 0.0449 | 0.8314 | 32.3122 | 3326 | 3326 | 3317 | 3326
BRAI4A | BULL41 | 12.343 | 0 | OHL | 0.0121 | 0.2133 | 8.2261 | 3066 | 2830 | 2418 | 2830
BRAI4B | PELH41 | 65.942 | 0 | OHL | 0.0648 | 1.1396 | 43.9331 | 2779 | 2568 | 2217 | 2568
BRAI4B | RAYL41 | 33.03 | 0 | OHL | 0.0325 | 0.5709 | 22.0036 | 2779 | 2568 | 2217 | 2568
BRAW21 | ELLA21 | 16.802 | 0.081 | Composite | 0.0769 | 0.7134 | 5.4384 | 762 | 762 | 619 | 619
BRAW21 | KIRK21 | 17.279 | 4.547 | Composite | 0.0844 | 0.855 | 54.1379 | 762 | 762 | 619 | 619
BRAW21 | MONF21 | 51.155 | 0 | OHL | 0.1174 | 1.8824 | 15.9388 | 1204 | 1115 | 1018 | 1115
BRAW4A | PADI41 | 59.3 | 0 | OHL | 0.0754 | 1.1321 | 35.9226 | 2470 | 2350 | 2146 | 2350
BRED21 | MACC21 | 19.612 | 0 | OHL | 0.0768 | 0.8127 | 5.4608 | 948 | 882 | 753 | 753
BRED21 | SMAN21 | 10.004 | 5.629 | Composite | 0.0513 | 0.4604 | 46.762 | 865 | 865 | 749 | 749
BRED21 | STAL21 | 15.054 | 0 | OHL | 0.0665 | 0.6343 | 4.1113 | 1093 | 1031 | 925 | 1031
BRFO41 | DISS4A | 31.4 | 0.1 | Composite | 0.0279 | 0.5404 | 23.1059 | 3326 | 3326 | 3326 | 3326
BRFO41 | DISS4B | 31.4 | 0.1 | Composite | 0.0279 | 0.5404 | 23.1059 | 3326 | 3326 | 3326 | 3326
BRFO41 | FRIS4A | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2779 | 2568 | 2217 | 2568
BRFO41 | FRIS4B | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2779 | 2568 | 2217 | 2568
BRFO41 | FRIS4C | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2779 | 2569 | 2217 | 2569
BRFO41 | FRIS4D | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2779 | 2568 | 2217 | 2568
BRFO41 | PELH41 | 69.301 | 0 | OHL | 0.0655 | 1.1949 | 46.3271 | 3102 | 2935 | 2765 | 2935
BRIM2A | TOTT23 | 7.437 | 0.311 | Composite | 0.0345 | 0.3234 | 5.3982 | 1085 | 1031 | 925 | 1031
BRIM2A | WALX22 | 5.865 | 0 | OHL | 0.0268 | 0.2482 | 1.5911 | 1093 | 1031 | 925 | 1031
BRIM2B | TOTT22 | 7.305 | 0.393 | Composite | 0.0341 | 0.3201 | 6.2537 | 1085 | 1031 | 925 | 1031
BRIM2B | WALX22 | 5.997 | 0 | OHL | 0.0274 | 0.2538 | 1.6269 | 1093 | 1031 | 925 | 1031
BRIM2C | TOTT24 | 7.455 | 0.235 | Composite | 0.0344 | 0.3223 | 4.5788 | 1085 | 1031 | 925 | 1031
BRIM2C | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIM2D | TOTT21 | 7.455 | 0.384 | Composite | 0.0347 | 0.3264 | 6.1984 | 1085 | 1031 | 925 | 1031
BRIM2D | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIN21 | CHTE21 | 22.464 | 0.22 | Composite | 0.0519 | 0.8305 | 9.3505 | 934 | 934 | 753 | 753
BRIN21 | JORD21 | 13.257 | 1.489 | Composite | 0.0647 | 0.5918 | 16.0432 | 557 | 557 | 499 | 499
BRIN21 | NORL2A | 13.257 | 2.845 | Composite | 0.0708 | 0.6085 | 24.8202 | 419 | 419 | 381 | 381
BRIN21 | TEMP21 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882
BRIN21 | TEMP22 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882
BRIN22 | CHTE21 | 22.375 | 0 | OHL | 0.0513 | 0.8236 | 6.9689 | 1204 | 1115 | 1018 | 1115
BRIN22 | THUR21 | 5.704 | 0 | OHL | 0.0599 | 0.2384 | 1.5621 | 626 | 591 | 535 | 591
BRIN22 | TINP21 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 955 | 882 | 762 | 882
BRIN22 | TINP22 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 919 | 869 | 762 | 869
BRIN41 | THOM41 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2518 | 2395 | 2188 | 2395
BRIN41 | THOM42 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2545 | 2421 | 2211 | 2421
BRLE41 | DIDC41 | 37.691 | 5.7 | Composite | 0.0419 | 0.6724 | 87.0663 | 2779 | 2568 | 2217 | 2245
BRLE41 | DIDC41 | 37.691 | 5.7 | Composite | 0.0419 | 0.6719 | 134.3668 | 2277 | 2277 | 2037 | 2037
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2779 | 2569 | 2217 | 2569
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2779 | 2569 | 2217 | 2569
BRLE41 | MELK41 | 81.569 | 0 | OHL | 0.176 | 1.6326 | 46.8641 | 1389 | 1284 | 1108 | 1284
BRLE41 | MELK41 | 82.134 | 0 | OHL | 0.1769 | 1.6438 | 47.1939 | 1389 | 1284 | 1108 | 1284
BRLE41 | WWEY4A | 49.375 | 0 | OHL | 0.0789 | 0.9495 | 29.6914 | 2199 | 2092 | 1911 | 2092
BRLE41 | WWEY4B | 49.375 | 0 | OHL | 0.0789 | 0.9495 | 29.6914 | 2199 | 2092 | 1911 | 2092
BRWA41 | BRWA4A | 4.371 | 0 | OHL | 0.0079 | 0.087 | 2.5326 | 2030 | 1930 | 1770 | 1930
BRWA42 | BRWA4B | 4 | 0.462 | Composite | 0.0076 | 0.085 | 7.3611 | 2030 | 1930 | 1770 | 1930
BRWA4A | MELK41 | 77.004 | 0 | OHL | 0.1368 | 1.5195 | 45.0234 | 2009 | 1911 | 1746 | 1911
BRWA4A | SHUR41 | 14.02 | 0 | OHL | 0.0218 | 0.269 | 8.4136 | 3100 | 3050 | 2960 | 3050
BRWA4B | MELK41 | 76.264 | 0 | OHL | 0.1356 | 1.5048 | 44.5918 | 2009 | 2009 | 2009 | 2009
BRWA4B | SHUR41 | 14.02 | 0 | OHL | 0.0218 | 0.269 | 8.4136 | 3100 | 3050 | 2960 | 3050
BULL41 | RAYL41 | 20.646 | 0 | OHL | 0.0203 | 0.3568 | 13.7565 | 2779 | 2569 | 2217 | 2569
BURW41 | PELH41 | 42.782 | 0 | OHL | 0.0379 | 0.7348 | 28.7545 | 3326 | 3159 | 2971 | 3159
BURW41 | PELH41 | 42.934 | 0 | OHL | 0.0381 | 0.7374 | 28.8562 | 3035 | 2876 | 2238 | 2515
BURW41 | WALP41 | 51.189 | 0 | OHL | 0.0454 | 0.8792 | 34.4056 | 3326 | 3160 | 2971 | 3160
BURW41 | WALP41 | 51.183 | 0 | OHL | 0.0454 | 0.8791 | 34.4016 | 3326 | 3160 | 2971 | 3160
BUSH21 | DRAK21 | 38.153 | 0 | OHL | 0.146 | 1.6016 | 10.4839 | 1204 | 1115 | 1018 | 1115
BUSH21 | PENN21 | 21.653 | 0 | OHL | 0.0824 | 0.9078 | 5.9595 | 1038 | 1038 | 762 | 762
BUSH21 | WIEN2B | 5.197 | 4.318 | Composite | 0.0311 | 0.3404 | 48.3427 | 762 | 762 | 681 | 681
BUST21 | NECH21 | 2.648 | 7.619 | Composite | 0.026 | 0.3163 | 76.3606 | 725 | 713 | 599 | 635
BUST21 | NECH21 | 2.648 | 7.648 | Composite | 0.026 | 0.3169 | 76.528 | 725 | 713 | 599 | 635
BUST4A | DRAK41 | 34.592 | 0 | OHL | 0.0375 | 0.6017 | 22.8026 | 1203 | 1203 | 1103 | 1119
BUST4B | DRAK41 | 34.537 | 0 | OHL | 0.0375 | 0.6007 | 22.7664 | 2779 | 2568 | 2217 | 2568
CAMA11 | IROA13 | 0 | 1 | Cable | 0.815 | 5.549 | 1.802 | 246 | 228 | 198 | 228
CAMA12 | IROA12 | 0 | 1 | Cable | 0.815 | 5.549 | 1.802 | 246 | 228 | 198 | 228
CANT41 | CANT41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 3102 | 3102 | 3102 | 3102
CANT41 | CANT41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 3102 | 3102 | 3102 | 3102
CANT41 | CANT41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 3102 | 3102 | 3102 | 3102
CANT41 | CLEH41 | 14.7 | 0 | OHL | 0.0229 | 0.282 | 8.8214 | 3102 | 3048 | 2853 | 3048
CANT41 | KEMS4A | 28.2 | 0 | OHL | 0.0439 | 0.5411 | 16.9228 | 3102 | 2935 | 2765 | 2935
CANT41 | RICH41 | 25 | 0 | OHL | 0.0399 | 0.4808 | 15.0336 | 2038 | 2038 | 1801 | 1801
CANT41 | RICH41 | 25 | 0 | OHL | 0.0399 | 0.4808 | 15.0336 | 2038 | 2038 | 1801 | 1801
CANT41 | SELL4C | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3102 | 3048 | 2958 | 3048
CANT41 | SELL4D | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3103 | 3048 | 2959 | 3048
CAPE1A | INCE11 | 0 | 1 | Cable | 0.2226 | 2.0652 | 3.2486 | 258 | 258 | 240 | 240
CAPE1B | INCE11 | 0 | 1 | Cable | 0.2204 | 2.0451 | 3.2416 | 240 | 240 | 240 | 240
CAPE4A | CONQ41 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3326 | 3160 | 2971 | 3160
CAPE4A | FROD41 | 18.404 | 0 | OHL | 0.0199 | 0.2926 | 13.3521 | 2889 | 2748 | 2418 | 2748
CAPE4B | CONQ41 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3326 | 3160 | 2971 | 3160
CAPE4B | FROD41 | 18.315 | 0 | OHL | 0.0198 | 0.2912 | 13.2878 | 2890 | 2749 | 2418 | 2749
CARE21 | COWT2A | 27.881 | 0 | OHL | 0.1533 | 1.4488 | 6.2406 | 682 | 629 | 538 | 629
CARE21 | USKM2B | 19.94 | 0 | OHL | 0.1096 | 1.0362 | 4.4651 | 682 | 629 | 538 | 629
CARR21 | SMAN21 | 9.294 | 0.133 | Composite | 0.0414 | 0.4101 | 3.8882 | 835 | 835 | 665 | 665
CARR21 | SMAN21 | 10.747 | 0.23 | Composite | 0.0475 | 0.476 | 5.3274 | 835 | 835 | 665 | 665
CARR41 | DAIN41 | 2.545 | 0 | OHL | 0.0043 | 0.0496 | 1.5076 | 2169 | 2084 | 1940 | 2084
CARR41 | DAIN41 | 3.352 | 0 | OHL | 0.0059 | 0.0653 | 1.9776 | 3102 | 3048 | 2958 | 3048
CARR41 | KEAR41 | 13.154 | 0 | OHL | 0.0225 | 0.2574 | 7.7626 | 2212 | 2125 | 1979 | 2125
CARR41 | PEWO4A | 56.9 | 0 | OHL | 0.0988 | 1.1179 | 33.4404 | 2169 | 2084 | 1940 | 2084
CARR42 | DAIN41 | 2.063 | 0 | OHL | 0.0035 | 0.0404 | 1.2165 | 1500 | 1500 | 1500 | 1500
CARR4B | DAIN41 | 2.036 | 0 | OHL | 0.0037 | 0.0405 | 1.1791 | 1553 | 1553 | 1553 | 1553
CELL41 | DAIN41 | 53.412 | 2.31 | Composite | 0.0842 | 1.0314 | 76.8805 | 2508 | 2508 | 2300 | 2300
CELL41 | DRAK41 | 45.012 | 0 | OHL | 0.0719 | 0.8656 | 27.0675 | 2397 | 2302 | 2144 | 2302
CELL41 | DRAK41 | 45.712 | 0 | OHL | 0.073 | 0.8791 | 27.4871 | 2397 | 2302 | 2144 | 2302
CELL41 | MACC41 | 31.617 | 0 | OHL | 0.0494 | 0.6067 | 18.9767 | 3102 | 3048 | 2958 | 3048
CHIC41 | EXET41 | 67.12 | 8.8 | Composite | 0.0786 | 1.3565 | 152.8884 | 2779 | 2568 | 2217 | 2568
CHIC41 | MANN41 | 53.913 | 0 | OHL | 0.0585 | 0.9377 | 35.5401 | 3065 | 2829 | 2418 | 2829
CHIC4A | MANN41 | 54.066 | 0 | OHL | 0.0587 | 0.9404 | 35.6406 | 3065 | 2829 | 2418 | 2829
CHIL41 | FAWL41 | 0 | 3.73 | Cable | 0.0037 | 0.0235 | 56.9944 | 970 | 928 | 800 | 928
CHIL41 | FAWL41 | 0 | 3.69 | Cable | 0.0037 | 0.0232 | 56.3832 | 970 | 928 | 800 | 928
CHIL41 | LOVE41 | 22.379 | 0.315 | Composite | 0.0201 | 0.389 | 20.2483 | 1109 | 1109 | 901 | 901
CHSI21 | WWEY21 | 15.318 | 0 | OHL | 0.0519 | 0.6229 | 4.351 | 1316 | 1213 | 1104 | 1213
CHSI21 | WWEY22 | 15.347 | 0 | OHL | 0.052 | 0.6241 | 4.3592 | 1316 | 1213 | 1104 | 1213
CHTE21 | HIGM21 | 43.792 | 0 | OHL | 0.1218 | 1.806 | 12.2763 | 1381 | 1339 | 1258 | 1339
CHTE21 | HIGM21 | 43.651 | 0 | OHL | 0.1214 | 1.8002 | 12.2369 | 1381 | 1381 | 1375 | 1381
CHUE4A | TILB41 | 13.045 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2827 | 2827 | 2591 | 2591
CHUE4A | WTHU4D | 2.419 | 0 | OHL | 0.0038 | 0.0488 | 1.378 | 3102 | 3048 | 2958 | 3048
CHUE4B | TILB41 | 13.045 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2924 | 2924 | 2591 | 2591
CHUE4B | WTHU4C | 2.581 | 0 | OHL | 0.004 | 0.0519 | 1.4744 | 3102 | 3048 | 2958 | 3048
CILF2A | UPPB21 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882
CILF2B | UPPB22 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882
CILF41 | IMPP41 | 25.119 | 0 | OHL | 0.0273 | 0.4396 | 16.4758 | 2779 | 2568 | 2217 | 2568
CILF41 | RASS41 | 26.901 | 0 | OHL | 0.0292 | 0.4679 | 17.7332 | 2779 | 2568 | 2217 | 2568
CILF41 | RHIG41 | 25.011 | 0 | OHL | 0.0271 | 0.435 | 16.4876 | 2779 | 2568 | 2217 | 2568
CILF41 | SWAN41 | 61.595 | 0 | OHL | 0.0668 | 1.0713 | 40.6034 | 2779 | 2568 | 2217 | 2568
CILF41 | SWAN42 | 61.655 | 0 | OHL | 0.0669 | 1.0724 | 40.6428 | 3180 | 3000 | 2692 | 3000
CILF41 | WHSO4A | 35.208 | 0 | OHL | 0.0383 | 0.6151 | 23.1262 | 2779 | 2568 | 2217 | 2568
CITR41 | CITR41 | 0 | 0.1 | Cable | 0.0001 | 0.0008 | 1.8 | 1733 | 1492 | 1362 | 1492
CITR41 | CITR41 | 0 | 0.1 | Cable | 0.0001 | 0.0008 | 1.8 | 1566 | 1538 | 1351 | 1424
CITR41 | PUDM41 | 0 | 7.29 | Cable | 0.0066 | 0.0598 | 131.22 | 1282 | 1136 | 984 | 1136
CITR41 | SJOW41 | 0 | 7.243 | Cable | 0.0065 | 0.0594 | 130.374 | 1282 | 1136 | 984 | 1136
CITR41 | SJOW41 | 0 | 6.776 | Cable | 0.0061 | 0.0556 | 121.968 | 1282 | 1136 | 984 | 1136
CITR41 | WHAM4B | 0 | 9.39 | Cable | 0.0085 | 0.077 | 169.02 | 1282 | 1136 | 984 | 1136
CLEH41 | KEMS4B | 13.5 | 0 | OHL | 0.021 | 0.259 | 8.1013 | 3102 | 3048 | 2853 | 3048
CONQ41 | DAIN41 | 60.331 | 0 | OHL | 0.094 | 1.1575 | 36.2038 | 3102 | 3048 | 2853 | 3048
CONQ41 | DAIN41 | 60.294 | 0 | OHL | 0.0938 | 1.1562 | 36.2009 | 3102 | 3048 | 2853 | 3048
CONQ41 | FLIB41 | 0 | 3.495 | Cable | 0.0022 | 0.05 | 43.9195 | 1438 | 1438 | 1389 | 1389
CONQ41 | FLIB41 | 0 | 3.388 | Cable | 0.0022 | 0.0485 | 42.5749 | 1438 | 1438 | 1389 | 1389
CONQ41 | GWYN4A | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 2665 | 2561 | 2217 | 2561
CONQ41 | GWYN4B | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 2665 | 2561 | 2217 | 2561
CONQ41 | TREU4A | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2397 | 2302 | 2144 | 2302
CONQ41 | TREU4B | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2212 | 2125 | 1979 | 2125
COSO41 | RAYL41 | 13.913 | 0 | OHL | 0.0217 | 0.2698 | 8.2601 | 2886 | 2835 | 2663 | 2835
COSO41 | TILB4B | 12.363 | 0 | OHL | 0.0193 | 0.24 | 7.3306 | 3075 | 2876 | 2663 | 2876
COTT41 | KEAD4C | 34.479 | 0 | OHL | 0.0592 | 0.6828 | 20.0931 | 2213 | 2126 | 1980 | 2126
COTT41 | KEAD4D | 34.628 | 0 | OHL | 0.0595 | 0.6858 | 20.1792 | 2212 | 2125 | 1979 | 2125
COTT41 | MARH4B | 100.853 | 0 | OHL | 0.1772 | 1.9852 | 59.1294 | 2009 | 1912 | 1746 | 1912
COTT41 | RYHA4A | 76.891 | 0 | OHL | 0.0682 | 1.3211 | 51.7563 | 3326 | 3326 | 3317 | 3326
COTT41 | STAY41 | 27.788 | 0.5 | Composite | 0.0506 | 0.5544 | 51.7563 | 2213 | 2126 | 1980 | 2052
COTT42 | RYHA4B | 76.816 | 0 | OHL | 0.0681 | 1.3196 | 51.7119 | 2807 | 2696 | 2511 | 2696
COTT42 | STAY41 | 27.698 | 0 | OHL | 0.0441 | 0.5297 | 16.7334 | 2212 | 2125 | 1979 | 2125
COTT42 | WBUR42 | 6.76 | 0 | OHL | 0.0105 | 0.1321 | 3.9942 | 3326 | 3160 | 2144 | 3160
COVE21 | NECH21 | 30.715 | 0 | OHL | 0.0736 | 1.1961 | 9.1449 | 1204 | 1115 | 1018 | 1115
COVE21 | RATS2A | 64.863 | 0.5 | Composite | 0.1812 | 2.5694 | 23.9446 | 1000 | 1000 | 1000 | 1000
COWL41 | CULJ4A | 6.496 | 0 | OHL | 0.0085 | 0.1266 | 3.8528 | 2771 | 2568 | 2217 | 2568
COWL41 | DIDC41 | 11.503 | 0 | OHL | 0.0151 | 0.2242 | 6.8223 | 2779 | 2568 | 2217 | 2568
COWL41 | ECLA41 | 36.301 | 0 | OHL | 0.0322 | 0.6236 | 24.4394 | 3326 | 3326 | 3326 | 3326
COWL41 | LEIB4A | 52.495 | 0 | OHL | 0.0465 | 0.9017 | 35.3306 | 2779 | 2568 | 2217 | 2568
COWL41 | MITY41 | 100.105 | 2.092 | Composite | 0.1418 | 1.8493 | 98.0711 | 1180 | 1132 | 877 | 979
COWL41 | WALH41 | 89.553 | 2.092 | Composite | 0.113 | 1.6366 | 92.0801 | 1180 | 1132 | 877 | 979
COWT2A | PYLE21 | 22.6 | 0 | OHL | 0.1334 | 0.9291 | 6.3441 | 932 | 879 | 790 | 879
CREB2A | HEDO21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1749 | 1664 | 1520 | 1664
CREB2B | SAEN21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1749 | 1664 | 1520 | 1664
CREB41 | GART4A | 32.081 | 0 | OHL | 0.0348 | 0.558 | 21.1475 | 3075 | 2876 | 2663 | 2876
CREB41 | GART4B | 32.109 | 0 | OHL | 0.0348 | 0.5585 | 21.1659 | 3326 | 3159 | 2971 | 3159
CREB41 | THTO41 | 29.671 | 0 | OHL | 0.0263 | 0.5096 | 19.9438 | 3075 | 2876 | 2663 | 2876
CREB41 | THTO42 | 29.809 | 0 | OHL | 0.0264 | 0.512 | 20.0362 | 3075 | 2876 | 2663 | 2876
CULJ4A | DIDC41 | 4.898 | 0 | OHL | 0.0064 | 0.0955 | 2.905 | 2771 | 2568 | 2217 | 2568
DAIN41 | MACC41 | 33.593 | 2.4 | Composite | 0.0535 | 0.6515 | 66.7385 | 2397 | 2302 | 2144 | 2300
DAMC41 | KINO41 | 0 | 0.919 | Cable | 0.0001 | 0.0005 | 2.6467 | 1528 | 1528 | 1528 | 1528
DIDC41 | DIDC41 | 0 | 0 | Series Reactor | 0.0063 | 0.5 | 0 | 2640 | 2640 | 2640 | 2640
DINO41 | PENT41 | 4.545 | 7.305 | Composite | 0.0088 | 0.1776 | 95.0951 | 1623 | 1623 | 1571 | 1571
DINO41 | PENT41 | 0 | 10.605 | Cable | 0.0056 | 0.153 | 133.2664 | 1604 | 1571 | 1571 | 1571
DINO41 | PENT41 | 0 | 10.762 | Cable | 0.0057 | 0.1552 | 135.2393 | 1604 | 1604 | 1557 | 1557
DISS4A | NORM41 | 29.7 | 0 | OHL | 0.0263 | 0.5101 | 19.9633 | 3326 | 3326 | 3326 | 3326
DISS4A | YAXL41 | 0.05 | 0 | OHL | 0 | 0.0009 | 0.0336 | 3326 | 3326 | 3326 | 3326
DISS4B | NORM41 | 29.7 | 0 | OHL | 0.0263 | 0.5101 | 19.9633 | 3326 | 3326 | 3326 | 3326
DISS4B | YAXL41 | 0.05 | 0 | OHL | 0 | 0.0009 | 0.0336 | 3326 | 3326 | 3326 | 3326
DRAK41 | HAMH41 | 29.434 | 0 | OHL | 0.0534 | 0.5857 | 17.0575 | 2009 | 1911 | 1746 | 1911
DRAK41 | OLDB4A | 48.818 | 0.5 | Composite | 0.0921 | 0.9799 | 36.5074 | 1169 | 1169 | 1068 | 1068
DRAK41 | RATS41 | 32.907 | 0 | OHL | 0.0489 | 0.6238 | 20.201 | 2009 | 1911 | 1746 | 1911
DRAK41 | RUGE41 | 20.966 | 0 | OHL | 0.0379 | 0.4173 | 12.1495 | 2009 | 1911 | 1746 | 1911
DRAK41 | WILE41 | 16.937 | 0 | OHL | 0.0208 | 0.3015 | 11.0841 | 2009 | 1911 | 1746 | 1911
DRAX41 | DRAX42 | 0 | 0 | Series Reactor | 0.006 | 2 | 0 | 1320 | 1320 | 1320 | 1320
DRAX41 | EGGB42 | 11.188 | 0.64 | Composite | 0.0128 | 0.2017 | 30.2999 | 2089 | 2089 | 1878 | 1878
DRAX41 | FENW4A | 13.443 | 0 | OHL | 0.0146 | 0.2338 | 8.8618 | 3180 | 3000 | 2692 | 3000
DRAX41 | THTO42 | 22.579 | 0 | OHL | 0.0198 | 0.3877 | 15.2046 | 3075 | 2876 | 2663 | 2876
DRAX42 | EGGB41 | 11.188 | 0 | OHL | 0.0124 | 0.1983 | 7.2605 | 2973 | 2778 | 2447 | 2778
DRAX42 | THOM41 | 21.73 | 0 | OHL | 0.0311 | 0.3992 | 13.6444 | 2981 | 2867 | 2248 | 2505
DRAX42 | THTO41 | 22.579 | 0 | OHL | 0.0198 | 0.3877 | 15.2046 | 3075 | 2876 | 2663 | 2876
DUNG41 | NINF41 | 44.081 | 0 | OHL | 0.0391 | 0.7571 | 29.6278 | 3065 | 2829 | 2418 | 2829
DUNG41 | NINF41 | 44.056 | 0 | OHL | 0.0391 | 0.7567 | 29.6111 | 3066 | 2830 | 2418 | 2830
DUNG41 | SELL4E | 25.387 | 0 | OHL | 0.0395 | 0.4871 | 15.2346 | 3066 | 2830 | 2418 | 2830
DUNG41 | SELL4F | 25.403 | 0 | OHL | 0.0396 | 0.4874 | 15.2441 | 3066 | 2830 | 2418 | 2830
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 524 | 518 | 401 | 401
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 525 | 525 | 426 | 426
EALI21 | WISD2A | 0 | 6.075 | Cable | 0.0121 | 0.1391 | 61.5397 | 750 | 750 | 735 | 735
EASO4A | RYHA4B | 58.769 | 0 | OHL | 0.0521 | 1.0095 | 39.5649 | 2779 | 2569 | 2217 | 2569
EASO4B | RYHA4A | 58.95 | 0 | OHL | 0.0522 | 1.0126 | 39.6863 | 3326 | 3160 | 2971 | 3160
EASO4B | WYMO41 | 35.272 | 0 | OHL | 0.0313 | 0.6059 | 23.7466 | 2779 | 2568 | 2217 | 2568
ECLA41 | LEIB4B | 15.985 | 0 | OHL | 0.0141 | 0.2745 | 10.7511 | 2779 | 2568 | 2217 | 2568
ECLA41 | PAFB4A | 44.72 | 0 | OHL | 0.0814 | 0.8898 | 25.9172 | 2009 | 1911 | 1746 | 1911
ECLA41 | PAFB4B | 44.886 | 0 | OHL | 0.0817 | 0.8931 | 26.0131 | 2009 | 1911 | 1746 | 1911
EGGB41 | MONF4A | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 1970 | 1970 | 1970 | 1970
EGGB41 | ROCH4A | 84.875 | 0.7 | Composite | 0.1416 | 1.6214 | 64.456 | 1239 | 1239 | 1122 | 1122
EGGB41 | THOM41 | 28.07 | 0.197 | Composite | 0.0293 | 0.4897 | 21.8489 | 2217 | 2217 | 1801 | 1801
EGGB42 | FERR4A | 11.864 | 0 | OHL | 0.0128 | 0.2063 | 7.8228 | 2779 | 2568 | 2217 | 2568
EGGB42 | MONF41 | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 2779 | 2568 | 2217 | 2568
EGGB42 | STSB4B | 48.084 | 0 | OHL | 0.052 | 0.8361 | 31.7071 | 2779 | 2568 | 2217 | 2568
ELLA21 | FERR22 | 45.565 | 0 | OHL | 0.1573 | 1.8245 | 13.1474 | 1324 | 1260 | 1151 | 1260
ELLA21 | KIRK21 | 33.995 | 5.044 | Composite | 0.1618 | 1.5765 | 64.0738 | 762 | 762 | 619 | 619
ELLA21 | STAL21 | 39.6 | 0 | OHL | 0.1647 | 1.6624 | 10.8691 | 955 | 882 | 762 | 882
ELST12 | HEND11 | 0 | 1 | Cable | 0.081 | 0.634 | 16.01 | 299 | 275 | 218 | 275
ELST21 | MILH2A | 6.375 | 6.338 | Composite | 0.0548 | 0.3963 | 55.677 | 524 | 524 | 430 | 430
ELST21 | MILH2B | 6.375 | 6.282 | Composite | 0.0546 | 0.3952 | 55.2004 | 524 | 524 | 430 | 430
ELST21 | WARL21 | 59.208 | 0.261 | Composite | 0.2449 | 2.4665 | 19.2619 | 762 | 762 | 619 | 619
ELST21 | WATS21 | 5.398 | 0.399 | Composite | 0.0254 | 0.2396 | 5.8016 | 762 | 762 | 619 | 619
ELST22 | WARL21 | 59.244 | 0.59 | Composite | 0.2456 | 2.4772 | 22.8481 | 762 | 762 | 619 | 619
ELST22 | WATS22 | 5.398 | 0.222 | Composite | 0.0251 | 0.2347 | 3.8776 | 762 | 762 | 619 | 619
ELST41 | ELST4A | 0 | 0 | Series Reactor | 0.0125 | 1.1437 | 0 | 2000 | 2000 | 2000 | 2000
ELST41 | SJOW41 | 0 | 20 | Cable | 0.014 | 0.176 | 244.29 | 1767 | 1732 | 1663 | 1732
ELST4A | SUND41 | 34.834 | 0 | OHL | 0.0556 | 0.6699 | 20.9635 | 2400 | 2300 | 2140 | 2300
ELST4B | SUND42 | 34.706 | 0 | OHL | 0.0554 | 0.6674 | 20.8867 | 1590 | 1500 | 1346 | 1500
ENDE41 | PAFB4A | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911
ENDE41 | PAFB4B | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911
ENDE41 | RATS41 | 36.941 | 0 | OHL | 0.0399 | 0.5872 | 26.8034 | 2779 | 2568 | 2217 | 2568
ENDE41 | RATS41 | 36.873 | 0 | OHL | 0.0398 | 0.5862 | 26.7543 | 2779 | 2568 | 2217 | 2568
EXET41 | TAUN41 | 38.147 | 0 | OHL | 0.0694 | 0.759 | 22.1074 | 2009 | 1911 | 1746 | 1911
EXET41 | TAUN42 | 38.107 | 0 | OHL | 0.0693 | 0.7582 | 22.0842 | 2009 | 1911 | 1746 | 1911
FAWL41 | MANN41 | 61.115 | 0 | OHL | 0.066 | 1.0014 | 43.0253 | 2779 | 2568 | 2217 | 2568
FAWL41 | MAWO41 | 18.639 | 0 | OHL | 0.0214 | 0.3062 | 13.1667 | 2423 | 2327 | 2167 | 2327
FECK41 | HAMH41 | 43.314 | 0 | OHL | 0.078 | 0.8621 | 25.1018 | 2009 | 1911 | 1746 | 1911
FECK41 | IRON41 | 66.123 | 0 | OHL | 0.123 | 1.3148 | 38.3377 | 2009 | 1911 | 1746 | 1911
FECK41 | MITY41 | 78.649 | 0 | OHL | 0.1527 | 1.5677 | 45.4527 | 1967 | 1874 | 1712 | 1874
FECK41 | WALH41 | 67.986 | 0 | OHL | 0.1237 | 1.3527 | 39.4005 | 1967 | 1875 | 1712 | 1875
FENW4A | KEAD42 | 42.517 | 0 | OHL | 0.0198 | 0.2161 | 24.6399 | 3075 | 2876 | 2663 | 2876
FENW4A | THOM42 | 8.287 | 0 | OHL | 0.0165 | 0.1653 | 4.7826 | 2009 | 1911 | 1746 | 1911
FERR21 | MONF21 | 4.485 | 0 | OHL | 0.0103 | 0.1651 | 1.3966 | 1372 | 1307 | 1207 | 1307
FERR21 | SKLG21 | 20.033 | 0.685 | Composite | 0.0991 | 0.9874 | 9.8077 | 865 | 823 | 752 | 823
FERR22 | FERR2B | 0.554 | 0.16 | Composite | 0.002 | 0.0234 | 1.3262 | 1031 | 1031 | 981 | 981
FERR23 | FERR2A | 0.586 | 0 | OHL | 0.0013 | 0.0216 | 0.1825 | 1381 | 1307 | 1227 | 1307
FERR2A | MONF22 | 3.922 | 0 | OHL | 0.009 | 0.1444 | 1.2212 | 1204 | 1115 | 1018 | 1115
FERR2B | SKLG21 | 19.545 | 0.56 | Composite | 0.0975 | 0.9671 | 8.7544 | 865 | 823 | 752 | 823
FFES21 | TRAW21 | 7.291 | 0.133 | Composite | 0.0771 | 0.3081 | 2.8868 | 551 | 512 | 442 | 512
FFES22 | TRAW21 | 7.358 | 0 | OHL | 0.0772 | 0.3075 | 2.0153 | 551 | 512 | 442 | 512
FIDF21 | FIDF21 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750
FIDF21 | FIDF21 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750
FIDF21 | FROD21 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213
FIDF21 | FROD22 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213
FIDF21 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213
FIDF21 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 3140 | 3086 | 2999 | 3086
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 3140 | 3086 | 2999 | 3086
FOUR21 | HARK24 | 55.711 | 0 | OHL | 0.3289 | 2.3608 | 15.2112 | 854 | 795 | 700 | 795
FOUR21 | STEW21 | 27.731 | 0 | OHL | 0.1637 | 1.1751 | 7.5717 | 854 | 795 | 700 | 795
FRIN4A | FRIS41 | 0 | 0.3 | Cable | 0.0002 | 0.0035 | 3.2746 | 2779 | 2779 | 2779 | 2779
FRIN4B | FRIS4C | 0 | 0.1 | Cable | 0 | 0 | 0 | 2780 | 2780 | 2780 | 2780
FRIS4A | FRIS41 | 0 | 0.2 | Cable | 0.0001 | 0.0024 | 2.183 | 2779 | 2779 | 2779 | 2779
FRIS4A | SIZE41 | 7.61 | 0 | OHL | 0.0083 | 0.1324 | 5.0166 | 2779 | 2568 | 2217 | 2568
FRIS4B | FRIS41 | 0 | 0.15 | Cable | 0.0001 | 0.0018 | 1.6373 | 2779 | 2779 | 2779 | 2779
FRIS4B | SIZE41 | 7.61 | 0 | OHL | 0.0083 | 0.1324 | 5.0166 | 2779 | 2568 | 2217 | 2568
FRIS4C | LEIS4A | 6.8 | 0 | OHL | 0.0074 | 0.1183 | 4.4826 | 2779 | 2569 | 2217 | 2569
FRIS4D | FRIS41 | 0 | 0.2 | Cable | 0 | 0 | 0 | 2779 | 2779 | 2779 | 2779
FRIS4D | SIZE41 | 7.61 | 0 | OHL | 0.0083 | 0.1324 | 5.0166 | 2779 | 2568 | 2217 | 2568
FROD41 | ROCK41 | 1.197 | 0 | OHL | 0.0022 | 0.0238 | 0.6917 | 1100 | 1100 | 1100 | 1100
GART4A | HUMR41 | 37.372 | 0 | OHL | 0.0413 | 0.7015 | 23.0779 | 3156 | 3032 | 2823 | 3032
GART4A | KEAD43 | 5.711 | 0 | OHL | 0.0062 | 0.0993 | 3.7642 | 3075 | 2876 | 2663 | 2876
GART4B | KEAD41 | 5.689 | 0 | OHL | 0.0062 | 0.0989 | 3.7497 | 3326 | 3256 | 2978 | 3256
GART4B | KILL41 | 34.462 | 0 | OHL | 0.038 | 0.6467 | 21.2883 | 3156 | 3032 | 2823 | 3032
GRAI41 | GRAI41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159
GRAI41 | GRAI41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159
GRAI41 | GRAI41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159
GRAI41 | GRAI41 | 0 | 0 | Series Reactor | 0.0027 | 2.3091 | 0 | 2002 | 2002 | 2002 | 2002
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570
GRAI41 | MEDW41 | 2.5 | 0 | OHL | 0.0054 | 0.0513 | 1.3945 | 1390 | 1390 | 1390 | 1390
GRAI41 | TILB41 | 26.642 | 2.049 | Composite | 0.0302 | 0.4832 | 61.2324 | 2003 | 2003 | 1939 | 2003
GREN41 | MARH4A | 28.74 | 0 | OHL | 0.0522 | 0.5717 | 16.6594 | 2514 | 2439 | 2314 | 2439
GREN41 | MARH4B | 28.56 | 0 | OHL | 0.052 | 0.5682 | 16.5517 | 2009 | 1912 | 1746 | 1912
GREN41 | MARV4A | 26 | 0 | OHL | 0.0473 | 0.5173 | 15.0681 | 2009 | 1911 | 1746 | 1911
GREN41 | MARV4B | 26 | 0 | OHL | 0.0473 | 0.5173 | 15.0681 | 2009 | 1911 | 1746 | 1911
GRIW41 | KEAD41 | 49.379 | 0 | OHL | 0.047 | 0.873 | 32.3362 | 3075 | 2876 | 2663 | 2876
GRIW41 | SHBA41 | 12.673 | 0 | OHL | 0.0127 | 0.2284 | 8.1498 | 2860 | 2720 | 2484 | 2720
GRST2A | LACK2A | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1175 | 1119 | 1023 | 1119
GRST2A | LACK2B | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1129 | 1119 | 1000 | 1000
GRST2A | WILT2A | 0 | 1 | Cable | 0 | 0.011 | 0 | 207 | 196 | 183 | 196
GRST2A | WILT2B | 0 | 1 | Cable | 0 | 0.011 | 0 | 207 | 198 | 185 | 198
GRST2B | LACK2B | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1129 | 1119 | 1000 | 1000
GRST2B | LACK2C | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1129 | 1119 | 1000 | 1000
GRST2B | WILT2C | 0 | 1 | Cable | 0 | 0.011 | 0 | 198 | 198 | 180 | 180
GRST2B | WILT2D | 0 | 1 | Cable | 0 | 0.011 | 0 | 206 | 204 | 190 | 204
GWYN4A | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568
GWYN4B | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568
HACK2A | TOTT2B | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 1093 | 1031 | 926 | 1031
HACK2B | TOTT2A | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 1093 | 1031 | 926 | 1031
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1770 | 1730 | 1600 | 1730
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1770 | 1730 | 1600 | 1730
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729
HAKB1- | HARK13 | 1 | 0 | OHL | 0.7047 | 2.0317 | 0.451 | 132 | 123 | 106 | 123
HAKB4- | HARK41 | 9.857 | 0 | OHL | 0.0176 | 0.1957 | 5.7308 | 2213 | 2126 | 1980 | 2126
HAKB4B | HARK41 | 9.857 | 0 | OHL | 0.0176 | 0.1957 | 5.7308 | 2170 | 2084 | 1941 | 2084
HAMB4A | HEYS41 | 25.85 | 0 | OHL | 0.0229 | 0.444 | 17.3733 | 3326 | 3299 | 3098 | 3299
HAMB4A | PEWO41 | 19.698 | 0.752 | Composite | 0.0308 | 0.3917 | 24.9792 | 2473 | 2473 | 2189 | 2189
HAMB4A | STAH4A | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 240 | 240 | 240 | 240
HAMB4B | HEYS41 | 26.02 | 0 | OHL | 0.0231 | 0.4469 | 17.4871 | 3326 | 3326 | 3152 | 3326
HAMB4B | PEWO41 | 19.698 | 0.592 | Composite | 0.0308 | 0.3911 | 20.9006 | 2473 | 2473 | 2189 | 2189
HAMB4B | STAH4B | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 240 | 240 | 240 | 240
HAMH1A | LEMR11 | 0 | 1 | Cable | 0.016 | 0.098 | 1.942 | 226 | 209 | 209 | 209
HAMH1B | LEMR11 | 0 | 1 | Cable | 0.027 | 0.129 | 0.424 | 211 | 170 | 170 | 170
HAMH2A | NECH21 | 10.439 | 0 | OHL | 0.0263 | 0.4067 | 3.0955 | 1362 | 1285 | 1202 | 1285
HAMH41 | WILE41 | 84.14 | 0.7 | Composite | 0.1001 | 1.549 | 78.4627 | 2009 | 1912 | 1746 | 1912
HARK13 | JUNV1- | 1 | 0 | OHL | 1.194 | 2.729 | 0.743 | 123 | 123 | 106 | 123
HARK21 | HARK21 | 0 | 0.05 | Cable | 0.0001 | 0.0013 | 0.258 | 953 | 953 | 953 | 953
HARK21 | HARK23 | 0 | 0 | SSSC | 0 | 1.8512 | 0 | 774 | 774 | 676 | 676
HARK21 | HARK24 | 0 | 0 | SSSC | 0 | 3.7025 | 0 | 854 | 795 | 700 | 795
HARK23 | STEW21 | 83.682 | 0.117 | Composite | 0.4944 | 3.549 | 23.7211 | 774 | 774 | 676 | 676
HARK41 | HUTT41 | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2663 | 2771
HARK41 | HUTT43 | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2771 | 2771
HARM21 | HATL21 | 13.983 | 0 | OHL | 0.0472 | 0.5702 | 3.9648 | 1093 | 1031 | 925 | 1031
HARM21 | HAWP21 | 17.287 | 0 | OHL | 0.0584 | 0.7033 | 4.9126 | 1204 | 1115 | 1018 | 1115
HATL21 | HAWP2A | 31.443 | 0 | OHL | 0.1066 | 1.2811 | 8.9228 | 1093 | 1031 | 926 | 1031
HATL21 | SALH21 | 7.794 | 0 | OHL | 0.0327 | 0.3353 | 2.0878 | 1381 | 1279 | 1157 | 1279
HATL21 | TODP21 | 18.433 | 0 | OHL | 0.0713 | 0.7756 | 5.0465 | 1381 | 1279 | 1157 | 1279
HAWP21 | NORT21 | 30.238 | 0.459 | Composite | 0.0719 | 1.1367 | 14.2369 | 908 | 874 | 720 | 801
HAWP21 | OFFE21 | 9.514 | 0 | OHL | 0.0379 | 0.3948 | 2.6412 | 1093 | 1031 | 925 | 1031
HAWP2A | WBOL21 | 17.721 | 0 | OHL | 0.0705 | 0.7355 | 4.9196 | 1176 | 1119 | 1024 | 1119
HAWP4A | NORT41 | 30.157 | 0 | OHL | 0.0335 | 0.531 | 19.6771 | 2545 | 2421 | 2211 | 2421
HEDO21 | SAES21 | 0.605 | 0 | OHL | 0.0017 | 0.0226 | 0.1876 | 1749 | 1664 | 1520 | 1664
HEYS41 | MIDL41 | 0.9 | 0 | OHL | 0.0008 | 0.0155 | 0.6049 | 3326 | 3160 | 2971 | 3160
HEYS41 | QUER4B | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3326 | 3299 | 3098 | 3299
HIBU41 | SJOW41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1770 | 1730 | 1600 | 1730
HIBU41 | SJOW41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1770 | 1730 | 1600 | 1730
HIGM21 | THUR2A | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 626 | 591 | 535 | 591
HIGM41 | WBUR41 | 14.852 | 0.229 | Composite | 0.0254 | 0.2958 | 13.2571 | 2212 | 2125 | 1979 | 2125
HIGM4A | STOB41 | 39.671 | 0 | OHL | 0.0722 | 0.7893 | 22.9886 | 2147 | 2056 | 1904 | 2056
HINP41 | SAFO41 | 26.58 | 8.94 | Composite | 0.0421 | 0.5573 | 218.3267 | 2009 | 1911 | 1746 | 1911
HINP41 | SEAB41 | 57.813 | 8.99 | Composite | 0.0765 | 1.1045 | 239.9146 | 2009 | 1911 | 1746 | 1911
HINP41 | SHUR41 | 1.2 | 0 | OHL | 0.0019 | 0.0235 | 0.7057 | 3103 | 3048 | 2959 | 3048
HINP41 | SHUR41 | 1.213 | 0 | OHL | 0.002 | 0.024 | 0.707 | 3103 | 3048 | 2959 | 3048
HUMR41 | KILL41 | 2.879 | 0 | OHL | 0.0032 | 0.0543 | 1.7706 | 2771 | 2771 | 2771 | 2771
HURS21 | LITT2A | 5.164 | 2.938 | Composite | 0.0279 | 0.3019 | 12.6277 | 864 | 864 | 824 | 861
HURS21 | LITT2B | 5.14 | 2.863 | Composite | 0.0277 | 0.2987 | 12.3347 | 864 | 864 | 824 | 861
HURS21 | NEWX21 | 0 | 21.864 | Cable | 0.0437 | 0.5007 | 221.4823 | 890 | 882 | 704 | 784
HURS21 | NEWX21 | 0 | 21.106 | Cable | 0.0422 | 0.4833 | 213.8038 | 890 | 882 | 704 | 784
HUTT41 | HUTT42 | 0 | 0 | Series Capacitor | 0 | 0.5114 | 0 | 2771 | 2771 | 2771 | 2771
HUTT41 | HUTT43 | 0 | 0 | Series Capacitor | 0 | 0.5114 | 0 | 2771 | 2771 | 2771 | 2771
HUTT41 | QUER4A | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048
HUTT41 | QUER4B | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048
IMPP41 | MELK41 | 78.775 | 3.913 | Composite | 0.0882 | 1.4129 | 130.2038 | 1424 | 1424 | 1424 | 1424
INDQ41 | LAND41 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 2199 | 2092 | 1911 | 2092
INDQ41 | LAND42 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 1389 | 1284 | 1108 | 1284
IROA11 | OLDS12 | 1 | 0 | OHL | 0.298 | 2.366 | 3.453 | 452 | 423 | 365 | 372
IROA12 | OLDS12 | 1 | 0 | OHL | 0.297 | 2.361 | 2.693 | 457 | 424 | 366 | 372
IROA21 | MELK2A | 33.683 | 0.38 | Composite | 0.1862 | 1.7591 | 10.7703 | 581 | 581 | 524 | 524
IROA21 | MELK2B | 33.683 | 0.951 | Composite | 0.1877 | 1.7704 | 15.6295 | 581 | 581 | 524 | 524
IROA21 | WHSO2A | 34.621 | 0 | OHL | 0.2033 | 1.4667 | 9.4554 | 750 | 750 | 715 | 750
IROA21 | WHSO2B | 34.555 | 0 | OHL | 0.2034 | 1.4638 | 9.4375 | 750 | 750 | 715 | 750
IRON41 | LEGA4B | 62.073 | 0 | OHL | 0.0991 | 1.1937 | 37.3273 | 2002 | 2002 | 2002 | 2002
IRON41 | PENN4A | 27.761 | 0 | OHL | 0.0574 | 0.5549 | 15.9851 | 1389 | 1284 | 1108 | 1284
IRON41 | PENN4B | 24.617 | 0 | OHL | 0.0488 | 0.491 | 14.2132 | 1590 | 1500 | 1346 | 1500
IRON41 | RUGE41 | 58.681 | 0 | OHL | 0.1135 | 1.1701 | 33.9045 | 1389 | 1284 | 1108 | 1284
IRON41 | SHRE4A | 15.129 | 0 | OHL | 0.0242 | 0.2909 | 9.0977 | 2397 | 2302 | 2144 | 2302
IVER21 | NHYD2A | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 381
IVER21 | WWEY22 | 25.652 | 0.342 | Composite | 0.0975 | 1.059 | 10.9579 | 960 | 960 | 839 | 839
IVER22 | NHYD2B | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 381
IVER22 | WATS21 | 13.881 | 0.483 | Composite | 0.0643 | 0.601 | 9.0158 | 776 | 776 | 631 | 631
IVER22 | WATS22 | 13.881 | 0.436 | Composite | 0.0642 | 0.5997 | 8.5049 | 776 | 776 | 631 | 631
IVER2A | LALE21 | 17.186 | 0.402 | Composite | 0.0656 | 0.7143 | 9.2206 | 841 | 841 | 665 | 665
JORD21 | NORL2B | 0 | 2.843 | Cable | 0.0109 | 0.0719 | 20.1177 | 419 | 419 | 381 | 381
KEAD42 | WBUR42 | 28.425 | 0 | OHL | 0.0252 | 0.4882 | 19.1053 | 3326 | 3249 | 3098 | 3249
KEAD43 | KEAD44 | 0 | 0 | SSSC | 0 | 0.25 | 0 | 3326 | 3159 | 2971 | 3159
KEAD43 | KILL41 | 41.067 | 0 | OHL | 0.0403 | 0.7345 | 26.6033 | 3060 | 2931 | 2715 | 2931
KEAD43 | WBUR41 | 28.266 | 0 | OHL | 0.0251 | 0.4855 | 18.9976 | 3326 | 3249 | 3098 | 3249
KEAR21 | WHGA21 | 14.509 | 0.241 | Composite | 0.0667 | 0.6208 | 6.5558 | 835 | 835 | 665 | 665
KEAR21 | WHGA21 | 14.509 | 0.129 | Composite | 0.0665 | 0.6177 | 5.3384 | 213 | 213 | 289 | 289
KEAR41 | PADI41 | 39.101 | 0 | OHL | 0.0567 | 0.7296 | 24.2055 | 2169 | 2084 | 1940 | 2084
KEMS41 | LOFI4A | 38.035 | 0 | OHL | 0.0623 | 0.726 | 23.0007 | 3102 | 2935 | 2765 | 2935
KEMS41 | LOFI4B | 37.572 | 0 | OHL | 0.0617 | 0.7176 | 22.7061 | 3102 | 2935 | 2765 | 2935
KENG41 | SJOW41 | 0 | 4.756 | Cable | 0.0032 | 0.0562 | 51.9127 | 1770 | 1730 | 1600 | 1730
KENG41 | SJOW41 | 0 | 4.769 | Cable | 0.0032 | 0.0564 | 52.0546 | 1770 | 1730 | 1600 | 1730
KENG41 | WIMB41 | 0 | 12.329 | Cable | 0.0085 | 0.1557 | 134.5735 | 1770 | 1730 | 1600 | 1730
KENG41 | WIMB41 | 0 | 12.2 | Cable | 0.0084 | 0.1541 | 133.1654 | 1770 | 1730 | 1600 | 1730
KENG41 | WISD41 | 0 | 2.939 | Cable | 0.002 | 0.0347 | 32.0798 | 1770 | 1730 | 1600 | 1730
KENG41 | WISD42 | 0 | 2.989 | Cable | 0.002 | 0.0353 | 32.6255 | 1770 | 1730 | 1600 | 1730
KIBY21 | LISD21 | 0 | 10.239 | Cable | 0.0173 | 0.2966 | 60.8154 | 762 | 762 | 698 | 698
KIBY21 | LISD21 | 0 | 9.518 | Cable | 0.0228 | 0.2008 | 86.3283 | 762 | 762 | 619 | 619
KIBY21 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339
KIBY21 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339
KIBY21 | WASF2A | 10.945 | 0 | OHL | 0.0414 | 0.4478 | 3.0891 | 1521 | 1461 | 1360 | 1461
KIBY21 | WASF2B | 10.978 | 0 | OHL | 0.0415 | 0.4491 | 3.0984 | 1521 | 1461 | 1360 | 1461
KILL41 | SHBA41 | 17.05 | 0 | OHL | 0.0179 | 0.3134 | 10.7556 | 2860 | 2720 | 2484 | 2720
KINO41 | NFLE41 | 23.626 | 0 | OHL | 0.0284 | 0.4216 | 15.2234 | 3102 | 2935 | 2692 | 2935
KINO41 | SING41 | 17.685 | 0 | OHL | 0.0192 | 0.3076 | 11.6582 | 2889 | 2748 | 2510 | 2748
KINO41 | TILB41 | 15.478 | 1.835 | Composite | 0.0181 | 0.2893 | 46.9053 | 2003 | 2003 | 1948 | 1948
KIRK2A | SKLG21 | 0 | 8.608 | Cable | 0.0146 | 0.2402 | 93.5689 | 762 | 762 | 619 | 619
KITW21 | OLDB21 | 7.704 | 0.597 | Composite | 0.0301 | 0.3318 | 8.6639 | 667 | 667 | 619 | 619
KITW21 | OLDB2A | 8.278 | 0.222 | Composite | 0.0317 | 0.3449 | 4.7492 | 772 | 772 | 619 | 619
KNAR21 | MONF21 | 38.531 | 0.141 | Composite | 0.2716 | 1.7712 | 11.0429 | 551 | 513 | 443 | 513
KNAR21 | POPP21 | 49.192 | 0 | OHL | 0.3299 | 2.3254 | 12.2192 | 551 | 512 | 442 | 512
LACK21 | TODP21 | 5.965 | 0 | OHL | 0.0212 | 0.2477 | 1.654 | 1408 | 1332 | 1251 | 1332
LACK41 | SALH41 | 10.237 | 0.25 | Composite | 0.0184 | 0.2024 | 10.54 | 1831 | 1739 | 1588 | 1739
LACK41 | THTO41 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2030
LACK41 | THTO42 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2030
LAGA41 | LAND41 | 21.224 | 0 | OHL | 0.0339 | 0.4081 | 12.7621 | 2423 | 2327 | 2168 | 2327
LAGA41 | LAND42 | 21.355 | 0 | OHL | 0.0341 | 0.4108 | 12.8369 | 2423 | 2327 | 2168 | 2327
LALE21 | WWEY2A | 8.395 | 0 | OHL | 0.0317 | 0.3434 | 2.3695 | 1316 | 1213 | 1104 | 1213
LEGA41 | TREU4A | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720
LEGA41 | TREU4B | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720
LEGA4A | SHRE4A | 46.944 | 0 | OHL | 0.075 | 0.9028 | 28.2295 | 2002 | 2002 | 2002 | 2002
LEIB4A | SUND42 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568
LEIB4B | SUND41 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568
LEIS11 | SIZE11 | 0 | 2.149 | Cable | 0.0196 | 0.2155 | 4.8028 | 301 | 301 | 243 | 243
LEIS11 | SIZE11 | 0 | 2.148 | Cable | 0.0195 | 0.2154 | 4.8006 | 301 | 301 | 243 | 243
LEIS11 | SIZE1A | 0 | 1.65 | Cable | 0.015 | 0.1655 | 3.6876 | 301 | 301 | 243 | 243
LEIS11 | SIZE1B | 0 | 1.65 | Cable | 0.015 | 0.1655 | 3.6876 | 301 | 301 | 243 | 243
LEIS4A | SIZE41 | 0.81 | 0 | OHL | 0.0009 | 0.0141 | 0.534 | 2779 | 2569 | 2217 | 2569
LISD21 | LISD2A | 0 | 0 | Series Reactor | 0.0173 | 1.387 | 0 | 750 | 750 | 740 | 740
LITT41 | LOFI4A | 8.152 | 0 | OHL | 0.0127 | 0.157 | 4.8712 | 3103 | 3048 | 2959 | 3048
LITT41 | LOFI4B | 8.152 | 0 | OHL | 0.0127 | 0.157 | 4.8712 | 3103 | 3048 | 2959 | 3048
LITT41 | WTHU4E | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1815
LITT41 | WTHU4F | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1815
LOFI4A | ROWD4A | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1500 | 1346 | 1500
LOFI4B | ROWD4B | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1500 | 1346 | 1500
LOVE41 | NURS41 | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2771 | 2568 | 2217 | 2568
LOVE41 | NURS4A | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2779 | 2568 | 2217 | 2568
MACC41 | STAL4B | 31.196 | 0 | OHL | 0.062 | 0.617 | 18.1761 | 1710 | 1627 | 1488 | 1627
MAGA21 | PYLE21 | 6.238 | 0 | OHL | 0.0211 | 0.2537 | 1.7667 | 1204 | 1115 | 1018 | 1115
MANN41 | MANN41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159
MANN41 | MANN41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159
MANN41 | NURS4A | 39.823 | 0 | OHL | 0.043 | 0.6631 | 27.5672 | 2779 | 2568 | 2217 | 2568
MARH41 | MARH4A | 0 | 0 | Zero Length | 0 | 0 | 0 | 2860 | 2860 | 2860 | 2860
MARH42 | MARH4B | 0 | 0 | Zero Length | 0 | 0 | 0 | 2860 | 2860 | 2860 | 2860
MARH4A | STAY41 | 73.027 | 0 | OHL | 0.1328 | 1.4529 | 42.3252 | 2514 | 2439 | 2314 | 2439
MARV41 | MARV4A | 0.145 | 0 | OHL | 0.0003 | 0.0029 | 0.0839 | 2009 | 2009 | 2009 | 2009
MARV41 | MARV4B | 0.077 | 0 | OHL | 0.0001 | 0.0015 | 0.0446 | 2009 | 2009 | 2009 | 2009
MARV4A | SUND41 | 13.75 | 0 | OHL | 0.025 | 0.2736 | 7.9687 | 2009 | 1911 | 1746 | 1911
MARV4B | SUND42 | 13.955 | 1 | Composite | 0.0254 | 0.2777 | 8.0872 | 2009 | 1911 | 1746 | 1911
MAWO41 | NURS41 | 7.441 | 0 | OHL | 0.0093 | 0.1281 | 5.0417 | 2423 | 2327 | 2167 | 2327
MEDB4A | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3326 | 3326 | 3326
MEDB4A | STWB4R | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3326 | 3326 | 3326
MEDB4B | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3326 | 3326 | 3326
MEDB4B | STWB4Q | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3326 | 3326 | 3326
MELK41 | MITY41 | 28.101 | 0 | OHL | 0.0511 | 0.5591 | 16.2853 | 2105 | 2016 | 1867 | 2016
MELK41 | MITY41 | 28.052 | 0 | OHL | 0.051 | 0.5581 | 16.257 | 2105 | 2016 | 1867 | 2016
MELK41 | SEAB41 | 53.558 | 0 | OHL | 0.0598 | 0.9451 | 34.8897 | 2545 | 2421 | 2211 | 2421
MIDL41 | QUER4A | 9.704 | 0 | OHL | 0.0086 | 0.1667 | 6.5225 | 3326 | 3159 | 2971 | 3159
MONF22 | POPP21 | 37.84 | 0 | OHL | 0.208 | 2.0034 | 8.337 | 682 | 629 | 538 | 629
MONF41 | PADI41 | 87.848 | 0 | OHL | 0.1064 | 1.6286 | 54.7416 | 2518 | 2395 | 2188 | 2395
NECT41 | NECT4A | 0 | 0 | Zero Length | 0 | 0 | 0 | 1364 | 1364 | 1250 | 1250
NECT41 | NECT4B | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159
NECT4A | NORM41 | 35.652 | 0 | OHL | 0.0316 | 0.6124 | 23.9626 | 3326 | 3326 | 3317 | 3326
NECT4A | WALP41 | 43.459 | 0 | OHL | 0.0385 | 0.7464 | 29.2107 | 3326 | 3326 | 3317 | 3326
NECT4B | NORM41 | 35.652 | 0 | OHL | 0.0316 | 0.6124 | 23.9626 | 3326 | 3258 | 3060 | 3258
NECT4B | WALP41 | 43.459 | 0 | OHL | 0.0385 | 0.7464 | 29.2107 | 3326 | 3160 | 2971 | 3160
NEEP21 | PITS21 | 0.851 | 3.975 | Composite | 0.0214 | 0.1378 | 26.8236 | 419 | 419 | 381 | 381
NEEP21 | SHEC21 | 0.851 | 4.428 | Composite | 0.0234 | 0.1494 | 29.8542 | 419 | 419 | 381 | 381
NEEP4A | STSB4B | 12.801 | 0 | OHL | 0.0276 | 0.2627 | 7.1402 | 2779 | 2568 | 2217 | 2568
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 827 | 827 | 779 | 779
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 819 | 819 | 813 | 813
NFLE41 | SING41 | 5.941 | 0 | OHL | 0.0093 | 0.114 | 3.5652 | 2889 | 2748 | 2510 | 2748
NFLE41 | WTHU4A | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907
NFLE41 | WTHU4B | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907
NORL2A | SHEC21 | 0 | 4.372 | Cable | 0.0192 | 0.1119 | 29.2487 | 419 | 419 | 381 | 381
NORL2B | PITS21 | 0 | 10.751 | Cable | 0.0473 | 0.2752 | 71.9242 | 419 | 419 | 381 | 381
NORT21 | SALH21 | 12.178 | 0 | OHL | 0.0464 | 0.526 | 3.2482 | 1381 | 1293 | 1197 | 1293
NORT41 | OSBA41 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911
NORT41 | OSBA42 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911
NORT41 | SALH42 | 12.206 | 0 | OHL | 0.022 | 0.2492 | 6.888 | 1831 | 1739 | 1588 | 1739
NORT41 | SPEN41 | 21.134 | 2 | Composite | 0.0276 | 0.4062 | 12.7287 | 2545 | 2421 | 2211 | 2421
NORT41 | SPEN42 | 21.134 | 2 | Composite | 0.0276 | 0.4062 | 12.7287 | 2545 | 2421 | 2211 | 2421
NORW11 | NOTR11 | 1 | 0 | OHL | 0.236 | 0.778 | 0.315 | 265 | 246 | 212 | 246
NORW12 | NOTR12 | 1 | 0 | OHL | 0.2362 | 0.778 | 0.3149 | 350 | 350 | 350 | 350
OCKH21 | OLDB2A | 5.46 | 0 | OHL | 0.0208 | 0.2294 | 1.4988 | 772 | 772 | 619 | 619
OCKH21 | WIEN2A | 4.623 | 0.283 | Composite | 0.0216 | 0.202 | 4.2819 | 672 | 672 | 599 | 599
OCKH2A | WIEN2B | 4.67 | 0 | OHL | 0.0213 | 0.1977 | 1.2665 | 760 | 760 | 760 | 760
OFFE21 | WBOL21 | 8.207 | 0 | OHL | 0.0327 | 0.3406 | 2.2784 | 1176 | 1115 | 1018 | 1115
OSBA41 | THTO43 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2779 | 2568 | 2217 | 2568
OSBA42 | THTO41 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2779 | 2568 | 2217 | 2568
PADI41 | PEWO4B | 37.608 | 0 | OHL | 0.0556 | 0.7049 | 23.1779 | 2169 | 2084 | 1940 | 2084
PELH41 | RYEH4A | 23.015 | 0 | OHL | 0.025 | 0.4003 | 15.1704 | 2779 | 2568 | 2217 | 2568
PELH41 | RYEH4B | 23.439 | 0 | OHL | 0.0254 | 0.4077 | 15.4489 | 2779 | 2569 | 2217 | 2569
PELH41 | SUND42 | 45.13 | 0 | OHL | 0.0487 | 0.752 | 31.2185 | 3180 | 3000 | 2692 | 3000
PELH41 | WYMO41 | 26.856 | 0 | OHL | 0.029 | 0.4469 | 18.6034 | 2771 | 2771 | 2692 | 2771
PEMB41 | SWAN41 | 84.697 | 0 | OHL | 0.0919 | 1.4731 | 55.833 | 2779 | 2568 | 2217 | 2568
PEMB41 | SWAN41 | 83.975 | 0 | OHL | 0.0911 | 1.4606 | 55.3574 | 2779 | 2568 | 2217 | 2568
PEMB41 | SWAN42 | 84.57 | 0 | OHL | 0.0918 | 1.4709 | 55.7496 | 2779 | 2568 | 2217 | 2568
PEMB41 | WALH41 | 217.727 | 5.468 | Composite | 0.2372 | 3.8063 | 207.4152 | 2779 | 2568 | 2217 | 2568
PENT41 | TRAW41 | 45.1 | 6.308 | Composite | 0.0633 | 0.9555 | 131.5497 | 1135 | 1135 | 992 | 992
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568
PEWO2A | PEWO2C | 0 | 0 | SSSC | 0 | 0.476 | 0 | 1521 | 1461 | 1360 | 1461
PEWO2B | PEWO2D | 0 | 0 | SSSC | 0 | 0.476 | 0 | 1521 | 1461 | 1360 | 1461
PEWO2C | WASF2A | 23.481 | 0 | OHL | 0.0887 | 0.9606 | 6.6274 | 1521 | 1461 | 1360 | 1461
PEWO2D | WASF2B | 23.521 | 0 | OHL | 0.0889 | 0.9623 | 6.6386 | 1521 | 1461 | 1360 | 1461
PEWO41 | QUER4A | 31.939 | 0 | OHL | 0.0498 | 0.6128 | 19.1665 | 3102 | 3048 | 2853 | 3048
PEWO41 | QUER4B | 32.087 | 0 | OHL | 0.05 | 0.6156 | 19.2551 | 3102 | 3048 | 2853 | 3048
PITS21 | TEMP21 | 0 | 6.69 | Cable | 0.0294 | 0.1713 | 44.7561 | 419 | 419 | 381 | 381
PITS21 | WIBA21 | 0 | 2.324 | Cable | 0.0077 | 0.0581 | 17.337 | 439 | 439 | 381 | 381
PUDM41 | WHAM4A | 0 | 2.17 | Cable | 0.002 | 0.0178 | 39.06 | 1282 | 1136 | 984 | 1136
PYLE21 | PYLE21 | 0 | 0.25 | Cable | 0.0004 | 0.0063 | 1.69 | 1204 | 1115 | 1018 | 1115
RASS41 | WALH41 | 72.788 | 5.269 | Composite | 0.0799 | 1.2847 | 109.6583 | 2779 | 2568 | 2217 | 2568
RATS41 | STAY4A | 43.614 | 0 | OHL | 0.0793 | 0.8678 | 25.2757 | 2147 | 2057 | 1905 | 2057
RATS41 | STOB41 | 26.72 | 0.179 | Composite | 0.0487 | 0.5326 | 21.4031 | 2147 | 2056 | 1904 | 2056
RATS41 | WILE41 | 21.748 | 0.216 | Composite | 0.0397 | 0.435 | 16.174 | 1309 | 1309 | 1067 | 1067
RATS41 | WILE41 | 21.684 | 0 | OHL | 0.0394 | 0.4314 | 12.5666 | 2009 | 1911 | 1746 | 1911
RAYL41 | TILB4A | 20.499 | 0 | OHL | 0.0319 | 0.3933 | 12.3014 | 3102 | 2935 | 2765 | 2935
REBR21 | TOTT23 | 3.305 | 9.678 | Composite | 0.0166 | 0.2027 | 106.1327 | 1205 | 1127 | 1044 | 1127
REBR22 | TOTT24 | 3.305 | 11.448 | Composite | 0.0174 | 0.2151 | 125.3726 | 1205 | 1127 | 1044 | 1127
RHIG41 | SWAN41 | 34.34 | 0 | OHL | 0.0373 | 0.5973 | 22.6374 | 2779 | 2568 | 2217 | 2568
ROCH21 | STAL21 | 31.256 | 0 | OHL | 0.1235 | 1.3183 | 8.54 | 1324 | 1260 | 1151 | 1260
ROCH21 | WHGA21 | 11.489 | 0.257 | Composite | 0.053 | 0.4934 | 5.9105 | 841 | 841 | 665 | 665
ROCH21 | WHGA21 | 11.489 | 0.238 | Composite | 0.0529 | 0.4929 | 5.7039 | 419 | 419 | 404 | 404
RYEH41 | RYEH4B | 0.137 | 0 | OHL | 0.0001 | 0.0024 | 0.0903 | 2779 | 2569 | 2217 | 2569
RYEH41 | WALX4A | 5.324 | 0 | OHL | 0.0058 | 0.0926 | 3.5096 | 2779 | 2568 | 2217 | 2568
RYEH4A | RYEH43 | 0.264 | 0 | OHL | 0.0004 | 0.0051 | 0.1585 | 2779 | 2569 | 2217 | 2569
RYEH4A | WALX4B | 5.461 | 0 | OHL | 0.0059 | 0.095 | 3.6 | 2779 | 2568 | 2217 | 2568
RYEH4B | RYEH42 | 0.215 | 0 | OHL | 0.0003 | 0.0041 | 0.1291 | 2779 | 2569 | 2217 | 2569
SAEN21 | SAES21 | 0.484 | 0 | OHL | 0.0013 | 0.018 | 0.1501 | 1749 | 1664 | 1520 | 1664
SAFO41 | SEAB41 | 31.28 | 0 | OHL | 0.0345 | 0.5479 | 20.4859 | 3190 | 3060 | 2850 | 3060
SEAB41 | WHSO4A | 30.426 | 3.89 | Composite | 0.0374 | 0.5858 | 97.4265 | 1424 | 1424 | 1424 | 1424
SELL4A | SELL4A | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 1860 | 1860 | 1860 | 1860
SELL4A | SELL4C | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 1642
SELL4A | SELL4D | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 1642
SELL4A | SELL4E | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 1642
SELL4A | SELL4F | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 1642
SELL4B | SELL4C | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3326 | 3159 | 2971 | 3159
SELL4B | SELL4D | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3326 | 3326 | 3326 | 3326
SELL4B | SELL4E | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3159 | 2971 | 3159
SELL4B | SELL4F | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3159 | 2971 | 3159
SHRE4A | SHRE4B | 0.054 | 0 | OHL | 0.0001 | 0.001 | 0.0324 | 240 | 240 | 240 | 240
SHUR41 | SHUR41 | 0 | 0 | Series Reactor | 0 | 2 | 0 | 2400 | 2400 | 2400 | 2400
SHUR41 | TAUN41 | 27 | 0 | OHL | 0.0487 | 0.5369 | 15.6574 | 2213 | 2126 | 1980 | 2126
SHUR41 | TAUN42 | 27 | 0 | OHL | 0.0487 | 0.5369 | 15.6574 | 2213 | 2126 | 1980 | 2126
SPEN41 | STEW41 | 37.795 | 0.126 | Composite | 0.0498 | 0.7386 | 24.4993 | 2470 | 2350 | 2146 | 2350
SPEN42 | SPEN42 | 0 | 0.131 | Cable | 0.0001 | 0.0015 | 1.4299 | 278 | 265 | 248 | 250
SPEN42 | STEW41 | 37.795 | 0 | OHL | 0.0497 | 0.7368 | 22.4165 | 2470 | 2350 | 2146 | 2350
SPLN41 | WALP41 | 29.234 | 0 | OHL | 0.0272 | 0.5117 | 19.3195 | 3189 | 3063 | 2853 | 3063
SSHI22 | TYNE2A | 7.028 | 0 | OHL | 0.031 | 0.2985 | 1.9072 | 1247 | 1180 | 1065 | 1180
SSHI22 | WBOL21 | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1176 | 1119 | 1024 | 1119
STAL4A | THOM41 | 69.271 | 6.952 | Composite | 0.0793 | 1.2727 | 151.2452 | 1442 | 1442 | 1314 | 1314
STAL4B | STSB4A | 26.581 | 7.031 | Composite | 0.0345 | 0.532 | 124.2199 | 1436 | 1436 | 1308 | 1308
STEN11 | STES11 | 1 | 0 | OHL | 0.0266 | 0.1193 | 0.1077 | 198 | 198 | 181 | 181
SUND41 | WYMO41 | 18.156 | 0 | OHL | 0.0196 | 0.302 | 12.5826 | 3048 | 3000 | 2692 | 3000
SWAN41 | SWAN4B | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 3048 | 3048 | 2971 | 3048
SWAN42 | SWAN4A | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 1389 | 1284 | 1108 | 1284
TEMP22 | WIBA21 | 0 | 3.607 | Cable | 0.0159 | 0.0923 | 24.1308 | 421 | 421 | 381 | 381
THOM21 | WMEL21 | 23.791 | 0.947 | Composite | 0.1105 | 1.0548 | 15.8849 | 764 | 764 | 698 | 698
THOM2A | WMEL21 | 24.413 | 0.8 | Composite | 0.1126 | 1.0793 | 10.588 | 955 | 882 | 762 | 882
THUR21 | THUR2A | 4.653 | 0 | OHL | 0.0488 | 0.1944 | 1.2745 | 551 | 512 | 442 | 512
THUR2A | WMEL21 | 16.348 | 0 | OHL | 0.0746 | 0.7099 | 4.3235 | 955 | 882 | 762 | 882
TILB21 | WARL21 | 13.065 | 0 | OHL | 0.0597 | 0.553 | 3.5441 | 1175 | 1119 | 1023 | 1119
TILB21 | WARL21 | 12.897 | 0 | OHL | 0.059 | 0.5459 | 3.4987 | 1175 | 1119 | 1023 | 1119
TILB41 | TILB4A | 0.058 | 0 | OHL | 0.0001 | 0.0012 | 0.033 | 3102 | 3048 | 2958 | 3048
TILB41 | TILB4B | 0.059 | 0 | OHL | 0.0001 | 0.0011 | 0.0353 | 3102 | 3048 | 2853 | 3048
TOTT2A | TOTT22 | 0 | 0 | Zero Length | 0 | 0 | 0 | 904 | 904 | 904 | 904
TOTT2A | TOTT24 | 0 | 0 | Zero Length | 0 | 0 | 0 | 950 | 950 | 830 | 830
TOTT2B | TOTT21 | 0 | 0 | Zero Length | 0 | 0 | 0 | 904 | 904 | 904 | 904
TOTT2B | TOTT23 | 0 | 0 | Zero Length | 0 | 0 | 0 | 950 | 950 | 830 | 830
TRAW41 | TREU4A | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5731 | 3102 | 3048 | 2958 | 3048
TRAW41 | TREU4B | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5731 | 3102 | 3048 | 2958 | 3048
TREM21 | USKM2A | 15.048 | 0 | OHL | 0.0854 | 0.7095 | 3.7487 | 695 | 641 | 548 | 641
TYNE21 | WBOL21 | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1131 | 1052 | 912 | 1052
USKM21 | USKM2A | 0.692 | 0 | OHL | 0.0038 | 0.036 | 0.1546 | 695 | 642 | 548 | 642
USKM21 | USKM2B | 0.391 | 0 | OHL | 0.0039 | 0.0167 | 0.1052 | 682 | 629 | 538 | 629
USKM21 | WHSO21 | 5.841 | 0 | OHL | 0.0345 | 0.2401 | 1.6394 | 1005 | 956 | 874 | 956
USKM21 | WHSO22 | 5.849 | 0 | OHL | 0.0345 | 0.2405 | 1.6417 | 1005 | 956 | 873 | 956
USKM2A | WHSO21 | 5.562 | 0 | OHL | 0.0306 | 0.289 | 1.2455 | 695 | 641 | 548 | 641
USKM2B | WHSO22 | 5.851 | 0 | OHL | 0.0322 | 0.304 | 1.3103 | 682 | 629 | 538 | 629
WBUR41 | WBUR42 | 0 | 0 | Series Reactor | 0.0026 | 2.3169 | 0 | 1500 | 1500 | 1500 | 1500
WHSO41 | WHSO4A | 0.077 | 0 | OHL | 0.0001 | 0.0013 | 0.0506 | 992 | 916 | 783 | 916
WIMB21 | WIMB2A | 0 | 0 | Zero Length | 0 | 0 | 0 | 995 | 930 | 728 | 806
WTHU4C | WTHU4E | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400
WTHU4D | WTHU4F | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400

## B-2-1d
B-2-1d - OFTO Transmission Circuits for 2024/25
OFTO | Station | Node 1 | Node 2 | OHL Length(km) | Cable Length(km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA) | Voltage (kV)
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSO11 | BOSW11 | 0 | 29.45 | Cable | 1.634 | 2.451 | 25.197 | 106 | 132
TC Beatrice OFTO Limited | Beatrice Offshore Wind Farm | BEIW21 | BEIW22 | 0 | 1.315 | Cable | 0.033 | 0.014 | 4.119 | 321 | 220
|  | BEIW21 | BEAT21 | 0 | 89.2 | Cable | 0.822 | 2.262 | 291.875 | 321 | 220
|  | BEIW22 | BEAT22 | 0 | 89.2 | Cable | 0.822 | 2.262 | 291.875 | 321 | 220
|  | BEAT41 | BLHI4- | 0 | 0.6 | Cable | 0.002 | 0.006 | 4.645 | 321 | 400
|  | BEAT41 | BLHI4- | 0 | 0.6 | Cable | 0.002 | 0.006 | 4.645 | 321 | 400
Diamond Transmission Partners BBE Limited | Burbo Bank Extension Wind Farm | BODE41 | BBWO41 | 0 | 0.6 | Cable | 0.0009 | 0.0064 | 5.1271 | 277 | 400
|  | BBWO21 | BBWW21 | 0 | 34.622 | Cable | 0.3875 | 0.9335 | 103.7511 | 277 | 220
DOGGERBANK OFFSHORE WIND FARM PROJECT 1 PROJCO LIMITED | Dogger Bank B Offshore Wind Farm | DBBODC | DBBWDC | 0 | 205 | Cable | 0.0024 | 0 | 0 | 1940 | ±320
|  | DBBO41 | CREB41 | 0 | 1.6 | Cable | 5.9e-06 | 8e-05 | 0.3796 | 2044 | 400
| Dogger Bank A Offshore Wind Farm | DBAOD | DBAWD | 0 | 205 | Cable | 0.0024 | 0 | 0 | 1940 | ±320
|  | CREB41 | DBAO41 | 0 | 1.6 | Cable | 5.9e-06 | 8e-05 | 0.3796 | 2044 | 400
TC Dudgeon OFTO plc | Dudgeon Offshore Wind Farm | DUDW11 | DUDO11 | 0 | 89.3 | Cable | 1.816 | 6.8182 | 110.6693 | 172 | 132
|  | DUDW12 | DUDO12 | 0 | 89.3 | Cable | 1.816 | 6.8182 | 110.6693 | 172 | 132
East Anglia One Limited | East Anglia Offshore Wind Farm | BRFO41 | BRST41 | 0 | 0.47 | Cable | 0.001209 | 0.0059617 | 3.8508 | 369 | 400
|  | BRFO41 | BRST42 | 0 | 0.47 | Cable | 0.001209 | 0.0059617 | 3.8508 | 369 | 400
|  | BRST21 | EAAW21 | 0 | 122.358 | Cable | 0.77153 | 3.2715 | 411.04 | 344 | 220
|  | BRST22 | EAAW22 | 0 | 122.358 | Cable | 0.77153 | 3.2715 | 411.04 | 344 | 220
Diamond Transmission Partners Galloper Limited | Galloper Offshore Wind Farm | GALO11 | LEIS11 | 0 | 0.28 | Cable | 0.01 | 0.03 | 0.38 | 208 | 132
|  | GALO12 | LEIS11 | 0 | 0.28 | Cable | 0.01 | 0.03 | 0.38 | 208 | 132
|  | GALO11 | GANW11 | 0 | 45.8 | Cable | 1.23 | 2.83 | 58.38 | 180.6 | 132
|  | GALO12 | GANW12 | 0 | 45.8 | Cable | 1.23 | 2.83 | 58.38 | 180.6 | 132
Greater Gabbard OFTO Plc | Greater Gabbard Offshore Wind Farm | GGON11 | LEIS11 | 0 | 0 | Cable | 0 | 0 | 0 | 180 | 132
|  | GGON12 | LEIS11 | 0 | 0 | Cable | 0 | 0 | 0 | 180 | 132
|  | GGON13 | LEIS11 | 0 | 0 | Cable | 0 | 0 | 0 | 180 | 132
|  | GREG11 | GGON11 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
|  | GREG12 | GGON12 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
|  | GREG13 | GGON13 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
|  | GREG12 | GREG14 | 0 | 17 | Cable | 0.36 | 1.07 | 20.5 | 150 | 132
TC Gunfleet Sands OFTO Limited | Gunfleet Sands Offshore Wind Farm | CLTO11 | GUNS11 | 0 | 12.789 | Cable | 0.3254 | 0.8061 | 15.5518 | 158 | 132
Gwynt y Môr OFTO plc | Gwynt Y Mor Offshore Wind Farm | GWYO11 | GWBW11 | 0 | 33.3 | Cable | 0.973 | 2.5403 | 37.6879 | 149 | 132
|  | GWYO11 | GWBW12 | 0 | 33.3 | Cable | 0.973 | 2.5403 | 37.6879 | 149 | 132
|  | GWYO12 | GWAW11 | 0 | 30.3 | Cable | 0.8763 | 2.3371 | 34.6335 | 149 | 132
|  | GWYO12 | GWAW12 | 0 | 30.3 | Cable | 0.8763 | 2.3371 | 34.6335 | 149 | 132
Diamond Transmission Partners Hornsea One Limited | Hornsea One Offshore Wind Farm | KILL41 | HOWA41 | 0 | 0.52 | Cable | 0.000387 | 0.007298 | 5.7608 | 1328 | 400
|  | KILL41 | HOWA41 | 0 | 0.5 | Cable | 0.000387 | 0.007298 | 5.7608 | 1328 | 400
|  | HOWA21 | HOWR2A | 0 | 105.1 | Cable | 0.68384 | 3.2701 | 292.1283 | 380 | 220
|  | HOWR2A | HOWW2A | 0 | 66.2 | Cable | 0.4924 | 1.6413 | 175.1469 | 380 | 220
|  | HOWA21 | HOWR2A | 0 | 104.9 | Cable | 0.69628 | 3.1955 | 303.8973 | 380 | 220
|  | HOWR2A | HOWW2B | 0 | 72.2 | Cable | 0.47736 | 1.7155 | 203.0972 | 380 | 220
|  | HOWA21 | HOWR2A | 0 | 104.7 | Cable | 0.6809 | 3.2601 | 291.07 | 380 | 220
|  | HOWR2A | HOWW2C | 0 | 85 | Cable | 0.63223 | 2.1074 | 224.8866 | 380 | 220
|  | HOWW2A | HOWW2B | 0 | 12.3 | Cable | 0.15756 | 0.30496 | 34.5997 | 364 | 220
|  | HOWW2B | HOWW2C | 0 | 13.9 | Cable | 0.17806 | 0.34463 | 39.1004 | 364 | 220
Breesea Limited | Hornsea Two Offshore Wind Farm | KILL41 | HOWB41 | 0 | 0.315 | Cable | 0.0002 | 0.004 | 3.7 | 935 | 400
|  | KILL41 | HOWB41 | 0 | 0.315 | Cable | 0.0002 | 0.004 | 3.7 | 935 | 400
|  | HOWB21 | HOWR2B | 0 | 103.7 | Cable | 0.59 | 2.69 | 338.42 | 415 | 220
|  | HOWR2B | HOWW2D | 0 | 60.2 | Cable | 0.4 | 1.5 | 165.42 | 412 | 220
|  | HOWB21 | HOWR2B | 0 | 103.55 | Cable | 0.59 | 2.69 | 337.97 | 415 | 220
|  | HOWR2B | HOWW2D | 0 | 61.6 | Cable | 0.42 | 1.52 | 169.26 | 412 | 220
|  | HOWB21 | HOWR2B | 0 | 103.4 | Cable | 0.59 | 2.69 | 382.85 | 415 | 220
|  | HOWR2B | HOWW2D | 0 | 62.2 | Cable | 0.42 | 1.54 | 170.9 | 412 | 220
Humber Gateway OFTO Limited | Humber Gateway Offshore Wind Farm | HUMO11 | HUMW11 | 0 | 39 | Cable | 1.417 | 3.447 | 46.189 | 121 | 132
|  | HUMO12 | HUMW12 | 0 | 39 | Cable | 1.417 | 3.447 | 46.189 | 121 | 132
|  | HUMO21 | HEDO21 | 0 | 0 | Cable | 0 | 0 | 0 | 121 | 132
|  | HUMO22 | HEDO21 | 0 | 0 | Cable | 0 | 0 | 0 | 121 | 132
TC Lincs OFTO Limited | Lincs Offshore Windfarm | LINO41 | WALP41 | 0 | 0.13 | Cable | 9.43e-05 | 0.001641 | 1.6336 | 492 | 400
|  | LINO11 | LINO13 | 0 | 0.129 | Cable | 0.000178 | 0.002903 | 1.4914 | 301 | 132
|  | LINO12 | LINO14 | 0 | 0.078 | Cable | 0.000108 | 0.001755 | 0.90176 | 301 | 132
|  | LINO13 | LINS11 | 0 | 60 | Cable | 2.0442 | 4.3446 | 69.5405 | 152 | 132
|  | LINO14 | LINS12 | 0 | 60 | Cable | 2.0442 | 4.3446 | 69.5405 | 152 | 132
Blue Transmission London Array Limited | London Array Offshore Wind Farm | CLEH41 | LONO4A | 0 | 0.08 | Cable | 0.00021 | 0.00052 | 0.76413 | 360 | 400
|  | CLEH41 | LONO4B | 0 | 0.13 | Cable | 0.00034125 | 0.000845 | 1.2417 | 360 | 400
|  | LONO11 | LOAW11 | 0 | 53.798 | Cable | 1.5829 | 2.9755 | 73.1044 | 167 | 150
|  | LONO12 | LOYW11 | 0 | 53.848 | Cable | 1.5837 | 2.9776 | 73.1539 | 167 | 150
|  | LONO13 | LOAW12 | 0 | 52.657 | Cable | 1.5488 | 2.9125 | 71.5816 | 167 | 150
|  | LONO14 | LOYW12 | 0 | 52.682 | Cable | 1.5492 | 2.9137 | 71.6099 | 167 | 150
Moray East Offshore Wind Limited | Moray East Offshore Wind Farm | MOWE21 | MORO21 | 0 | 90.69 | Cable | 0.632 | 2.405 | 284.21 | 312 | 220
|  | MOWE22 | MORO22 | 0 | 97.8 | Cable | 0.632 | 2.405 | 304.75 | 312 | 220
|  | MOWE23 | MORO23 | 0 | 91.48 | Cable | 0.632 | 2.405 | 286.49 | 312 | 220
|  | NEDE4K | MORF41 | 0 | 0.06 | Cable | 0.0027 | 0.001 | 0.27 | 398 | 275
|  | NEDE4K | MORF42 | 0 | 0.1 | Cable | 0.0043 | 0.002 | 0.42 | 398 | 275
|  | NEDE4K | MORF43 | 0 | 0.15 | Cable | 0.001 | 0.003 | 0.67 | 398 | 275
Ocean Winds Limited | Moray West Offshore Wind Farm | BLHI4- | MOWO4- | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999
|  | BLHI4- | MOWO41 | 0 | 3 | Cable | 0.0098 | 0.0323 | 22.7026 | 470 | 400
|  | BLHI4- | MOWO42 | 0 | 3 | Cable | 0.0098 | 0.0323 | 22.7026 | 470 | 400
|  | MOWO21 | MOWW21 | 0 | 29 | Cable | 0.10961 | 0.79111 | 133.6478 | 440 | 220
|  | MOWO22 | MOWW22 | 0 | 29 | Cable | 0.10961 | 0.79111 | 133.6478 | 440 | 220
|  | MOWW61 | MOWW63 | 0 | 49 | Cable | 0.3341 | 1.0428 | 175.8342 | 440 | 66
|  | MOWW62 | MOWW64 | 0 | 51 | Cable | 0.3477 | 1.0853 | 183.0111 | 440 | 66
NEART NA GAOITHE OFFSHORE WIND LIMITED | Neart na Gaoithe Offshore Wind Farm | CRYR4- | NNGO41 | 0 | 0.58 | Cable | 0.0015 | 0.0059 | 0 | 245 | 400
|  | CRYR4- | NNGO42 | 0 | 0.58 | Cable | 0.0015 | 0.0059 | 0 | 245 | 400
|  | NNGO21 | NNGW21 | 0 | 50.659 | Cable | 0.7591 | 1.4011 | 0.006 | 230 | 220
|  | NNGO22 | NNGW22 | 0 | 50.917 | Cable | 0.7592 | 1.4081 | 0.0006 | 230 | 220
TC Ormonde OFTO Limited | Ormonde Offshore Wind Farm | ORMO11 | ORMW11 | 0 | 44.3 | Cable | 0.7323 | 3.104 | 46.68 | 158 | 132
Diamond Transmission Partners RB Limited | Race Bank Offshore Wind Farm | RACW22 | RACO22 | 0 | 82.5 | Cable | 0.487 | 2.1111 | 247.8447 | 302 | 220
|  | RACW21 | RACO21 | 0 | 83.5 | Cable | 0.4934 | 2.1359 | 250.7489 | 302 | 220
|  | WALP41 | RACO41 | 0 | 0.1 | Cable | 0.0001 | 0.0011 | 0.8093 | 450 | 400
|  | WALP41 | RACO42 | 0 | 0.1 | Cable | 0.0001 | 0.0011 | 0.8093 | 450 | 400
|  | RACW21 | RACW22 | 0 | 6.7 | Cable | 0.0433 | 0.1661 | 19.4582 | 302 | 220
TC Rampion OFTO Limited | Rampion Offshore Wind Farm | BOLN41 | TWNE41 | 0 | 0.602 | Cable | 0.0028 | 0.0042 | 4.4179 | 411 | 400
|  | BOLN41 | TWNE42 | 0 | 0.764 | Cable | 0.0036 | 0.0053 | 5.6068 | 411 | 400
|  | TWNE11 | RAMW11 | 0 | 42.35 | Cable | 0.7285 | 1.9531 | 75.9552 | 210 | 150
|  | TWNE12 | RAMW12 | 0 | 42.29 | Cable | 0.7275 | 1.9502 | 75.842 | 210 | 150
TC Robin Rigg OFTO Limited | Robin Rigg East Offshore Wind Farm | RORE11 | RREW11 | 0 | 14.4 | Cable | 0.78 | 1.17 | 12.06 | 103 | 132
| Robin Rigg West Offshore Wind Farm | RORW11 | RRWW11 | 0 | 14.4 | Cable | 0.78 | 1.17 | 12.06 | 103 | 132
Sofia Offshore Wind Farm Limited | Sofia Offshore Wind Farm | LACK41 | LAZE41 | 0 | 2 | Cable | 0.0015 | 0.0168 | 24.23 | 744 | 400
|  | LACK42 | LAZE41 | 0 | 2 | Cable | 0.0015 | 0.0168 | 24.23 | 744 | 400
Seagreen Wind Energy Limited | Seagreen One Wind Farm | TEAL2K | SGRX21 | 0 | 0.228 | Cable | 0.000783 | 0.00464 | 1.18 | 419 | 275
|  | TEAL2K | SGRX22 | 0 | 0.183 | Cable | 0.000629 | 0.00373 | 0.95 | 419 | 275
|  | TEAL2K | SGRX23 | 0 | 0.738 | Cable | 0.00254 | 0.015 | 3.83 | 419 | 275
|  | SGRO21 | SGRW21 | 0 | 84.1 | Cable | 0.61407 | 2.1131 | 283.19 | 362 | 220
|  | SGRO22 | SGRW22 | 0 | 84.1 | Cable | 0.61407 | 2.1131 | 283.19 | 362 | 220
|  | SGRO22 | SGRW22 | 0 | 84.1 | Cable | 0.61407 | 2.1131 | 283.19 | 362 | 220
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SSAW11 | SALL11 | 0 | 44.8 | Cable | 1.0219 | 3.6202 | 55.2715 | 178 | 132
|  | SSBW11 | SALL12 | 0 | 42.9 | Cable | 0.9695 | 3.4676 | 53.1915 | 178 | 132
Thanet OFTO Limited | Thanet Offshore Wind Farm | THAW11 | THOW11 | 0 | 28.89 | Cable | 0.9305 | 1.9682 | 33.0484 | 155 | 132
|  | THAW12 | THOW12 | 0 | 28.89 | Cable | 0.9305 | 1.9682 | 33.0484 | 155 | 132
Triton Knoll Wind Farm Limited | Triton Knoll Offshore Wind Farm | TKNO22 | TKNW21 | 0 | 107.8 | Cable | 0.57 | 3.15 | 313 | 427 | 220
|  | TKNO21 | TKNE21 | 0 | 106.8 | Cable | 0.56 | 3.13 | 310 | 427 | 220
|  | BICF41 | TKNO41 | 0 | 2.01 | Cable | 0.004 | 0.02 | 18.6 | 505 | 400
|  | BICF41 | TKNO42 | 0 | 1.78 | Cable | 0.004 | 0.02 | 16.5 | 505 | 400
Diamond Transmission Partners Walney Extension Limited | Walney Extension Offshore Wind Farm | WOWE21 | WACW21 | 0 | 80.1 | Cable | 0.9432 | 1.99 | 251.59 | 347 | 220
|  | WADW21 | WACW21 | 0 | 22.9 | Cable | 0.4826 | 0.6719 | 50.0868 | 220 | 220
|  | WOWE22 | WADW21 | 0 | 66 | Cable | 0.7713 | 1.6434 | 207.5336 | 347 | 220
|  | MIDL41 | WOWE41 | 0 | 0.3 | Cable | 0.0015 | 0.0023 | 2.7143 | 470 | 400
|  | MIDL41 | WOWE42 | 0 | 0.3 | Cable | 0.0015 | 0.0023 | 2.7143 | 470 | 400
Blue Transmission Walney 1 OFTO Limited | Walney 1 Offshore Wind Farm | WAAO11 | WAAO1A | 0 | 2.9 | Cable | 0.076045 | 0.13688 | 3.5539 | 192 | 132
|  | WAAO1A | WAAW11 | 0 | 43.7 | Cable | 1.2943 | 2.3298 | 55.0577 | 164 | 132
Blue Transmission Walney 2 OFTO Limited | Walney 2 Offshore Wind Farm | WABO11 | WABO1A | 0 | 5.23 | Cable | 0.15 | 0.27 | 6.384 | 192 | 132
|  | WABO1A | WABW11 | 0 | 44.13 | Cable | 1.266 | 2.279 | 53.869 | 164 | 132
WoDS Transmission plc | West of Duddon Sands Offshore Wind Farm | WDSW11 | WDSO11 | 0 | 42.075 | Cable | 0.663 | 1.9978 | 69.3823 | 209 | 155
|  | WDSW12 | WDSO12 | 0 | 42.075 | Cable | 0.663 | 1.9978 | 69.3823 | 209 | 155
|  | HEYS41 | WDSO41 | 0 | 0.225 | Cable | 0.0004 | 0.0024 | 1.7417 | 346 | 400
|  | HEYS41 | WDSO42 | 0 | 0.225 | Cable | 0.0004 | 0.0024 | 1.7417 | 346 | 400
TC Westermost Rough OFTO Limited | Westermost Rough Offshore Wind Farm | WERO11 | WERW11 | 0 | 25.8335 | Cable | 0.2949 | 1.4823 | 45.7125 | 140 | 150
|  | HEDO21 | WERO21 | 0 | 0.368 | Cable | 0.003 | 0.0122 | 1.2704 | 256.7809 | 275
|  | HEDO21 | WERO22 | 0 | 0.329 | Cable | 0.0027 | 0.0109 | 1.1357 | 256.7809 | 275

## B-2-2a
B-2-2a - SHE Transmission Circuit Changes 2025/26 to 2035/36
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
CHAR1S | GLAG1Q | 2025 | Removed | 0.935 | 1.375 | Composite | 0.1697 | 0.3805 | 1.708 | 126 | 117 | 101 | 117
CHAR1S | GLAG1S | 2025 | Addition | 1.4 | 0 | OHL | 0.1274 | 0.3262 | 0.07 | 126 | 117 | 101 | 117
CHAR1T | GLAG1R | 2025 | Removed | 0.935 | 1.375 | Composite | 0.1697 | 0.3805 | 1.708 | 126 | 117 | 101 | 117
CHAR1T | GLAG1T | 2025 | Addition | 1.4 | 0 | OHL | 0.1274 | 0.3262 | 0.07 | 126 | 117 | 101 | 117
CLAY1Q | REDM1Q | 2025 | Change | 0 | 4.8 | Cable | 0.1402 | 0.4475 | 5.686 | 153 | 129 | 129 | 129
CLAY1R | REDM1R | 2025 | Change | 0 | 4.8 | Cable | 0.1402 | 0.4475 | 5.686 | 153 | 129 | 129 | 129
CONN1J | CONN1K | 2025 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CONN2K | DOUN2- | 2025 | Addition | 10.34 | 0 | OHL | 0.062 | 0.5688 | 2.193 | 702 | 665 | 599 | 665
CONN2K | GORW2- | 2025 | Addition | 47.76 | 0 | OHL | 0.2866 | 2.6272 | 10.127 | 702 | 665 | 599 | 665
CRSS1K | HICL1- | 2025 | Addition | 0 | 0.4 | Cable | 0.0072 | 0.056 | 0.48 | 158 | 146 | 146 | 146
DOUN1- | LIMK1A | 2025 | Addition | 0 | 0.9 | Cable | 0.01 | 0.058 | 1.389 | 306 | 253 | 253 | 253
DOUN2- | GORW2- | 2025 | Removed | 58.1 | 0 | OHL | 0.3486 | 3.196 | 12.32 | 702 | 665 | 599 | 665
GARB1Q | SLOY1K | 2025 | Change | 14.229 | 0.671 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230
GARB1R | SLOY1J | 2025 | Change | 14.185 | 0.715 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230
GARB1S | SLOY1J | 2025 | Change | 14.229 | 0.671 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230
GARB1T | SLOY1K | 2025 | Change | 14.185 | 0.715 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230
GLAG1Q | GLAG1S | 2025 | Addition | 0 | 2.25 | Cable | 0.0671 | 0.133 | 3.356 | 160 | 145 | 145 | 145
GLAG1R | GLAG1T | 2025 | Addition | 0 | 2.25 | Cable | 0.0671 | 0.133 | 3.356 | 160 | 145 | 145 | 145
GREM1J | GREM1L | 2025 | Addition | 0 | 3.83 | Cable | 0.02 | 0.305 | 6.898 | 272 | 272 | 250 | 272
GREM1K | GREM1N | 2025 | Addition | 0 | 1.72 | Cable | 0.0106 | 0.1372 | 3.098 | 272 | 272 | 272 | 272
GREM1L | GREM1P | 2025 | Addition | 2.3 | 0 | OHL | 0.115 | 0.4761 | 0.129 | 241 | 230 | 210 | 230
GREM1M | GREM1N | 2025 | Addition | 0 | 2.3 | Cable | 0.0141 | 0.1834 | 4.143 | 272 | 272 | 272 | 272
GREM1M | KERG1M | 2025 | Addition | 0 | 11.1 | OHL | 0.555 | 2.2977 | 0.622 | 203 | 193 | 176 | 193
GREM1P | GREM1Q | 2025 | Addition | 0 | 0.93 | Cable | 0.0057 | 0.0742 | 1.675 | 272 | 272 | 272 | 272
GREM1Q | KERG1L | 2025 | Addition | 0 | 7.94 | OHL | 0.397 | 1.6436 | 0.445 | 241 | 230 | 210 | 230
INRU1Q | PEHE1- | 2025 | Change | 6.7 | 0 | OHL | 0.3417 | 1.5008 | 0.348 | 241 | 230 | 210 | 230
INRU1R | PEHE1- | 2025 | Change | 6.7 | 0 | OHL | 0.3417 | 1.5008 | 0.348 | 241 | 230 | 210 | 230
KERG1J | KERG1L | 2025 | Addition | 0 | 5.85 | Cable | 0.0359 | 0.4662 | 10.53 | 272 | 272 | 272 | 272
KERG1K | KERG1M | 2025 | Addition | 0 | 5.85 | Cable | 0.0359 | 0.4662 | 10.53 | 272 | 272 | 272 | 272
LIMK1- | LIMK1A | 2025 | Addition | 4.9 | 0 | OHL | 0.245 | 1.014 | 0.652 | 203 | 193 | 176 | 193
ABED1- | DUNM1T | 2027 | Addition | 5 | 0 | OHL | 0.25 | 1.035 | 0.28 | 163 | 152 | 131 | 152
ACHE1- | SHIN1- | 2027 | Addition | 17.5 | 0 | OHL | 0.875 | 3.6225 | 0.98 | 203 | 193 | 176 | 193
AIGA1Q | KIOR1Q | 2027 | Removed | 2.797 | 0.123 | Composite | 0.264 | 0.594 | 0.66 | 111 | 103 | 89 | 103
AIGN1- | AIGN1A | 2027 | Addition | 0 | 0.43 | Cable | 0.0121 | 0.0381 | 0.569 | 149 | 137 | 137 | 137
AIGN1A | KION1A | 2027 | Addition | 2.92 | 0 | OHL | 0.264 | 0.594 | 0.66 | 111 | 103 | 89 | 103
ALYT2A | ALYT2B | 2027 | Removed | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ALYT2A | FETT2P | 2027 | Removed | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2A | KINB2J | 2027 | Removed | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT2B | FETT2Q | 2027 | Removed | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030
ALYT2B | KINB2K | 2027 | Removed | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030
ALYT4J | ALYT4K | 2027 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ALYT4J | FETT4R | 2027 | Addition | 67.06 | 0 | OHL | 0.1341 | 1.2799 | 41.079 | 2000 | 1920 | 1790 | 1920
ALYT4J | KINB4J | 2027 | Addition | 69.22 | 0 | OHL | 0.1384 | 1.311 | 42.688 | 2000 | 1920 | 1790 | 1920
ALYT4K | FETT4Q | 2027 | Addition | 67.06 | 0 | OHL | 0.1341 | 1.2799 | 41.079 | 2000 | 1920 | 1790 | 1920
ALYT4K | KINB4K | 2027 | Addition | 69.22 | 0 | OHL | 0.1384 | 1.311 | 42.688 | 2000 | 1920 | 1790 | 1920
BAGP2- | BAGP2J | 2027 | Addition | 0.25 | 0 | OHL | 0.01 | 0.0138 | 0.053 | 965 | 925 | 865 | 925
BAGP2- | BAGP2K | 2027 | Addition | 0.25 | 0 | OHL | 0.01 | 0.0138 | 0.053 | 965 | 925 | 865 | 925
BEAU1J | KION1B | 2027 | Addition | 1.5 | 0 | OHL | 0.0295 | 0.0433 | 1.175 | 251 | 252 | 252 | 252
BEAU1K | KION1A | 2027 | Addition | 1.5 | 0 | OHL | 0.0295 | 0.0433 | 1.175 | 251 | 252 | 252 | 252
BEAU1K | KIOR1Q | 2027 | Removed | 1.24 | 0.06 | Composite | 0.13 | 0.29 | 0.06 | 111 | 103 | 89 | 103
BEAU2J | FYRI2J | 2027 | Change | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 702 | 665 | 599 | 665
BEAU2K | FYRI2K | 2027 | Change | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 702 | 665 | 599 | 665
BERB2Q | CAID2- | 2027 | Addition | 7.99 | 0 | OHL | 0.0452 | 0.3288 | 2.178 | 935 | 880 | 790 | 880
BERB2Q | KNOC2J | 2027 | Removed | 46.98 | 0 | OHL | 0.266 | 1.934 | 12.809 | 935 | 880 | 790 | 880
BLEX1- | BLEX1B | 2027 | Addition | 0 | 3 | Cable | 0.0315 | 0.168 | 2.851 | 199 | 199 | 199 | 199
BLEX1A | BLEX1B | 2027 | Addition | 14.4 | 0 | OHL | 0.7191 | 3.2528 | 0.79 | 203 | 193 | 176 | 193
BLEX1A | FAUG1J | 2027 | Addition | 0 | 2.2 | Cable | 0.0231 | 0.1232 | 2.09 | 199 | 199 | 199 | 199
BLHI1J | ELCH1- | 2027 | Addition | 24 | 0 | OHL | 1.209 | 4.97 | 1.344 | 203 | 193 | 176 | 193
BLHI2J | CLGO2A | 2027 | Addition | 45.8 | 0 | OHL | 0.2593 | 1.8854 | 12.487 | 935 | 880 | 790 | 880
CAID2- | KNOC2J | 2027 | Addition | 0 | 38.99 | OHL | 0.2208 | 1.6052 | 10.631 | 935 | 880 | 790 | 880
CLGO2- | KNOC2K | 2027 | Addition | 0 | 47.45 | OHL | 0.2687 | 1.9535 | 12.938 | 935 | 880 | 790 | 880
CONN1D | CONN1K | 2027 | Addition | 0 | 0.66 | Cable | 0.0138 | 0.0553 | 0.905 | 200 | 178 | 178 | 178
CONN1D | STSO1A | 2027 | Addition | 12.2 | 0 | OHL | 0.6059 | 2.5084 | 0.6786 | 203 | 193 | 176 | 193
CONN2J | DOUN2- | 2027 | Change | 10.34 | 0 | OHL | 0.0621 | 0.5689 | 2.193 | 780 | 750 | 700 | 750
CONN2J | LOCB2J | 2027 | Change | 76.071 | 0.269 | Composite | 0.458 | 4.1987 | 16.184 | 780 | 750 | 700 | 750
CONN2K | DOUN2- | 2027 | Change | 10.34 | 0 | OHL | 0.0621 | 0.5689 | 2.193 | 780 | 750 | 700 | 750
CONN2K | GORW2- | 2027 | Change | 47.76 | 0 | OHL | 0.2866 | 2.6272 | 10.127 | 780 | 750 | 700 | 750
CRSS1K | HICL1- | 2027 | Addition | 0 | 0.4 | Cable | 0.0072 | 0.056 | 0.48 | 158 | 146 | 146 | 146
CULL1A | CULL1Q | 2027 | Addition | 0 | 0.43 | Cable | 0.0046 | 0.0274 | 0.664 | 149 | 137 | 137 | 137
CULL1Q | DEAN1Q | 2027 | Removed | 0 | 9 | Cable | 0.93 | 2.12 | 0.45 | 111 | 103 | 89 | 103
CULL1Q | DEAW1A | 2027 | Addition | 9 | 0 | OHL | 0.93 | 2.12 | 0.45 | 111 | 103 | 89 | 103
CULL1Q | KION1B | 2027 | Addition | 12.6 | 0 | OHL | 1.287 | 2.952 | 0.621 | 111 | 103 | 89 | 103
DAAS2- | KNOC2K | 2027 | Removed | 60.22 | 0 | OHL | 0.341 | 2.479 | 16.419 | 935 | 880 | 790 | 880
DEAW1- | DEAW1A | 2027 | Addition | 0 | 3.8 | Cable | 0.1067 | 0.3362 | 5.031 | 149 | 137 | 137 | 137
DELL1- | DELL1B | 2027 | Addition | 0 | 7.4 | Cable | 0.1902 | 0.4122 | 5.212 | 127 | 127 | 127 | 127
DELL1A | DELL1B | 2027 | Addition | 7.2 | 0 | OHL | 0.2304 | 1.5696 | 0.382 | 280 | 270 | 245 | 270
DELL1A | MELG1K | 2027 | Addition | 0 | 0.7 | Cable | 0.018 | 0.039 | 0.493 | 127 | 127 | 127 | 127
DLCH1B | LAIS1A | 2027 | Addition | 3.7 | 0 | OHL | 0.0869 | 0.8073 | 0.195 | 464 | 446 | 414 | 446
DLCH1B | LOCB1M | 2027 | Removed | 17 | 0 | OHL | 0.3992 | 3.7085 | 0.898 | 464 | 446 | 414 | 446
DOUN1- | OWFD1- | 2027 | Addition | 0 | 1 | Cable | 0.0206 | 0.0849 | 1.349 | 190 | 147 | 147 | 147
DOUN2- | BAGP2J | 2027 | Addition | 5 | 0 | OHL | 0.025 | 0.275 | 1.065 | 965 | 925 | 865 | 925
DOUN2- | THUS2J | 2027 | Removed | 15.4 | 0 | OHL | 0.077 | 0.847 | 3.28 | 965 | 925 | 865 | 925
DUDH1Q | GLAG1Q | 2027 | Removed | 0 | 1.95 | Cable | 0.0585 | 0.1151 | 2.73 | 124 | 114 | 114 | 114
DUDH1Q | MILC1R | 2027 | Removed | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113
DUDH1R | GLAG1R | 2027 | Removed | 0 | 1.95 | Cable | 0.0585 | 0.1151 | 2.73 | 124 | 114 | 114 | 114
DUDH1R | MILC1V | 2027 | Removed | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113
DUNO1Q | WHTB1S | 2027 | Change | 18.1 | 0 | OHL | 0.9231 | 4.1087 | 0.923 | 241 | 230 | 210 | 230
DUNO1R | WHTB1T | 2027 | Change | 18.1 | 0 | OHL | 0.9231 | 4.1087 | 0.923 | 241 | 230 | 210 | 230
FETT2P | FETT2R | 2027 | Removed | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT2P | KINT2K | 2027 | Removed | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
FETT2Q | FETT2R | 2027 | Removed | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT2Q | KINT2K | 2027 | Removed | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030
FETT4J | FETT4Q | 2027 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT4J | FETT4R | 2027 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT4Q | KINT4J | 2027 | Addition | 0 | 32.19 | Cable | 0.0644 | 0.6052 | 19.977 | 2000 | 1920 | 1790 | 1920
FETT4R | KINT4K | 2027 | Addition | 0 | 32.19 | Cable | 0.0644 | 0.6052 | 19.977 | 2000 | 1920 | 1790 | 1920
FOYE2- | FOYE2J | 2027 | Change | 0 | 0.8 | Cable | 0.0053 | 0.0152 | 3.23 | 319 | 319 | 319 | 319
FYRI2J | LOCB2K | 2027 | Change | 35.93 | 0 | OHL | 0.2156 | 1.9762 | 7.617 | 780 | 750 | 700 | 750
FYRI2K | LOCB2J | 2027 | Change | 35.93 | 0 | OHL | 0.2156 | 1.9762 | 7.617 | 780 | 750 | 700 | 750
GILB1J | GILB1K | 2027 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
GILB1J | GILB1L | 2027 | Addition | 0 | 7.06 | Cable | 0.0419 | 0.5395 | 12.655 | 348 | 348 | 348 | 348
GILB1J | MEYG1- | 2027 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
GILB1K | GILB1M | 2027 | Addition | 0 | 7.06 | Cable | 0.0419 | 0.5395 | 12.655 | 348 | 348 | 348 | 348
GILB1L | THUS1L | 2027 | Addition | 13.1 | 0 | OHL | 0.303 | 2.776 | 0.72 | 463 | 444 | 415 | 444
GILB1M | THUS1M | 2027 | Addition | 13.1 | 0 | OHL | 0.303 | 2.776 | 0.72 | 463 | 444 | 415 | 444
GLAG1Q | STNG1D | 2027 | Addition | 0 | 2.21 | Cable | 0.0663 | 0.1304 | 3.094 | 124 | 114 | 114 | 114
GLAG1R | STNG1C | 2027 | Addition | 0 | 2.21 | Cable | 0.0663 | 0.1304 | 3.094 | 124 | 114 | 114 | 114
GORW2- | STRB2- | 2027 | Change | 10.3 | 0 | OHL | 0.0618 | 0.5665 | 2.184 | 780 | 750 | 700 | 750
KINT4J | FETT4Q | 2027 | Addition | 32.19 | 0 | OHL | 0.0644 | 0.6052 | 19.977 | 2000 | 1920 | 1790 | 1920
KINT4J | KINT4K | 2027 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINT4K | FETT4R | 2027 | Addition | 32.19 | 0 | OHL | 0.0644 | 0.6052 | 19.977 | 2000 | 1920 | 1790 | 1920
KION1- | KION1A | 2027 | Addition | 0 | 0.28 | Cable | 0.0079 | 0.0248 | 0.371 | 149 | 137 | 137 | 137
LAIS1A | LAIS1B | 2027 | Addition | 1.6 | 0 | OHL | 0.1456 | 0.3456 | 0.0864 | 111 | 103 | 89 | 103
LAIS1A | LOCB1M | 2027 | Addition | 13.3 | 0 | OHL | 0.3123 | 2.9012 | 0.703 | 464 | 446 | 414 | 446
LOCB2K | STRB2- | 2027 | Change | 18.9 | 0 | OHL | 0.1134 | 1.0395 | 4.007 | 780 | 750 | 700 | 750
MILC1R | STNG1B | 2027 | Addition | 0 | 1.53 | Cable | 0.0813 | 0.1409 | 1.691 | 131 | 113 | 113 | 113
MILC1V | STNG1A | 2027 | Addition | 0 | 1.53 | Cable | 0.0813 | 0.1409 | 1.691 | 131 | 113 | 113 | 113
STNG1A | STNG1E | 2027 | Addition | 0 | 0.63 | Cable | 0.0189 | 0.0372 | 0.882 | 160 | 145 | 145 | 145
STNG1B | STNG1E | 2027 | Addition | 0 | 0.63 | Cable | 0.0189 | 0.0372 | 0.882 | 160 | 145 | 145 | 145
STNG1C | STNG1E | 2027 | Addition | 0 | 0.81 | Cable | 0.0243 | 0.0478 | 1.134 | 160 | 145 | 145 | 145
STNG1D | STNG1E | 2027 | Addition | 0 | 0.81 | Cable | 0.0243 | 0.0478 | 1.134 | 160 | 145 | 145 | 145
STRW1A | STWO1- | 2027 | Addition | 0 | 5 | Cable | 0.455 | 1.08 | 0.27 | 126 | 119 | 108 | 119
STSO1A | STSO1B | 2027 | Addition | 0 | 0.27 | Cable | 0.0056 | 0.0226 | 0.37 | 200 | 178 | 178 | 178
THUS1J | THUS1L | 2027 | Addition | 0 | 3.03 | Cable | 0.018 | 0.2316 | 5.431 | 348 | 348 | 348 | 348
THUS1K | THUS1M | 2027 | Addition | 0 | 3.03 | Cable | 0.018 | 0.2316 | 5.431 | 348 | 348 | 348 | 348
THUS2J | BAGP2K | 2027 | Addition | 10.4 | 0 | OHL | 0.052 | 0.572 | 2.215 | 965 | 925 | 865 | 925
WIOW1- | WIOW1Q | 2027 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
WIOW1- | WIOW1R | 2027 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ALYT4J | ASBS4B | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ANSN2- | CRDH2J | 2029 | Addition | 20.25 | 0 | OHL | 0.081 | 0.8303 | 5.711 | 1540 | 1480 | 1380 | 1480
ANSN2- | CRMU2J | 2029 | Addition | 24.95 | 0 | OHL | 0.0998 | 1.023 | 7.036 | 1540 | 1480 | 1380 | 1480
ANSN2- | ERED2- | 2029 | Addition | 0 | 0.6 | Cable | 0.0016 | 0.011 | 3.435 | 580 | 546 | 546 | 546
ANSU1- | INVE1K | 2029 | Removed | 11.35 | 0 | OHL | 0.1816 | 2.009 | 0.738 | 739 | 710 | 662 | 710
ANSU1- | PORA1R | 2029 | Removed | 24.95 | 0 | OHL | 0.3992 | 4.4162 | 1.622 | 739 | 710 | 662 | 710
ARMA1- | STCS1B | 2029 | Addition | 15 | 0 | OHL | 0.49 | 2.0286 | 0.549 | 203 | 193 | 176 | 193
ARMO1J | DUGR1Q | 2029 | Change | 14 | 0 | OHL | 0.7 | 2.898 | 0.784 | 203 | 193 | 176 | 193
BANN4J | BANN4K | 2029 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BANN4J | OWPL4- | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BEAU2J | FASN2- | 2029 | Removed | 24.288 | 1.012 | Composite | 0.069 | 1.025 | 7.23 | 1910 | 1830 | 1710 | 1830
BEAU4- | BING4- | 2029 | Addition | 25.3 | 0 | OHL | 0.0328 | 0.4847 | 15.298 | 2780 | 2670 | 2480 | 2670
BEWF1- | SYEL1- | 2029 | Addition | 0 | 1.5 | Cable | 0.0315 | 0.1265 | 2.054 | 206 | 206 | 206 | 206
BING4- | FAUG4K | 2029 | Addition | 25.4 | 0 | OHL | 0.0329 | 0.4866 | 15.358 | 2780 | 2670 | 2480 | 2670
BLGH1- | CRDH1J | 2029 | Addition | 0 | 10 | Cable | 0.91 | 2.16 | 0.54 | 126 | 119 | 108 | 119
BLHI2A | BLHI2J | 2029 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI2A | CLGO2A | 2029 | Addition | 45.8 | 0 | OHL | 0.2593 | 1.8854 | 12.487 | 935 | 880 | 790 | 880
BLHI2B | BLHI2K | 2029 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BLHI2B | DAAS2- | 2029 | Addition | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880
BLHI2J | CLGO2A | 2029 | Removed | 45.8 | 0 | OHL | 0.2593 | 1.8854 | 12.487 | 935 | 880 | 790 | 880
BLHI2K | DAAS2- | 2029 | Removed | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880
BONB2J | BRCW2K | 2029 | Removed | 10.1 | 0 | OHL | 0.028 | 0.409 | 2.886 | 1910 | 1830 | 1710 | 1830
BONB4A | CMBS4B | 2029 | Addition | 10.1 | 0 | OHL | 0.0131 | 0.1935 | 6.107 | 2780 | 2670 | 2480 | 2670
BRCW2J | BRCW2K | 2029 | Removed | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BRCW2J | KINA2K | 2029 | Removed | 59.8 | 0 | OHL | 0.1638 | 2.4224 | 17.089 | 1910 | 1830 | 1710 | 1830
BREC1Q | FASQ1- | 2029 | Addition | 0 | 4 | Cable | 0.065 | 0.334 | 6.245 | 176 | 176 | 176 | 176
BROA1- | BROA1J | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BROA1- | BROA1K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BROA1A | BROA1J | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BROA1A | QUOI1Q | 2029 | Addition | 63 | 0 | OHL | 1.4888 | 13.3653 | 3.474 | 465 | 445 | 415 | 445
BROA1B | BROA1K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BROA1B | FAUG1S | 2029 | Addition | 82 | 0 | OHL | 1.9378 | 17.3962 | 4.522 | 465 | 445 | 415 | 445
BROA1C | BROA1J | 2029 | Addition | 7.75 | 0 | OHL | 0.1831 | 1.6441 | 0.427 | 465 | 445 | 415 | 445
BROA1C | EDIN1C | 2029 | Addition | 0 | 15 | Cable | 0.1481 | 1.2148 | 27.585 | 207 | 207 | 207 | 207
BROA1C | EDIN1C | 2029 | Addition | 0 | 15 | Cable | 0.1481 | 1.2148 | 27.585 | 207 | 207 | 207 | 207
BROA1D | BROA1K | 2029 | Addition | 7.75 | 0 | OHL | 0.1831 | 1.6441 | 0.427 | 465 | 445 | 415 | 445
BROA1D | EDIN1D | 2029 | Addition | 0 | 15 | Cable | 0.1481 | 1.2148 | 27.585 | 207 | 207 | 207 | 207
BROA1D | EDIN1D | 2029 | Addition | 0 | 15 | Cable | 0.1481 | 1.2148 | 27.585 | 207 | 207 | 207 | 207
BROA1J | BROA1K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BROA1Q | EDIN1- | 2029 | Removed | 44.9 | 0 | OHL | 6.014 | 9.963 | 2.332 | 99 | 92 | 79 | 92
BROA1Q | QUOI1Q | 2029 | Removed | 63.4 | 0 | OHL | 8.99 | 14.87 | 3.11 | 99 | 92 | 79 | 92
CAAD1Q | CRSS1J | 2029 | Removed | 13.08 | 0 | OHL | 0.3091 | 2.7749 | 0.721 | 448 | 430 | 398 | 430
CAAD1Q | TNGF1- | 2029 | Addition | 1 | 0 | OHL | 0.0236 | 0.2121 | 0.055 | 448 | 430 | 398 | 430
CHLS1- | DLCH1A | 2029 | Addition | 10.5 | 0 | OHL | 0.525 | 2.1735 | 0.588 | 203 | 193 | 176 | 193
CLOI1A | MELG1K | 2029 | Addition | 0 | 0.7 | Cable | 0.0093 | 0.0536 | 0.95 | 220 | 211 | 211 | 211
CLUN1S | ERRO1K | 2029 | Change | 15.4 | 0 | OHL | 0.7801 | 3.4546 | 0.795 | 241 | 230 | 210 | 230
CLUN1T | ERRO1J | 2029 | Change | 15.4 | 0 | OHL | 0.7801 | 3.4546 | 0.795 | 241 | 230 | 210 | 230
CMBS4A | CMBS4B | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CMBS4A | KINA4B | 2029 | Addition | 59.8 | 0 | OHL | 0.0775 | 1.1456 | 36.158 | 2780 | 2670 | 2480 | 2670
COGL4J | LOCL4J | 2029 | Addition | 3.5 | 0 | OHL | 0.0045 | 0.067 | 2.116 | 2780 | 2670 | 2480 | 2670
COGL4K | LOCL4K | 2029 | Addition | 3.5 | 0 | OHL | 0.0045 | 0.067 | 2.116 | 2780 | 2670 | 2480 | 2670
CONN1C | CONN1J | 2029 | Removed | 0 | 0.76 | Cable | 0.0161 | 0.0631 | 1.035 | 200 | 178 | 178 | 178
CONN1C | STRW1A | 2029 | Removed | 12 | 0 | OHL | 0.605 | 2.485 | 0.672 | 203 | 193 | 176 | 193
CONN1D | CONN1K | 2029 | Removed | 0 | 0.66 | Cable | 0.0138 | 0.0553 | 0.905 | 200 | 178 | 178 | 178
CONN1D | STSO1A | 2029 | Removed | 12.12 | 0 | OHL | 0.6109 | 2.5094 | 0.679 | 203 | 193 | 176 | 193
CONN1J | STCS1A | 2029 | Addition | 11 | 0 | OHL | 0.2159 | 1.9817 | 0.689 | 335 | 320 | 290 | 320
CONN1K | KRKN1- | 2029 | Addition | 2 | 0 | OHL | 0.1 | 0.414 | 0.112 | 203 | 193 | 176 | 193
CONN1K | STCS1B | 2029 | Addition | 11 | 0 | OHL | 0.2159 | 1.9817 | 0.689 | 335 | 320 | 290 | 320
COST1- | COST1A | 2029 | Addition | 0 | 2.6 | Cable | 0.0346 | 0.1992 | 4.3 | 292 | 292 | 292 | 292
COST1A | ELIB1- | 2029 | Addition | 0 | 11.5 | Cable | 0.575 | 2.3805 | 0.644 | 292 | 292 | 292 | 292
CRAR1R | INVE1J | 2029 | Removed | 22.58 | 0 | OHL | 0.3613 | 3.9967 | 1.468 | 739 | 710 | 662 | 710
CRAR1R | PORA1S | 2029 | Removed | 13.72 | 0 | OHL | 0.2195 | 2.4284 | 0.892 | 739 | 710 | 662 | 710
CRAS2- | CRDH2K | 2029 | Addition | 31.48 | 0 | OHL | 0.1259 | 1.2907 | 8.877 | 1540 | 1480 | 1380 | 1480
CRAS2- | CRMU2K | 2029 | Addition | 13.72 | 0 | OHL | 0.0549 | 0.5625 | 3.869 | 1540 | 1480 | 1380 | 1480
CRDH1J | CRDH1K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRDH1J | KILC1Q | 2029 | Addition | 4.98 | 0 | OHL | 0.7095 | 1.1715 | 0.244 | 99 | 92 | 79 | 92
CRDH1K | FERO1S | 2029 | Addition | 5.02 | 0 | OHL | 0.7118 | 1.1784 | 0.246 | 99 | 92 | 79 | 92
CRDH2J | CRDH2K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRDH2J | DALB2A | 2029 | Addition | 14 | 0 | OHL | 0.0516 | 0.5615 | 3.962 | 1540 | 1480 | 1380 | 1480
CRDH2K | DALB2B | 2029 | Addition | 14 | 0 | OHL | 0.0516 | 0.5615 | 3.962 | 1540 | 1480 | 1380 | 1480
CRMU2J | ANSN2- | 2029 | Addition | 24.95 | 0 | OHL | 0.0998 | 1.023 | 7.036 | 1540 | 1480 | 1380 | 1480
CRMU2J | CRMU2K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRMU2J | CRSN2Q | 2029 | Addition | 44.7 | 0 | OHL | 0.1788 | 1.8327 | 12.605 | 1540 | 1480 | 1380 | 1480
CRMU2K | EARR21 | 2029 | Addition | 28.34 | 0 | OHL | 0.1134 | 1.1621 | 7.993 | 1540 | 1480 | 1380 | 1480
CRSN1Q | CRSN1R | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRSN1Q | CRSS1J | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRSN1R | CRSS1K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRSN2Q | CRSN2R | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CRSN2R | EARR2A | 2029 | Addition | 16.36 | 0 | OHL | 0.0654 | 0.6706 | 4.612 | 1540 | 1480 | 1380 | 1480
CRSS1J | TNGF1- | 2029 | Addition | 12.08 | 0 | OHL | 0.2855 | 2.5628 | 0.666 | 448 | 430 | 398 | 430
CRSS1Q | PORA1R | 2029 | Removed | 44.7 | 0 | OHL | 0.7152 | 7.9119 | 2.905 | 739 | 710 | 662 | 710
CRSS1R | PORA1S | 2029 | Removed | 44.7 | 0 | OHL | 0.7152 | 7.9119 | 2.905 | 739 | 710 | 662 | 710
DOUN2A | DOUN2B | 2029 | Addition | 0 | 0.79 | Cable | 0.0048 | 0.0255 | 2.87 | 292 | 292 | 292 | 292
DOUN2B | DOUN2C | 2029 | Addition | 0 | 1.85 | Cable | 0.0141 | 0.0459 | 5.201 | 294 | 294 | 294 | 294
DOUN2C | FINS2C | 2029 | Addition | 0 | 48.3 | Cable | 0.5558 | 1.3971 | 104.968 | 231 | 231 | 231 | 231
DUGR1Q | EDIN1- | 2029 | Removed | 9 | 0 | OHL | 1.206 | 1.997 | 0.468 | 99 | 92 | 79 | 92
DUGR1Q | EDIN1J | 2029 | Addition | 9.5 | 0 | OHL | 0.475 | 1.9665 | 0.532 | 203 | 193 | 176 | 193
EARR21 | EARR2B | 2029 | Addition | 5.6 | 0 | OHL | 0.0224 | 0.2296 | 1.579 | 1540 | 1480 | 1380 | 1480
EARR2A | EARR2B | 2029 | Addition | 5.6 | 0 | OHL | 0.0224 | 0.2296 | 1.579 | 1540 | 1480 | 1380 | 1480
EDIN1A | EDIN1C | 2029 | Addition | 20.25 | 0 | OHL | 0.4785 | 4.296 | 1.117 | 465 | 445 | 415 | 445
EDIN1A | EDIN1J | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
EDIN1B | EDIN1D | 2029 | Addition | 20.25 | 0 | OHL | 0.4785 | 4.296 | 1.117 | 465 | 445 | 415 | 445
EDIN1B | EDIN1K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
EDIN1J | EDIN1K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
EDIN1J | GLUE1- | 2029 | Addition | 0 | 2.8 | Cable | 0.0166 | 0.214 | 5.019 | 348 | 348 | 348 | 348
EDIN1K | EDIN1J | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
EDIN1K | GLNU1- | 2029 | Addition | 0.5 | 0 | OHL | 0.0118 | 0.1061 | 0.028 | 448 | 430 | 398 | 430
ELIB1- | ELIB1A | 2029 | Addition | 7.5 | 0 | OHL | 0.375 | 1.5525 | 0.42 | 241 | 230 | 210 | 230
ELIB1A | FINS1- | 2029 | Addition | 0 | 3.1 | Cable | 0.0502 | 0.318 | 4.584 | 208 | 187 | 187 | 187
ENEI1- | ENEI1N | 2029 | Addition | 0 | 1 | Cable | 0.0133 | 0.0766 | 1.654 | 250 | 250 | 250 | 250
ENEI1N | SYEL1N | 2029 | Addition | 18 | 0 | OHL | 0.9 | 3.726 | 1.008 | 203 | 193 | 176 | 193
FASN1A | FASN1B | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FASN2- | FAUG2J | 2029 | Removed | 24.384 | 1.016 | Composite | 0.069 | 1.029 | 7.259 | 1910 | 1830 | 1710 | 1830
FASQ1- | FASQ1J | 2029 | Addition | 10 | 0 | OHL | 1 | 4.14 | 1.12 | 203 | 193 | 176 | 193
FAUG1- | FAUG1M | 2029 | Removed | 0 | 0.25 | Cable | 0.0028 | 0.0145 | 0.45 | 319 | 295 | 295 | 295
FAUG1- | FAUG1N | 2029 | Removed | 0 | 0.17 | Cable | 0.0018 | 0.0097 | 0.302 | 319 | 297 | 297 | 297
FAUG1- | FAUG1P | 2029 | Removed | 0 | 0.54 | Cable | 0.0088 | 0.0486 | 0.801 | 230 | 218 | 218 | 218
FAUG1- | FAUG1R | 2029 | Addition | 0 | 9 | Cable | 0.0889 | 0.7289 | 16.551 | 207 | 207 | 207 | 207
FAUG1- | FAUG1R | 2029 | Addition | 0 | 9 | Cable | 0.0889 | 0.7289 | 16.551 | 207 | 207 | 207 | 207
FAUG1- | FAUG1S | 2029 | Addition | 0 | 9 | Cable | 0.0889 | 0.7289 | 16.551 | 207 | 207 | 207 | 207
FAUG1- | FAUG1S | 2029 | Addition | 0 | 9 | Cable | 0.0889 | 0.7289 | 16.551 | 207 | 207 | 207 | 207
FAUG1M | LOCL1Q | 2029 | Removed | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG1N | LOCL1R | 2029 | Removed | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247
FAUG1P | QUOI1Q | 2029 | Removed | 28.2 | 0 | OHL | 1.41 | 5.8391 | 1.576 | 203 | 193 | 176 | 193
FAUG1R | QUOI1Q | 2029 | Addition | 19 | 0 | OHL | 0.449 | 4.0308 | 1.048 | 465 | 445 | 415 | 445
FAUG2J | FAUG2K | 2029 | Removed | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FAUG2K | TUMM2J | 2029 | Removed | 77.2 | 0 | OHL | 0.211 | 3.128 | 22.063 | 1910 | 1830 | 1710 | 1830
FAUG4J | LOCL4K | 2029 | Addition | 8.5 | 0 | OHL | 0.0109 | 0.1627 | 5.139 | 2780 | 2670 | 2480 | 2670
FAUG4K | KINA4A | 2029 | Addition | 80.2 | 0 | OHL | 0.104 | 1.5363 | 48.493 | 2780 | 2670 | 2480 | 2670
FAUG4K | LOCL4J | 2029 | Addition | 8.5 | 0 | OHL | 0.0109 | 0.1627 | 5.139 | 2780 | 2670 | 2480 | 2670
FERO1S | INVE1J | 2029 | Removed | 15.21 | 0 | OHL | 2.157 | 3.571 | 0.744 | 99 | 92 | 79 | 92
FETT1- | GLDY1- | 2029 | Addition | 19 | 0 | OHL | 0.9488 | 4.2918 | 1.068 | 203 | 193 | 176 | 193
FETT4J | FETT4K | 2029 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 100 | 100 | 100 | 100
FETT4J | FETT4R | 2029 | Removed | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FETT4K | FETT4R | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FINS2A | FINS2B | 2029 | Addition | 0 | 13.61 | Cable | 0.0827 | 0.4387 | 49.435 | 292 | 292 | 292 | 292
FINS2B | FINS2C | 2029 | Addition | 0 | 2.2 | Cable | 0.0167 | 0.0545 | 6.185 | 294 | 294 | 294 | 294
FWIL1Q | LOCL1K | 2029 | Addition | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1Q | LOCL1Q | 2029 | Removed | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1R | LOCL1K | 2029 | Addition | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
FWIL1R | LOCL1R | 2029 | Removed | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247
GILB1J | SLCK1- | 2029 | Addition | 7.5 | 0 | OHL | 0.375 | 1.5525 | 0.42 | 203 | 193 | 176 | 193
GRNV4- | NEDE4J | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
INGA1Q | LOCL1K | 2029 | Addition | 2.4 | 0 | OHL | 0.2184 | 0.5592 | 0.12 | 111 | 103 | 89 | 103
INGA1Q | LOCL1Q | 2029 | Removed | 2.4 | 0 | OHL | 0.2184 | 0.5592 | 0.12 | 111 | 103 | 89 | 103
INRU1Q | SALM1A | 2029 | Addition | 3.05 | 0 | OHL | 0.1555 | 0.6832 | 0.158 | 241 | 230 | 210 | 230
INRU1Q | SFER1L | 2029 | Removed | 6.1 | 0 | OHL | 0.3111 | 1.3664 | 0.317 | 241 | 230 | 210 | 230
INRU1R | SALM1B | 2029 | Addition | 3.05 | 0 | OHL | 0.1555 | 0.6832 | 0.158 | 241 | 230 | 210 | 230
INRU1R | SFER1M | 2029 | Removed | 6.1 | 0 | OHL | 0.3111 | 1.3664 | 0.317 | 241 | 230 | 210 | 230
INVE1K | KILC1Q | 2029 | Removed | 15.1 | 0 | OHL | 2.15 | 3.55 | 0.74 | 99 | 92 | 79 | 92
KERG1A | KERG1W | 2029 | Addition | 0 | 4 | Cable | 0.0246 | 0.319 | 7.205 | 272 | 272 | 272 | 272
KERG1A | SYEL1A | 2029 | Addition | 0 | 12 | Cable | 0.4007 | 0.7573 | 16.422 | 189 | 189 | 189 | 189
KERG1B | KERG1W | 2029 | Addition | 0 | 4 | Cable | 0.0246 | 0.319 | 7.205 | 272 | 272 | 272 | 272
KERG1B | SYEL1B | 2029 | Addition | 0 | 12 | Cable | 0.4007 | 0.7573 | 16.422 | 189 | 189 | 189 | 189
KERG1K | KERG1N | 2029 | Addition | 0 | 0.35 | Cable | 0.0021 | 0.0279 | 0.63 | 272 | 272 | 272 | 272
KERG1N | KERG1U | 2029 | Addition | 0 | 3 | Cable | 0.1551 | 0.651 | 0.158 | 295 | 295 | 295 | 295
KERG1U | KERG1V | 2029 | Addition | 0 | 2 | Cable | 0.0123 | 0.1595 | 3.602 | 272 | 272 | 272 | 272
KERG1V | KERG1W | 2029 | Addition | 0 | 12.5 | Cable | 0.6463 | 2.7125 | 0.659 | 295 | 295 | 295 | 295
KILC1Q | CRDH1J | 2029 | Addition | 4.98 | 0 | OHL | 0.7095 | 1.1715 | 0.244 | 99 | 92 | 79 | 92
KINA2J | KINA2K | 2029 | Removed | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINA2J | TUMM2K | 2029 | Removed | 3 | 0 | OHL | 0.01 | 0.1216 | 0.858 | 1910 | 1830 | 1710 | 1830
KINA4A | KINA4B | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINM2A | KINM2C | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINM2A | PEHE2- | 2029 | Addition | 23.8 | 0 | OHL | 0.12 | 1.04 | 6.26 | 1090 | 1030 | 920 | 1030
KINM2B | KINM2C | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINM2B | PERS2Q | 2029 | Addition | 23.8 | 0 | OHL | 0.12 | 1.04 | 6.26 | 1090 | 1030 | 920 | 1030
LOCL1J | LOCL1K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOCL4J | LOCL4K | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHE2- | PERS2Q | 2029 | Removed | 47.6 | 0 | OHL | 0.24 | 2.08 | 12.52 | 1090 | 1030 | 920 | 1030
PEHE4J | PEHE4L | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PORA1R | PORA1T | 2029 | Removed | 6.14 | 0 | OHL | 0.8535 | 1.3692 | 0.301 | 99 | 92 | 79 | 92
PORA1S | PORA1U | 2029 | Removed | 6.14 | 0 | OHL | 0.8535 | 1.3692 | 0.301 | 99 | 92 | 79 | 92
PORA1T | PORA1U | 2029 | Removed | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SALM1A | SALM1C | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SALM1A | SFER1L | 2029 | Addition | 3.05 | 0 | OHL | 0.1555 | 0.6832 | 0.158 | 241 | 230 | 210 | 230
SALM1B | SALM1C | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SALM1B | SFER1M | 2029 | Addition | 3.05 | 0 | OHL | 0.1555 | 0.6832 | 0.158 | 241 | 230 | 210 | 230
STCS1A | STCS1B | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
STCS1A | STRW1A | 2029 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
STCS1B | STSO1A | 2029 | Addition | 0 | 6 | Cable | 0.1181 | 0.1733 | 4.7 | 251 | 252 | 252 | 252
SYEL1- | SYEL1M | 2029 | Addition | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
SYEL1- | SYEL1N | 2029 | Addition | 0 | 2.5 | Cable | 0.0333 | 0.1915 | 4.135 | 250 | 250 | 250 | 250
SYEL1A | SYEL1M | 2029 | Addition | 0 | 2 | Cable | 0.0123 | 0.1595 | 3.602 | 272 | 272 | 272 | 272
SYEL1B | SYEL1M | 2029 | Addition | 0 | 2 | Cable | 0.0123 | 0.1595 | 3.602 | 272 | 272 | 272 | 272
TNGF1- | TNGF1A | 2029 | Addition | 21.5 | 0 | OHL | 1.075 | 4.4505 | 1.204 | 203 | 193 | 176 | 193
TUMM2J | TUMM2K | 2029 | Removed | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
ALYT2A | TEAL2J | 2032 | Removed | 16.2 | 0 | OHL | 0.0685 | 0.6615 | 4.505 | 1090 | 1030 | 925 | 1030
ALYT2B | TEAL2K | 2032 | Removed | 16.2 | 0 | OHL | 0.0685 | 0.6615 | 4.505 | 1090 | 1030 | 925 | 1030
ALYT4J | EMMO4K | 2032 | Addition | 16.2 | 0 | OHL | 0.0324 | 0.3078 | 10.417 | 2349 | 2266 | 2120 | 2266
ALYT4J | FETT4R | 2032 | Change | 67.06 | 0 | OHL | 0.1341 | 1.2741 | 41.1751 | 2349 | 2266 | 2120 | 2266
ALYT4J | KINB4J | 2032 | Change | 69.22 | 0 | OHL | 0.1384 | 1.3152 | 42.501 | 2349 | 2266 | 2120 | 2266
ALYT4K | EMMO4J | 2032 | Addition | 16.2 | 0 | OHL | 0.0324 | 0.3078 | 10.417 | 2349 | 2266 | 2120 | 2266
ALYT4K | FETT4Q | 2032 | Change | 67.06 | 0 | OHL | 0.1341 | 1.2741 | 41.1751 | 2349 | 2266 | 2120 | 2266
ALYT4K | KINB4K | 2032 | Change | 69.22 | 0 | OHL | 0.1384 | 1.3152 | 42.501 | 2349 | 2266 | 2120 | 2266
BALA1A | BALA1B | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BALA1A | HARI1- | 2032 | Addition | 32.5 | 0 | OHL | 1.6575 | 7.28 | 1.69 | 241 | 230 | 210 | 230
BALA1A | LEWI1J | 2032 | Addition | 26 | 0 | OHL | 1.326 | 5.824 | 1.352 | 241 | 230 | 210 | 230
BALA1A | MUAI1A | 2032 | Addition | 13 | 0 | OHL | 0.65 | 2.691 | 0.728 | 203 | 193 | 176 | 193
BALA1B | LEWI1K | 2032 | Addition | 26 | 0 | OHL | 1.326 | 5.824 | 1.352 | 241 | 230 | 210 | 230
BANN4J | BANN4R | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BANN4J | CAAI4J | 2032 | Addition | 85 | 0 | OHL | 0.085 | 1.445 | 58.395 | 2780 | 2670 | 2480 | 2670
BANN4K | CAAI4K | 2032 | Addition | 85 | 0 | OHL | 0.085 | 1.445 | 58.395 | 2780 | 2670 | 2480 | 2670
BEAU1J | BEAU1T | 2032 | Removed | 0 | 0.22 | Cable | 0.01 | 0.0147 | 0.268 | 141 | 136 | 136 | 136
BEAU1K | BEAU1N | 2032 | Removed | 0 | 0.25 | Cable | 0.01 | 0.0167 | 0.305 | 141 | 136 | 136 | 136
BEAU1N | KNOC1J | 2032 | Removed | 17.1 | 0 | OHL | 1.5561 | 3.9843 | 0.855 | 132 | 123 | 106 | 123
BEAU1T | KNOC1J | 2032 | Removed | 17.1 | 0 | OHL | 1.5561 | 3.9843 | 0.855 | 132 | 123 | 106 | 123
BEAU2J | FYRI2J | 2032 | Removed | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 780 | 750 | 700 | 750
BEAU2J | FYRI2M | 2032 | Addition | 29 | 0 | OHL | 0.174 | 1.5947 | 6.147 | 780 | 750 | 700 | 750
BEAU2K | FYRI2K | 2032 | Removed | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 780 | 750 | 700 | 750
BEAU2K | FYRI2L | 2032 | Addition | 29 | 0 | OHL | 0.174 | 1.5947 | 6.147 | 780 | 750 | 700 | 750
BEAU4- | BING4- | 2032 | Removed | 25.3 | 0 | OHL | 0.0328 | 0.4847 | 15.298 | 2780 | 2670 | 2480 | 2670
BEAU4- | FAUG4J | 2032 | Removed | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2780 | 2670 | 2480 | 2670
BEAU4- | FNLN4A | 2032 | Addition | 5 | 0 | OHL | 0.0065 | 0.0958 | 3.023 | 2780 | 2670 | 2480 | 2670
BEAU4- | FNLN4B | 2032 | Addition | 5 | 0 | OHL | 0.0065 | 0.0958 | 3.023 | 2780 | 2670 | 2480 | 2670
BING4- | FNLN4A | 2032 | Addition | 20.3 | 0 | OHL | 0.0263 | 0.3889 | 12.274 | 2780 | 2670 | 2480 | 2670
BLHI4- | COFD4A | 2032 | Addition | 2.5 | 0 | OHL | 0.005 | 0.0483 | 1.471 | 2000 | 1920 | 1790 | 1920
BLHI4- | COFD4B | 2032 | Addition | 2.5 | 0 | OHL | 0.005 | 0.0483 | 1.471 | 2000 | 1920 | 1790 | 1920
BLHI4- | ROTI4J | 2032 | Removed | 35.4 | 0 | OHL | 0.0708 | 0.6832 | 20.826 | 2000 | 1920 | 1790 | 1920
BLHI4- | ROTI4K | 2032 | Removed | 35.4 | 0 | OHL | 0.0708 | 0.6832 | 20.826 | 2000 | 1920 | 1790 | 1920
BROR1Q | DUBE1A | 2032 | Addition | 34.58 | 0 | OHL | 3.1568 | 8.0501 | 1.716 | 126 | 117 | 101 | 117
BROR1Q | DUBE1Q | 2032 | Removed | 38.58 | 0 | OHL | 3.522 | 8.9813 | 1.914 | 126 | 117 | 101 | 117
CAAI4J | CAAI4K | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CAAI4J | FNLN4A | 2032 | Addition | 82 | 0 | OHL | 0.082 | 1.394 | 56.334 | 2780 | 2670 | 2480 | 2670
CAAI4K | FNLN4B | 2032 | Addition | 82 | 0 | OHL | 0.082 | 1.394 | 56.334 | 2780 | 2670 | 2480 | 2670
CAID2- | KNOC2J | 2032 | Removed | 38.99 | 0 | OHL | 0.2208 | 1.6052 | 10.631 | 935 | 880 | 790 | 880
CAID2- | KNOC2N | 2032 | Addition | 0 | 6 | Cable | 0.0465 | 0.1721 | 34.121 | 930 | 900 | 900 | 900
CALD4- | GRNS4M | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CLGO2- | KNOC2K | 2032 | Removed | 47.45 | 0 | OHL | 0.2687 | 1.9535 | 12.938 | 935 | 880 | 790 | 880
CLGO2- | KNOC2P | 2032 | Addition | 0 | 6 | Cable | 0.0465 | 0.1721 | 34.121 | 930 | 900 | 900 | 900
COFD4A | COFD4B | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
COFD4A | FNLN4A | 2032 | Addition | 110 | 0 | OHL | 0.11 | 1.87 | 75.57 | 2780 | 2670 | 2480 | 2670
COFD4A | GRNS4L | 2032 | Addition | 60.37 | 0 | OHL | 0.0604 | 1.0263 | 41.474 | 2780 | 2670 | 2480 | 2670
COFD4A | ROTI4J | 2032 | Addition | 32.9 | 0 | OHL | 0.0658 | 0.635 | 19.355 | 2000 | 1920 | 1790 | 1920
COFD4B | FNLN4B | 2032 | Addition | 110 | 0 | OHL | 0.11 | 1.87 | 75.57 | 2780 | 2670 | 2480 | 2670
COFD4B | GRNS4M | 2032 | Addition | 60.37 | 0 | OHL | 0.0604 | 1.0263 | 41.474 | 2780 | 2670 | 2480 | 2670
COFD4B | ROTI4K | 2032 | Addition | 32.9 | 0 | OHL | 0.0658 | 0.635 | 19.355 | 2000 | 1920 | 1790 | 1920
CONN2J | LOCB2J | 2032 | Removed | 76.071 | 0.269 | Composite | 0.458 | 4.1987 | 16.184 | 780 | 750 | 700 | 750
CONN2J | LOCB2M | 2032 | Addition | 75.34 | 0 | OHL | 0.452 | 4.1437 | 15.972 | 780 | 750 | 700 | 750
CRDH1J | KILC1Q | 2032 | Removed | 4.98 | 0 | OHL | 0.7095 | 1.1715 | 0.244 | 99 | 92 | 79 | 92
CRDH1J | KILC1Q | 2032 | Addition | 4.9 | 0 | OHL | 0.1158 | 1.0399 | 0.269 | 463 | 444 | 415 | 444
CRDH1K | FERO1S | 2032 | Change | 5.01 | 0 | OHL | 0.1184 | 1.0632 | 0.275 | 463 | 444 | 415 | 444
DUBE1A | DUBE1Q | 2032 | Addition | 0 | 4 | Cable | 0.1457 | 0.3676 | 4.74 | 152 | 140 | 140 | 140
DUBE1B | DUBE1C | 2032 | Addition | 0 | 4 | Cable | 0.1457 | 0.3676 | 4.74 | 152 | 140 | 140 | 140
DUBE1B | MYBS1Q | 2032 | Addition | 20.84 | 0 | OHL | 1.9025 | 4.8515 | 1.034 | 126 | 117 | 101 | 117
DUBE1C | LOCB1U | 2032 | Addition | 60.46 | 0 | OHL | 5.5195 | 14.0749 | 3 | 126 | 117 | 101 | 117
DUBE1Q | MYBS1R | 2032 | Removed | 20.84 | 0 | OHL | 1.9025 | 4.8515 | 1.034 | 126 | 117 | 101 | 117
EDAY1- | EDAY1B | 2032 | Addition | 4.4 | 0 | OHL | 0.22 | 0.9108 | 0.246 | 203 | 193 | 173 | 193
EDAY1A | EDAY1B | 2032 | Addition | 0 | 18.6 | Cable | 0.5877 | 1.1107 | 24.085 | 189 | 189 | 189 | 189
EDAY1A | ELIB1- | 2032 | Addition | 3 | 0 | OHL | 0.15 | 0.621 | 0.168 | 203 | 193 | 173 | 193
EDIN1J | GLUE1- | 2032 | Addition | 0 | 2.8 | Cable | 0.0166 | 0.214 | 5.019 | 348 | 348 | 348 | 348
ELGI1Q | KEIT1- | 2032 | Removed | 27.4 | 0 | Cable | 1.3974 | 6.1376 | 1.425 | 241 | 230 | 210 | 230
ELGI1Q | KEIT1N | 2032 | Addition | 22.9 | 0 | OHL | 1.1679 | 5.1296 | 1.191 | 241 | 230 | 210 | 230
ELGI1R | KEIT1- | 2032 | Removed | 27.4 | 0 | OHL | 1.3974 | 6.1376 | 1.425 | 241 | 230 | 210 | 230
ELGI1R | KEIT1M | 2032 | Addition | 22.9 | 0 | OHL | 1.1679 | 5.1296 | 1.191 | 241 | 230 | 210 | 230
EMMO4J | EMMO4K | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
EMMO4J | GLRB4- | 2032 | Addition | 38.8 | 0 | OHL | 0.0825 | 0.7703 | 22.612 | 2780 | 2740 | 2660 | 2740
EMMO4J | HURL4A | 2032 | Addition | 59 | 0 | OHL | 0.059 | 1.003 | 40.533 | 2780 | 2670 | 2480 | 2670
EMMO4K | HURL4B | 2032 | Addition | 59 | 0 | OHL | 0.059 | 1.003 | 40.533 | 2780 | 2670 | 2480 | 2670
EMMO4K | WFIB4- | 2032 | Addition | 38.8 | 0 | OHL | 0.0825 | 0.7703 | 22.612 | 2780 | 2740 | 2660 | 2740
FAUG2T | LHEU2- | 2032 | Addition | 0 | 6 | Cable | 0.0099 | 0.1626 | 70 | 1100 | 1100 | 1100 | 1100
FAUG4J | FNLN4B | 2032 | Addition | 43.6 | 0 | OHL | 0.0565 | 0.8352 | 26.363 | 2780 | 2670 | 2480 | 2670
FERO1S | TAYN1R | 2032 | Change | 7.49 | 0 | OHL | 0.177 | 1.5895 | 0.411 | 463 | 444 | 415 | 444
FETT4Q | KINT4J | 2032 | Change | 32.19 | 0 | OHL | 0.0644 | 0.6116 | 19.765 | 2349 | 2266 | 2120 | 2266
FETT4R | KINT4K | 2032 | Change | 32.19 | 0 | OHL | 0.0644 | 0.6116 | 19.765 | 2349 | 2266 | 2120 | 2266
FNLN4A | FNLN4B | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FNLN4B | FNLN4R | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
FOYE2- | LKEM2- | 2032 | Addition | 0 | 10.5 | Cable | 0.0285 | 0.1919 | 60.12 | 580 | 546 | 546 | 546
FYRI2J | FYRI2M | 2032 | Addition | 0 | 1.5 | Cable | 0.0116 | 0.043 | 8.53 | 930 | 900 | 900 | 900
FYRI2K | FYRI2L | 2032 | Addition | 0 | 1.5 | Cable | 0.0116 | 0.043 | 8.53 | 930 | 900 | 900 | 900
GILB1J | HOME1- | 2032 | Addition | 3.5 | 0 | OHL | 0.175 | 0.7245 | 0.196 | 203 | 193 | 176 | 193
GLRB2- | TEAL2K | 2032 | Removed | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030
GRNS4L | GRNS4M | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
GRNS4L | LOSD4A | 2032 | Addition | 22.39 | 0 | OHL | 0.0224 | 0.3806 | 15.382 | 2780 | 2670 | 2480 | 2670
GRNS4L | NEDE4J | 2032 | Addition | 0 | 3 | Cable | 0.002 | 0.0164 | 33.651 | 1300 | 1235 | 1235 | 1235
GRNS4L | NEDE4J | 2032 | Addition | 0 | 3 | Cable | 0.002 | 0.0164 | 33.651 | 1300 | 1235 | 1235 | 1235
GRNS4M | LOSD4B | 2032 | Addition | 22.39 | 0 | OHL | 0.0224 | 0.3806 | 15.382 | 2780 | 2670 | 2480 | 2670
GRNS4M | NEDE4K | 2032 | Addition | 0 | 3 | Cable | 0.002 | 0.0164 | 33.651 | 1300 | 1235 | 1235 | 1235
HURL4A | HURL4B | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
HURL4A | KINT4K | 2032 | Addition | 41 | 0 | OHL | 0.041 | 0.697 | 28.167 | 2780 | 2670 | 2480 | 2670
HURL4B | KINT4J | 2032 | Addition | 41 | 0 | OHL | 0.041 | 0.697 | 28.167 | 2780 | 2670 | 2480 | 2670
KEIT1- | KEIT1M | 2032 | Addition | 0 | 4.5 | Cable | 0.0591 | 0.3694 | 7.389 | 265 | 263 | 263 | 263
KEIT1- | KEIT1N | 2032 | Addition | 0 | 4.5 | Cable | 0.0591 | 0.3694 | 7.389 | 265 | 263 | 263 | 263
KILC1Q | TAYN1Q | 2032 | Change | 7.6 | 0 | OHL | 0.1796 | 1.6129 | 0.417 | 463 | 444 | 415 | 444
KINA4A | KINA4B | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINT2J | KINT2L | 2032 | Addition | 0 | 1.5 | Cable | 0.0116 | 0.043 | 8.53 | 930 | 900 | 900 | 900
KINT2J | TEAL2A | 2032 | Removed | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2K | KINT2M | 2032 | Addition | 0 | 1.5 | Cable | 0.0116 | 0.043 | 8.53 | 930 | 900 | 900 | 900
KINT2K | TEAL2B | 2032 | Removed | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640
KINT2L | TEAL2A | 2032 | Addition | 99.1 | 0 | OHL | 0.6009 | 5.2801 | 21.812 | 695 | 640 | 550 | 640
KINT2M | TEAL2B | 2032 | Addition | 99.1 | 0 | OHL | 0.6009 | 5.2801 | 21.812 | 695 | 640 | 550 | 640
KNOC2J | KNOC2L | 2032 | Addition | 0 | 1 | Cable | 0.0078 | 0.0287 | 5.687 | 930 | 900 | 900 | 900
KNOC2J | REJO2A | 2032 | Addition | 0 | 9 | Cable | 0.024 | 0.165 | 51.532 | 580 | 546 | 546 | 546
KNOC2K | KNOC2M | 2032 | Addition | 0 | 1 | Cable | 0.0078 | 0.0287 | 5.687 | 930 | 900 | 900 | 900
KNOC2K | REJO2B | 2032 | Addition | 0 | 9 | Cable | 0.024 | 0.165 | 51.532 | 580 | 546 | 546 | 546
KNOC2L | KNOC2N | 2032 | Addition | 31.99 | 0 | OHL | 0.1811 | 1.317 | 8.723 | 935 | 880 | 790 | 880
KNOC2M | KNOC2P | 2032 | Addition | 40.45 | 0 | OHL | 0.2291 | 1.6653 | 11.029 | 935 | 880 | 790 | 880
LEWI1J | LEWI1K | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LEWI1J | STOR1- | 2032 | Addition | 1 | 0 | OHL | 0.0452 | 0.1608 | 0.07 | 300 | 285 | 255 | 285
LEWI1K | STOR1- | 2032 | Addition | 1 | 0 | OHL | 0.0452 | 0.1608 | 0.07 | 300 | 285 | 255 | 285
LEWI4- | LEWI4J | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LEWI4J | LEWI4K | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LEWI4J | LEWI4R | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LEWI4K | NPIC4- | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LEWI4K | TLSK4- | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOCB1R | SHIN1- | 2032 | Change | 8.34 | 0 | OHL | 0.1958 | 0.9525 | 0.203 | 464 | 446 | 414 | 446
LOCB1S | SHIN1- | 2032 | Change | 8.34 | 0 | OHL | 0.1958 | 0.9525 | 0.203 | 464 | 446 | 414 | 446
LOCB2J | LOCB2M | 2032 | Addition | 1 | 0 | Cable | 0.0078 | 0.0287 | 5.687 | 930 | 900 | 900 | 900
LOCB2K | LOCB2L | 2032 | Addition | 1 | 0 | Cable | 0.0078 | 0.0287 | 5.687 | 930 | 900 | 900 | 900
LOCB2K | STRB2- | 2032 | Removed | 18.9 | 0 | OHL | 0.1134 | 1.0395 | 4.007 | 780 | 750 | 700 | 750
LOCB2L | STRB2- | 2032 | Addition | 17.9 | 0 | OHL | 0.1074 | 0.9845 | 3.795 | 780 | 750 | 700 | 750
LOSD1A | LOSD1B | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOSD4A | LOSD4B | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOSD4A | LOSD4R | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOSD4A | MARA4- | 2032 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOSD4A | NEDE4K | 2032 | Addition | 24.5 | 0 | OHL | 0.049 | 0.4728 | 14.413 | 2000 | 1920 | 1790 | 1920
LOSD4A | PEHE4J | 2032 | Addition | 7.3 | 0 | OHL | 0.0146 | 0.1409 | 4.295 | 2000 | 1920 | 1790 | 1920
LOSD4B | NEDE4J | 2032 | Addition | 24.5 | 0 | OHL | 0.049 | 0.4728 | 14.413 | 2000 | 1920 | 1790 | 1920
LOSD4B | PEHE4K | 2032 | Addition | 7.3 | 0 | OHL | 0.0146 | 0.1409 | 4.295 | 2000 | 1920 | 1790 | 1920
MOTA1Q | SHIN1- | 2032 | Removed | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 132 | 123 | 106 | 123
MOTA1Q | SHIN1B | 2032 | Addition | 28.95 | 0 | OHL | 3.127 | 7.1633 | 1.522 | 132 | 123 | 106 | 123
MOTA1R | SHIN1- | 2032 | Removed | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 126 | 117 | 101 | 117
MOTA1R | SHIN1A | 2032 | Addition | 28.95 | 0 | OHL | 3.127 | 7.1633 | 1.522 | 126 | 117 | 101 | 117
NEDE4J | PEHE4J | 2032 | Removed | 30.04 | 0 | OHL | 0.0601 | 0.5798 | 17.673 | 2000 | 1920 | 1790 | 1920
NEDE4K | PEHE4K | 2032 | Removed | 30.04 | 0 | OHL | 0.0601 | 0.5798 | 17.673 | 2000 | 1920 | 1790 | 1920
SHIN1- | SHIN1A | 2032 | Addition | 0 | 2.25 | Cable | 0.082 | 0.2068 | 2.666 | 152 | 140 | 140 | 140
SHIN1- | SHIN1B | 2032 | Addition | 0 | 2.25 | Cable | 0.082 | 0.2068 | 2.666 | 152 | 140 | 140 | 140
LOCB1U | MYBS1Q | 2033 | Removed | 85.3 | 0 | OHL | 7.7872 | 19.8576 | 4.233 | 126 | 117 | 101 | 117
TEAL2J | WFIB2- | 2033 | Removed | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030
ANSN2- | CADU2C | 2035 | Addition | 13.25 | 0 | OHL | 0.053 | 0.5433 | 3.737 | 1540 | 1480 | 1380 | 1480
ANSN2- | CRDH2J | 2035 | Removed | 20.25 | 0 | OHL | 0.081 | 0.8303 | 5.711 | 1540 | 1480 | 1380 | 1480
AYRE4- | BANN4K | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BANN4J | THUS4A | 2035 | Addition | 12.1 | 0 | OHL | 0.0121 | 0.2057 | 8.313 | 2780 | 2670 | 2480 | 2670
BANN4K | THUS4B | 2035 | Addition | 12.1 | 0 | OHL | 0.0121 | 0.2057 | 8.313 | 2780 | 2670 | 2480 | 2670
BLHI2J | KINT2K | 2035 | Removed | 50.85 | 0 | OHL | 0.298 | 2.08 | 14.14 | 935 | 880 | 790 | 880
BLHI2K | CAIN2- | 2035 | Removed | 9.77 | 0 | OHL | 0.0573 | 0.3997 | 2.717 | 935 | 880 | 790 | 880
BLHI4- | CAIN4- | 2035 | Addition | 9.77 | 0 | OHL | 0.0098 | 0.1661 | 6.712 | 2780 | 2670 | 2480 | 2670
BLHI4- | CAIN4- | 2035 | Addition | 9.77 | 0 | OHL | 0.0098 | 0.1661 | 6.712 | 2780 | 2670 | 2480 | 2670
BOWD4- | HURL4A | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
BUCH4- | PEHE4J | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
CADU2A | CADU2B | 2035 | Addition | 5 | 0 | OHL | 0.02 | 0.205 | 1.41 | 1290 | 1240 | 1160 | 1240
CADU2A | CRDH2J | 2035 | Addition | 7 | 0 | OHL | 0.028 | 0.287 | 1.974 | 1540 | 1480 | 1380 | 1480
CADU2B | CADU2C | 2035 | Addition | 5 | 0 | OHL | 0.02 | 0.205 | 1.41 | 1290 | 1240 | 1160 | 1240
CAIN2- | KINT2J | 2035 | Removed | 41.08 | 0 | OHL | 0.2407 | 1.6803 | 11.423 | 935 | 880 | 790 | 880
CAIN4- | KINT4J | 2035 | Addition | 41.08 | 0 | OHL | 0.0411 | 0.6984 | 28.222 | 2780 | 2670 | 2480 | 2670
CAIN4- | KINT4K | 2035 | Addition | 41.08 | 0 | OHL | 0.0411 | 0.6984 | 28.222 | 2780 | 2670 | 2480 | 2670
COFD4A | COFD4Z | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
DOUN4A | DOUN4B | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
DOUN4A | HVBY4- | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
DOUN4A | THUS4A | 2035 | Addition | 15.4 | 0 | OHL | 0.0154 | 0.2618 | 10.58 | 2780 | 2670 | 2480 | 2670
DOUN4B | THUS4B | 2035 | Addition | 15.4 | 0 | OHL | 0.0154 | 0.2618 | 10.58 | 2780 | 2670 | 2480 | 2670
DUNA1- | TAYN1Q | 2035 | Addition | 11.2 | 0 | OHL | 1.019 | 2.419 | 0.605 | 126 | 119 | 108 | 119
GRNS4M | STMR4- | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
HURL4A | HURL4Z | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINM2A | PEHE2- | 2035 | Removed | 23.8 | 0 | OHL | 0.12 | 1.04 | 6.26 | 1090 | 1030 | 920 | 1030
KINM2B | PERS2Q | 2035 | Removed | 23.8 | 0 | OHL | 0.12 | 1.04 | 6.26 | 1090 | 1030 | 920 | 1030
KINM4A | KINM4C | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINM4A | PEHE4K | 2035 | Addition | 23.8 | 0 | OHL | 0.0476 | 0.4522 | 14.613 | 2349 | 2266 | 2120 | 2266
KINM4B | KINM4C | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
KINM4B | NASS4N | 2035 | Addition | 11.1 | 0 | OHL | 0.0222 | 0.2109 | 6.815 | 2349 | 2266 | 2120 | 2266
KINT2J | PERS2R | 2035 | Removed | 28.2 | 0 | OHL | 0.14 | 1.23 | 7.42 | 1090 | 1030 | 920 | 1030
KINT2K | PEHE2R | 2035 | Removed | 50.4 | 0 | OHL | 0.26 | 2.19 | 13.22 | 1090 | 1030 | 920 | 1030
KINT4J | NASS4Q | 2035 | Addition | 15.5 | 0 | OHL | 0.031 | 0.2945 | 9.517 | 2349 | 2266 | 2120 | 2266
KINT4K | NASS4R | 2035 | Addition | 15.5 | 0 | OHL | 0.031 | 0.2945 | 9.517 | 2349 | 2266 | 2120 | 2266
LOSD1B | SCRA1A | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOSD1B | SCRA1B | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOSD4A | LOSD4M | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOSD4A | MUMR4- | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
LOSD4A | PEHE4J | 2035 | Change | 7.3 | 0 | OHL | 0.0073 | 0.1241 | 5.015 | 3464 | 3464 | 3320 | 3464
LOSD4B | PEHE4K | 2035 | Change | 7.3 | 0 | OHL | 0.0073 | 0.1241 | 5.015 | 3464 | 3464 | 3320 | 3464
NASS2Q | PERS2Q | 2035 | Addition | 12.8 | 0 | OHL | 0.0579 | 0.5313 | 3.482 | 1090 | 1030 | 920 | 1030
NASS2R | PERS2R | 2035 | Addition | 12.8 | 0 | OHL | 0.0579 | 0.5313 | 3.482 | 1090 | 1030 | 920 | 1030
NASS4M | NASS4R | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
NASS4M | PEHE4J | 2035 | Addition | 34.9 | 0 | OHL | 0.0698 | 0.6631 | 21.429 | 2349 | 2266 | 2120 | 2266
NASS4N | NASS4Q | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
NASS4Q | NASS4R | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999
PEHE2Z | PEHERSV1 | 2035 | Addition | 0 | 0.47 | Cable | 0.01 | 0.01 | 5.009 | 1560 | 1560 | 1560 | 1560
THUS4A | THUS4B | 2035 | Addition | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999

## B-2-2b
B-2-2b - SPT Circuit Changes 2025/26 to 2035/36
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
AREX1- | AREX1A | 2025 | Addition | 0 | 1.7 | Cable | 0.048 | 0.1103 | 2.0938 | 85 | 85 | 85 | 85
AREX1A | CHMO1T | 2025 | Addition | 4.7 | 0 | OHL | 0.35711 | 1.0182 | 0.24839 | 284 | 272 | 249 | 278
AREX1A | MAHI1B | 2025 | Addition | 7.5 | 0.5 | Composite | 0.5731 | 1.6545 | 1.2722 | 365 | 360 | 350 | 360
AYRS4- | HBES4- | 2025 | Addition | 0 | 0.1 | Cable | 0.0001 | 0.0013 | 1.1119 | 2770 | 2770 | 2770 | 2770
AYRS4- | HESF4- | 2025 | Addition | 0 | 0.1 | Cable | 0.0001 | 0.0013 | 1.1119 | 2770 | 2770 | 2770 | 2770
AYRS4- | HUNE4- | 2025 | Addition | 0 | 0.9 | Cable | 0.0005 | 0.012 | 10.0073 | 1247 | 1247 | 1247 | 1247
BENB1- | BENB1T | 2025 | Addition | 2.5 | 0 | OHL | 0.1875 | 0.5505 | 0.1315 | 167 | 160 | 148 | 160
BENB1T | BLCW1- | 2025 | Addition | 32.15 | 0.9 | Composite | 1.1801 | 6.5296 | 3.3413 | 199 | 191 | 178 | 191
BENB1T | NECU1B | 2025 | Addition | 4 | 0 | OHL | 0.1038 | 0.7722 | 0.2394 | 482 | 460 | 420 | 460
BLAH1- | GLGL1Q | 2025 | Change | 13.6 | 0.375 | Composite | 0.5207 | 2.9382 | 1.1932 | 297 | 281 | 258 | 281
BLAH1- | GLGL1R | 2025 | Change | 13.6 | 0.375 | Composite | 0.5207 | 2.9382 | 1.1932 | 297 | 281 | 258 | 281
BLAH3B | PLOE3- | 2025 | Addition | 0 | 1.01 | Cable | 0.2795 | 0.8831 | 0.1185 | 40 | 38 | 38 | 38
BLAH3B | PLOE3- | 2025 | Addition | 0 | 1.01 | Cable | 0.2795 | 0.8831 | 0.1185 | 40 | 38 | 38 | 38
BLCW1- | NECU1Q | 2025 | Removed | 36.15 | 0.9 | Composite | 1.2839 | 7.3019 | 3.5807 | 167 | 160 | 148 | 160
CHAP1- | HAKB1- | 2025 | Change | 14.72 | 0 | OHL | 0.78187 | 3.1313 | 0.80314 | 242 | 225 | 194 | 225
CHMO1- | CHMO1T | 2025 | Addition | 0.3 | 0 | OHL | 0.0225 | 0.066 | 0.0158 | 167 | 160 | 148 | 160
CHMO1T | STOC1- | 2025 | Addition | 5.9 | 0 | OHL | 0.4426 | 1.2993 | 0.3103 | 167 | 160 | 148 | 160
CLAU1- | MAHI1C | 2025 | Addition | 0 | 4 | Cable | 0.0583 | 0.3646 | 5.0764 | 199 | 191 | 178 | 191
CLYS3A | WHBR3A | 2025 | Addition | 13.1 | 2.5 | Composite | 16.4566 | 43.5395 | 0.3436 | 42 | 40 | 36 | 40
CLYS3B | WHBR3B | 2025 | Addition | 13.1 | 2.5 | Composite | 17.1837 | 42.3511 | 0.2892 | 42 | 40 | 36 | 40
COAB4- | COAL4- | 2025 | Addition | 0 | 2.5 | Cable | 0.0017 | 0.032 | 27.7981 | 1247 | 1247 | 1247 | 1247
COAL1B | CUMW1- | 2025 | Addition | 0 | 11.1 | Cable | 0.3134 | 0.7205 | 14.5825 | 120 | 120 | 120 | 120
CROO1Q | NEIL1- | 2025 | Change | 12.56 | 0.22 | Composite | 0.4737 | 2.7011 | 0.9855 | 229 | 211 | 183 | 211
CROO1R | NEIL1- | 2025 | Change | 12.56 | 0.23 | Composite | 0.4738 | 2.702 | 0.9994 | 229 | 211 | 183 | 211
DEVM1- | ERSK1Q | 2025 | Change | 16.5 | 0 | OHL | 1.0026 | 3.563 | 0.8861 | 213 | 202 | 185 | 202
DEVM1- | SPAV1Q | 2025 | Change | 7.63 | 0 | OHL | 0.5726 | 1.7268 | 0.3878 | 107 | 107 | 101 | 107
DEVM1- | SPAV1R | 2025 | Change | 7.51 | 0 | OHL | 0.5636 | 1.699 | 0.3818 | 107 | 107 | 101 | 107
DONO3A | DWEX3- | 2025 | Addition | 0 | 4 | Cable | 0.5534 | 1.7488 | 0.9388 | 40 | 38 | 38 | 38
EWEH1Q | GRNA1- | 2025 | Change | 15.9 | 0.36 | Composite | 1.2138 | 3.4754 | 1.4335 | 295 | 295 | 295 | 295
FASI1- | FASI1A | 2025 | Addition | 5 | 0 | OHL | 0.3756 | 1.1002 | 0.2633 | 199 | 191 | 178 | 191
FASI1- | FASI1B | 2025 | Addition | 5 | 0 | OHL | 0.3756 | 1.1002 | 0.2633 | 199 | 191 | 178 | 191
FASI1A | HAWI1- | 2025 | Addition | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124
FASI1A | JUNV1- | 2025 | Addition | 31.5 | 0 | OHL | 2.3859 | 7.5314 | 1.5385 | 199 | 191 | 178 | 191
FASI1B | HAWI1- | 2025 | Addition | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124
FASI1B | JUNV1A | 2025 | Addition | 31.5 | 0 | OHL | 2.3859 | 7.5314 | 1.5385 | 199 | 191 | 178 | 191
FIGS2- | KINC2- | 2025 | Addition | 0 | 0.7 | Cable | 0.0018 | 0.0075 | 5.395 | 352 | 352 | 352 | 352
GLGL1- | SANQ1- | 2025 | Addition | 0 | 4 | Cable | 0.0629 | 0.3444 | 6.5906 | 283 | 277 | 269 | 277
GORG1Q | TELR1Q | 2025 | Change | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 72 | 72 | 72 | 72
GORG1R | TELR1R | 2025 | Change | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 72 | 72 | 72 | 72
GRNA1- | HAWI1- | 2025 | Removed | 55.35 | 0 | OHL | 4.2501 | 13.0393 | 2.7334 | 132 | 123 | 106 | 123
GRNA1- | JUNV1- | 2025 | Change | 4.74 | 0 | OHL | 0.359 | 1.1333 | 0.2315 | 199 | 191 | 178 | 191
GRNA1- | JUNV1A | 2025 | Addition | 4.74 | 0 | OHL | 0.359 | 1.1333 | 0.2315 | 199 | 191 | 178 | 191
HAWI1- | JUNV1- | 2025 | Removed | 50.34 | 0 | OHL | 3.7968 | 11.8507 | 2.4895 | 132 | 123 | 106 | 123
HOLM1- | HOLM1T | 2025 | Addition | 0 | 0.28 | Cable | 0.0025 | 0.0233 | 0.5242 | 293 | 293 | 293 | 293
HOLM1- | SHRG1T | 2025 | Addition | 8 | 0 | OHL | 0.6078 | 1.7331 | 0.4228 | 365 | 360 | 350 | 360
HOLM1T | KEOO1- | 2025 | Addition | 10.16 | 0 | OHL | 0.4101 | 2.0583 | 0.5825 | 132 | 123 | 106 | 123
HOLM1T | NECU1B | 2025 | Addition | 16.35 | 0 | OHL | 0.4243 | 3.1565 | 0.9785 | 482 | 460 | 420 | 460
HUCR4- | HUNE4- | 2025 | Addition | 0 | 0.4 | Cable | 0.0002 | 0.0053 | 4.4477 | 1247 | 1247 | 1247 | 1247
HUER1- | HUNF1Q | 2025 | Removed | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 146 | 146 | 146
HUER1- | HUNF1R | 2025 | Removed | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 146 | 146 | 146
HUER1- | JUNA1T | 2025 | Removed | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 175 | 175 | 175
HUER4- | KILS4- | 2025 | Removed | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930
HUER4- | KILS4T | 2025 | Removed | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930
HUNE1- | HUNF1Q | 2025 | Addition | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 146 | 146 | 146
HUNE1- | HUNF1R | 2025 | Addition | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 146 | 146 | 146
HUNE1- | JUNA1T | 2025 | Addition | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 175 | 175 | 175
HUNE4- | KILS4- | 2025 | Addition | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930
HUNE4- | KILS4T | 2025 | Addition | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930
JUNB1A | JUNV1A | 2025 | Addition | 1 | 0 | OHL | 0 | 0.0001 | 0 | 2286 | 2286 | 2286 | 2286
KEOO1- | NECU1R | 2025 | Removed | 26.51 | 0 | OHL | 0.8345 | 5.2149 | 1.561 | 132 | 123 | 106 | 123
LAMB2- | WIYH2- | 2025 | Change | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1380 | 1320 | 1230 | 1320
LAMB2T | WIYH2- | 2025 | Change | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1380 | 1320 | 1230 | 1320
MOFF1- | SCOP1- | 2025 | Addition | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293
MOFF1A | SCOP1A | 2025 | Addition | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293
MOFF1A | SCOP1A | 2025 | Addition | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293
NECU1B | OHLL1- | 2025 | Addition | 0 | 3 | Cable | 0.0534 | 0.2861 | 3.5006 | 180 | 180 | 180 | 180
NECU1C | SOKY1- | 2025 | Change | 0 | 4.5 | Cable | 0.0458 | 0.2435 | 7.265 | 242 | 223 | 192 | 223
ARCR2- | MAHI2- | 2027 | Addition | 0 | 9.5 | Cable | 0.0488 | 0.2034 | 36.6087 | 352 | 352 | 352 | 352
BAGA1Q | BONN1- | 2027 | Change | 18.3 | 0 | OHL | 0.6862 | 3.8983 | 0.9904 | 242 | 223 | 192 | 223
BAGA1R | BONN1- | 2027 | Change | 18.4 | 0 | OHL | 0.69 | 3.9202 | 0.9957 | 242 | 223 | 192 | 223
BENB1T | BLCW1- | 2027 | Removed | 32.15 | 0.9 | Composite | 1.1801 | 6.5296 | 3.3413 | 199 | 191 | 178 | 191
BENB1T | KEOO1Q | 2027 | Addition | 20.25 | 0 | OHL | 0.5256 | 3.9095 | 1.2119 | 482 | 460 | 420 | 460
BLCW1- | GNSH1- | 2027 | Addition | 1.8 | 0 | OHL | 0.1352 | 0.3961 | 0.0948 | 167 | 160 | 148 | 160
CAFA1Q | KEOO1- | 2027 | Change | 2.58 | 0 | OHL | 0.198 | 0.5682 | 0.1357 | 135 | 126 | 110 | 126
CHAP1- | DUMF1- | 2027 | Removed | 26.9 | 0.18 | Composite | 1.0661 | 6.0867 | 1.6344 | 171 | 155 | 155 | 155
CHAP1- | GRNA1- | 2027 | Change | 12.83 | 0.3 | Composite | 0.797 | 3.0442 | 0.9509 | 198 | 186 | 168 | 186
CHAP1- | GRNA1- | 2027 | Change | 12.83 | 0.35 | Composite | 0.7983 | 3.0495 | 1.0029 | 198 | 186 | 168 | 186
CHAP1- | OFOA1T | 2027 | Addition | 24.82 | 0.18 | Composite | 0.984 | 5.6173 | 1.5274 | 171 | 155 | 155 | 155
CLAW1- | DESA1Q | 2027 | Addition | 6.4 | 2.3 | Composite | 0.5256 | 1.6179 | 3.5471 | 167 | 160 | 147 | 160
CLAW1- | NECU1- | 2027 | Addition | 0 | 2.21 | Cable | 0.0438 | 0.2004 | 3.0848 | 182 | 182 | 182 | 182
COAL4- | ELVA4- | 2027 | Removed | 26.71 | 0 | OHL | 0.0467 | 0.5062 | 15.9918 | 2210 | 2130 | 1980 | 2130
COAL4- | REDS4- | 2027 | Addition | 11 | 0 | OHL | 0.0192 | 0.2085 | 6.5859 | 2210 | 2130 | 1980 | 2130
COAN4- | COBA4- | 2027 | Addition | 0 | 2.5 | Cable | 0.0017 | 0.032 | 27.7981 | 1247 | 1247 | 1247 | 1247
COAN4- | REDS4- | 2027 | Addition | 11 | 0 | OHL | 0.0192 | 0.2085 | 6.5859 | 2210 | 2130 | 1980 | 2130
COAN4- | STHA4A | 2027 | Addition | 21.79 | 0 | OHL | 0.0381 | 0.413 | 13.045 | 2210 | 2130 | 1980 | 2130
COYL2- | CRCK2- | 2027 | Addition | 25 | 0 | OHL | 0.1824 | 1.4207 | 5.0907 | 1110 | 1090 | 1060 | 1090
COYL2- | MAHI2- | 2027 | Removed | 49.5 | 0 | OHL | 0.3612 | 2.813 | 10.0797 | 1110 | 1090 | 1060 | 1090
CRCK2- | MAHI2- | 2027 | Addition | 25 | 0 | OHL | 0.1824 | 1.4207 | 5.0907 | 1110 | 1090 | 1060 | 1090
CRYR4- | TORN4- | 2027 | Change | 9.36 | 1.97 | Composite | 0.0144 | 0.2171 | 44.1355 | 1415 | 1415 | 1415 | 1415
CULR2- | DEBS2- | 2027 | Addition | 1.6 | 0 | OHL | 0.0069 | 0.0697 | 0.4224 | 1010 | 930 | 805 | 930
CULR2- | LOAN2- | 2027 | Addition | 3.75 | 0.174 | Composite | 0.0171 | 0.1576 | 4.1452 | 1096 | 1029 | 924 | 1029
CULR2- | MOSM2- | 2027 | Addition | 27.746 | 0 | OHL | 0.1257 | 1.1735 | 7.4554 | 1090 | 1030 | 925 | 1030
CULR2T | LOAN2T | 2027 | Addition | 3.79 | 0 | OHL | 0.0169 | 0.1556 | 1.02 | 1090 | 1030 | 925 | 1030
CULR2T | WFIE2- | 2027 | Addition | 25.419 | 0 | OHL | 0.1146 | 1.055 | 6.9136 | 1096 | 1029 | 924 | 1029
CURR2- | SIGH2Q | 2027 | Change | 1.54 | 1.7 | Composite | 0.0169 | 0.1036 | 6.0402 | 180 | 180 | 180 | 180
CURR2- | SIGH2R | 2027 | Change | 1.54 | 1.67 | Composite | 0.0168 | 0.103 | 5.941 | 180 | 180 | 180 | 180
DESA1Q | NECU1C | 2027 | Removed | 6.4 | 4.3 | Composite | 0.5652 | 1.7993 | 6.3388 | 167 | 160 | 147 | 160
DUMF1- | OFOA1T | 2027 | Addition | 2.08 | 0 | OHL | 0.0822 | 0.4694 | 0.1069 | 229 | 212 | 183 | 212
DUMF1- | TONG1Q | 2027 | Removed | 43.58 | 0 | OHL | 4.447 | 10.71 | 2.18 | 132 | 123 | 106 | 123
DUNF1Q | INKE1Q | 2027 | Change | 7.58 | 0.09 | Composite | 0.5757 | 1.7891 | 0.5513 | 132 | 122 | 106 | 122
DUNF1R | INKE1R | 2027 | Change | 7.58 | 0.09 | Composite | 0.5757 | 1.7891 | 0.5513 | 132 | 122 | 106 | 122
EAST1Q | GLLE1- | 2027 | Addition | 1.5 | 0.3 | Composite | 0.1236 | 0.3498 | 0.4484 | 133 | 124 | 107 | 124
EAST1Q | GLLE1- | 2027 | Removed | 1.69 | 0 | OHL | 0.1536 | 0.3503 | 0.094 | 132 | 123 | 106 | 123
ELVA4- | REDS4- | 2027 | Addition | 15.77 | 0 | OHL | 0.0276 | 0.2989 | 9.4418 | 2210 | 2130 | 1980 | 2130
ELVA4- | REDS4- | 2027 | Addition | 15.77 | 0 | OHL | 0.0276 | 0.2989 | 9.4418 | 2210 | 2130 | 1980 | 2130
ELVA4- | STHA4A | 2027 | Removed | 48.56 | 0 | OHL | 0.085 | 0.9204 | 29.0717 | 2210 | 2130 | 1980 | 2130
ENHI3- | MONQ3- | 2027 | Addition | 7 | 0 | OHL | 8.424 | 21.315 | 0.0269 | 34 | 32 | 28 | 32
EWEH1Q | HORI1- | 2027 | Addition | 6 | 0 | OHL | 0.4507 | 1.3202 | 0.316 | 199 | 191 | 178 | 191
FASI1A | HAWI1D | 2027 | Addition | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124
FASI1B | HAWI1C | 2027 | Addition | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124
FELL1- | WNUK1- | 2027 | Addition | 5 | 0 | OHL | 0.3751 | 1.1011 | 0.263 | 167 | 160 | 148 | 160
GALA1- | HAWI1- | 2027 | Addition | 23.55 | 0 | OHL | 1.7838 | 5.6307 | 1.1502 | 167 | 160 | 148 | 160
GALA1- | HAWI1- | 2027 | Addition | 23.55 | 0 | OHL | 1.7838 | 5.6307 | 1.1502 | 167 | 160 | 148 | 160
GALA1- | HAWI1B | 2027 | Removed | 23.55 | 0 | OHL | 1.211 | 2.684 | 7.57 | 132 | 122 | 106 | 122
GHPS1- | GLGL1- | 2027 | Addition | 10 | 0 | OHL | 0.2554 | 1.7761 | 0.6376 | 12 | 12 | 11 | 12
GHPS1- | GLGL1- | 2027 | Addition | 10 | 0 | OHL | 0.2554 | 1.7761 | 0.6376 | 12 | 12 | 11 | 12
GHPS1- | LETH1- | 2027 | Addition | 0 | 3 | Cable | 0.0404 | 0.2597 | 9.3604 | 200 | 200 | 200 | 200
GLLE1- | HOLM1T | 2027 | Addition | 18.58 | 0 | OHL | 0.479 | 3.4684 | 1.142 | 482 | 460 | 420 | 460
GLLE1- | KEOO1- | 2027 | Addition | 7.68 | 0 | OHL | 0.1961 | 1.3641 | 0.4896 | 482 | 445 | 385 | 445
GLLE1- | KEOO1- | 2027 | Removed | 7.68 | 0 | OHL | 0.6969 | 1.6787 | 0.405 | 132 | 123 | 106 | 123
GLLE1- | NETS1- | 2027 | Change | 30.04 | 0 | OHL | 2.3011 | 7.0802 | 1.472 | 284 | 278 | 270 | 278
GLLE1- | NETS1- | 2027 | Change | 30.04 | 0 | OHL | 2.3011 | 7.0802 | 1.472 | 284 | 278 | 270 | 278
GLLE1- | TONG1- | 2027 | Addition | 33.1 | 0 | OHL | 2.0116 | 7.2879 | 1.729 | 198 | 186 | 168 | 186
GLLE1- | TONG1- | 2027 | Change | 33.1 | 0 | OHL | 2.0116 | 7.2879 | 1.729 | 197.7656 | 186.1054 | 168.0436 | 186.1054
GLLE1- | WNUK1- | 2027 | Addition | 17 | 0.5 | Composite | 1.2996 | 3.7201 | 1.6799 | 200 | 200 | 200 | 200
GNSH1- | KEOO1Q | 2027 | Addition | 10.1 | 0.9 | Composite | 0.7816 | 2.2655 | 2.0167 | 272 | 231 | 231 | 231
GNSH1- | TRSN1- | 2027 | Addition | 5 | 0 | OHL | 0.3751 | 1.1011 | 0.263 | 167 | 160 | 148 | 160
GRNA4- | HAKB4B | 2027 | Change | 1.97 | 0 | OHL | 0.0035 | 0.0381 | 1.1674 | 2370 | 2270 | 2270 | 2270
HAKB4- | MOFF4C | 2027 | Change | 43.79 | 0 | OHL | 0.0772 | 0.8467 | 25.9494 | 2370 | 2270 | 2270 | 2270
HARE1- | MOFF1- | 2027 | Change | 0 | 15.33 | Cable | 0.3071 | 0.8622 | 21.8179 | 184 | 184 | 184 | 184
HOLM1T | KEOO1- | 2027 | Removed | 10.16 | 0 | OHL | 0.4101 | 2.0583 | 0.5825 | 132 | 123 | 106 | 123
KEOO1- | KEOO1Q | 2027 | Addition | 3 | 0 | OHL | 0.0779 | 0.5792 | 0.1795 | 482 | 460 | 420 | 460
KILS2- | KILT2Q | 2027 | Change | 3.56 | 0.29 | Composite | 0.0165 | 0.1465 | 2.1425 | 204 | 177 | 177 | 177
KILS2- | KILT2R | 2027 | Change | 3.56 | 0.33 | Composite | 0.0168 | 0.1474 | 2.2967 | 204 | 177 | 177 | 177
KINB2J | KINC2- | 2027 | Removed | 10.71 | 0 | OHL | 0.0482 | 0.4368 | 2.969 | 1090 | 1030 | 925 | 1030
KINB2K | KINC2- | 2027 | Removed | 10.325 | 0.385 | Composite | 0.0467 | 0.4255 | 6.9142 | 1090 | 1030 | 925 | 1030
KINB4J | KINN4- | 2027 | Addition | 8.8 | 0 | OHL | 0.0181 | 0.1864 | 4.8531 | 2000 | 1920 | 1790 | 1920
KINB4K | KINN4- | 2027 | Addition | 8.8 | 0 | OHL | 0.0181 | 0.1864 | 4.8531 | 2000 | 1920 | 1790 | 1920
KINC2- | KINN2A | 2027 | Addition | 1.9 | 0 | OHL | 0.0083 | 0.0851 | 0.4956 | 1100 | 1100 | 1100 | 1100
KINC2- | KINN2B | 2027 | Addition | 1.9 | 0 | OHL | 0.0083 | 0.0851 | 0.4956 | 1100 | 1100 | 1100 | 1100
LOAN2- | MOSM2- | 2027 | Removed | 31.496 | 0.174 | Composite | 0.1429 | 1.3311 | 11.6006 | 1090 | 1030 | 925 | 1030
LOAN2T | WFIE2- | 2027 | Removed | 29.209 | 0 | OHL | 0.1316 | 1.2106 | 7.9335 | 1090 | 1030 | 925 | 1030
LORG1- | SHRG1T | 2027 | Addition | 10 | 0 | OHL | 0.7598 | 2.1663 | 0.5285 | 284 | 279 | 270 | 279
OFOA1- | OFOA1T | 2027 | Addition | 20 | 0 | OHL | 1.5025 | 4.4007 | 1.0533 | 167 | 160 | 148 | 160
SMEA4Q | STHA4B | 2027 | Removed | 73.37 | 0 | OHL | 0.1593 | 1.4873 | 41.7375 | 900 | 760 | 760 | 760
SMEA4Q | TORN4- | 2027 | Change | 54.32 | 1.94 | Composite | 0.0742 | 1.1033 | 70.0791 | 1360 | 1280 | 1280 | 1280
SMEA4Q | WISH4- | 2027 | Addition | 61.77 | 0 | OHL | 0.1344 | 1.2615 | 34.9418 | 1386 | 1282 | 1109 | 1282
STHA4B | WISH4- | 2027 | Addition | 11.6 | 0 | OHL | 0.0249 | 0.2258 | 6.7957 | 1704 | 1635 | 1496 | 1635
DENN2T | KINC2- | 2028 | Addition | 17.75 | 0 | OHL | 0.0442 | 0.6378 | 5.5815 | 1500 | 1500 | 1500 | 1500
AREX1- | AREX1A | 2029 | Change | 0 | 1.7 | Cable | 0.048 | 0.1103 | 2.0938 | 181 | 164 | 164 | 164
AYR-2Q | COYW2S | 2029 | Change | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 955 | 885 | 760 | 885
AYR-2R | COYW2T | 2029 | Change | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 955 | 885 | 760 | 885
BAGA1Q | BONN1- | 2029 | Change | 18.3 | 0 | OHL | 0.6862 | 3.8983 | 0.9904 | 238 | 220 | 191 | 220
BAGA1R | BONN1- | 2029 | Change | 18.4 | 0 | OHL | 0.69 | 3.9202 | 0.9957 | 238 | 220 | 191 | 220
BLAH1- | GLGL1Q | 2029 | Change | 13.6 | 0.375 | Composite | 0.5207 | 2.9382 | 1.1932 | 181 | 164 | 164 | 164
BLAH1- | GLGL1R | 2029 | Change | 13.6 | 0.375 | Composite | 0.5207 | 2.9382 | 1.1932 | 181 | 164 | 164 | 164
BLCW3- | BLKS3- | 2029 | Change | 0 | 2.801 | Cable | 0.3875 | 1.2246 | 0.6574 | 35 | 35 | 35 | 35
BONB2J | DENN2- | 2029 | Removed | 19.894 | 0 | OHL | 0.054 | 0.7739 | 5.8126 | 1500 | 1500 | 1500 | 1500
BONB4- | DENN4- | 2029 | Change | 19.894 | 0 | OHL | 0.0255 | 0.3658 | 12.2977 | 2570 | 2570 | 2508 | 2570
BONB4A | DENN4- | 2029 | Addition | 19.894 | 0 | OHL | 0.0255 | 0.3658 | 12.2977 | 2570 | 2570 | 2508 | 2570
BRAP1- | ERSK1Q | 2029 | Change | 3.17 | 5.4 | Composite | 0.3985 | 1.1026 | 12.4454 | 121 | 110 | 106 | 110
BRAP1- | ERSK1R | 2029 | Change | 3.45 | 6.23 | Composite | 0.4418 | 1.1771 | 12.9647 | 102 | 79 | 79 | 79
BREE1- | CLAW1- | 2029 | Addition | 6.5 | 0 | OHL | 0.4883 | 1.4302 | 0.3423 | 199 | 191 | 178 | 191
BRNX4- | BRNX4A | 2029 | Addition | 0 | 0.25 | Cable | 0 | 0 | 0 | 2770 | 2770 | 2770 | 2770
BRNX4- | ECCL4B | 2029 | Addition | 34.2 | 0 | OHL | 0.0442 | 0.6403 | 20.975 | 2470 | 2350 | 2150 | 2350
BRNX4- | SMEA4Q | 2029 | Addition | 54.32 | 0 | OHL | 0.0716 | 1.0582 | 32.3337 | 2473 | 2349 | 2148 | 2349
BRNX4- | TORN4- | 2029 | Addition | 0 | 1.94 | Cable | 0.0005 | 0.013 | 43.1426 | 945 | 800 | 800 | 800
BRNX4- | TORN4- | 2029 | Addition | 0 | 2.1 | Cable | 0.0005 | 0.014 | 46.7008 | 1040 | 900 | 900 | 900
BRNX4Q | CRYR4- | 2029 | Addition | 9.36 | 0 | OHL | 0.012 | 0.1717 | 5.799 | 2522 | 2397 | 2189 | 2397
BRNX4Q | TORN4- | 2029 | Addition | 0 | 1.97 | Cable | 0.002 | 0.0326 | 38.612 | 935 | 785 | 785 | 785
BRNX4R | ECCL4A | 2029 | Addition | 34.2 | 0 | OHL | 0.0442 | 0.6403 | 20.975 | 2470 | 2350 | 2150 | 2350
BRNX4R | TORN4- | 2029 | Addition | 0 | 1.94 | Cable | 0.0019 | 0.0321 | 38.024 | 900 | 760 | 760 | 760
BROC1- | BROT1- | 2029 | Change | 0 | 0.22 | Cable | 0.0044 | 0.0183 | 0.3167 | 234 | 234 | 234 | 234
BROT1- | LINM1Q | 2029 | Change | 5.774 | 0 | OHL | 0.1373 | 1.3023 | 0.2972 | 134 | 123 | 123 | 123
BUSB2- | WLER2- | 2029 | Addition | 0 | 12 | Cable | 0.0372 | 0.2829 | 51.3179 | 450 | 450 | 450 | 450
CCSS1- | COAL1B | 2029 | Change | 0 | 6.97 | Cable | 0.1096 | 0.6 | 11.4841 | 241 | 241 | 241 | 241
CCSS1- | GAWH1Q | 2029 | Change | 0 | 2.6 | Cable | 0.0409 | 0.2238 | 4.2839 | 241 | 241 | 241 | 241
CCSS3- | CUMH3- | 2029 | Change | 0 | 2.3 | Cable | 0.3182 | 1.0055 | 0.5398 | 38 | 38 | 38 | 38
CHAP1- | GRNA1- | 2029 | Change | 12.83 | 0.35 | Composite | 0.7983 | 3.0495 | 1.0029 | 144 | 144 | 144 | 144
CHAP1- | GRNA1- | 2029 | Change | 12.83 | 0.3 | Composite | 0.797 | 3.0442 | 0.9509 | 144 | 144 | 144 | 144
CLAU1- | MAHI1C | 2029 | Change | 0 | 4 | Cable | 0.0583 | 0.3646 | 5.0764 | 161 | 161 | 161 | 161
CLAW1- | NECU1- | 2029 | Change | 0 | 2.21 | Cable | 0.0438 | 0.2004 | 3.0848 | 133 | 133 | 133 | 133
CLFO1- | CURR1A | 2029 | Addition | 27 | 1.6 | Composite | 2.1169 | 6.0497 | 3.3907 | 133 | 124 | 107 | 124
CLYM2- | LOAN2- | 2029 | Removed | 54.57 | 0 | OHL | 0.1231 | 1.9141 | 17.477 | 1500 | 1500 | 1500 | 1500
CLYM4- | KINN4- | 2029 | Addition | 49.48 | 0 | OHL | 0.0528 | 0.8203 | 33.5272 | 2780 | 2570 | 2220 | 2570
COAL1A | KENN1- | 2029 | Change | 16 | 3.4 | Composite | 1.2963 | 3.7441 | 5.0291 | 167 | 160 | 148 | 160
COAL1A | LEGO1Q | 2029 | Addition | 0 | 4 | Cable | 0.1129 | 0.2596 | 4.9265 | 134 | 123 | 123 | 123
COAL1A | LEGO1R | 2029 | Addition | 0 | 4 | Cable | 0.1129 | 0.2596 | 4.9265 | 134 | 123 | 123 | 123
COAL1A | MIDM1- | 2029 | Removed | 0 | 13.881 | Cable | 0.3802 | 0.937 | 17.3258 | 153 | 134 | 134 | 134
COAL1B | CUMW1- | 2029 | Change | 0 | 11.1 | Cable | 0.3134 | 0.7205 | 14.5825 | 122 | 107 | 107 | 107
COAL1B | DONO1- | 2029 | Change | 0 | 4.806 | Cable | 0.0662 | 0.3007 | 6.9978 | 165 | 165 | 165 | 165
COCK4Q | ECCL4A | 2029 | Removed | 65.9 | 0 | OHL | 0.135 | 1.4191 | 35.4794 | 1120 | 1060 | 990 | 1060
COCK4Q | GALN4- | 2029 | Addition | 35.5 | 0 | OHL | 0.0727 | 0.7644 | 19.1125 | 1120 | 1060 | 990 | 1060
COCK4R | ECCL4B | 2029 | Removed | 65.89 | 0 | OHL | 0.135 | 1.4189 | 35.4739 | 1120 | 1060 | 990 | 1060
COCK4R | GALN4- | 2029 | Addition | 35.5 | 0 | OHL | 0.0727 | 0.7644 | 19.1125 | 1120 | 1060 | 990 | 1060
COYL2- | NECU2- | 2029 | Change | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1540 | 1480 | 1380 | 1480
COYL2- | NECU2- | 2029 | Change | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1540 | 1480 | 1380 | 1480
CRDY3A | EWEH3- | 2029 | Change | 4.736 | 0.35 | Composite | 3.8899 | 14.1591 | 0.06 | 38 | 38 | 38 | 38
CRDY3B | EWEH3- | 2029 | Change | 4.775 | 0.35 | Composite | 3.9211 | 14.2732 | 0.0602 | 38 | 38 | 38 | 38
CRYR4- | FALL4- | 2029 | Change | 13.86 | 0 | OHL | 0.0182 | 0.2732 | 8.1821 | 2473 | 2349 | 2148 | 2349
CRYR4- | TORN4- | 2029 | Removed | 9.36 | 1.97 | Composite | 0.0144 | 0.2171 | 44.1355 | 1415 | 1415 | 1415 | 1415
CULR2- | DEBS2- | 2029 | Removed | 1.6 | 0 | OHL | 0.0069 | 0.0697 | 0.4224 | 1010 | 930 | 805 | 930
CULR2- | LOAN2- | 2029 | Removed | 3.75 | 0.174 | Composite | 0.0171 | 0.1576 | 4.1452 | 1096 | 1029 | 924 | 1029
CULR2- | MOSM2- | 2029 | Removed | 27.746 | 0 | OHL | 0.1257 | 1.1735 | 7.4554 | 1090 | 1030 | 925 | 1030
CULR2T | LOAN2T | 2029 | Removed | 3.79 | 0 | OHL | 0.0169 | 0.1556 | 1.02 | 1090 | 1030 | 925 | 1030
CULR2T | WFIE2- | 2029 | Removed | 25.419 | 0 | OHL | 0.1146 | 1.055 | 6.9136 | 1096 | 1029 | 924 | 1029
CURR2- | SIGH2Q | 2029 | Change | 1.54 | 1.7 | Composite | 0.0169 | 0.1036 | 6.0402 | 120 | 120 | 120 | 120
CURR2- | SIGH2R | 2029 | Change | 1.54 | 1.67 | Composite | 0.0168 | 0.103 | 5.941 | 120 | 120 | 120 | 120
DAER1- | MOFF1A | 2029 | Addition | 6.1 | 6.8 | Composite | 0.6601 | 1.7847 | 8.6959 | 133 | 124 | 107 | 124
DALB2A | DALL2- | 2029 | Addition | 5.7 | 0 | OHL | 0.0241 | 0.2328 | 1.5851 | 1380 | 1320 | 1230 | 1320
DALB2B | WIYH2- | 2029 | Addition | 72.45 | 0 | OHL | 0.3064 | 2.9592 | 20.1469 | 1380 | 1320 | 1230 | 1320
DALL2- | INVR2- | 2029 | Addition | 22.55 | 0 | OHL | 0.0954 | 0.921 | 6.2707 | 570 | 570 | 570 | 570
DALL2- | INVR2- | 2029 | Removed | 22.55 | 0 | OHL | 0.0954 | 0.921 | 6.2707 | 570 | 570 | 570 | 570
DALL2- | WIYH2- | 2029 | Removed | 78.15 | 0 | OHL | 0.3305 | 3.192 | 21.732 | 570 | 570 | 570 | 570
DEBS2- | LOAN2- | 2029 | Addition | 0 | 5 | Cable | 0.0102 | 0.1381 | 30.4106 | 820 | 736 | 674 | 736
DENN2- | DENN2T | 2029 | Addition | 1 | 0 | OHL | 0 | 0 | 0 | 4763 | 4763 | 4763 | 4763
DENN2- | LAMB2- | 2029 | Change | 31.991 | 0 | OHL | 0.1391 | 1.4345 | 8.3553 | 1380 | 1320 | 1230 | 1320
DENN2- | LAMB2T | 2029 | Removed | 31.991 | 0 | OHL | 0.1442 | 1.3015 | 8.8844 | 955 | 885 | 760 | 885
DENN2- | LOAN2- | 2029 | Removed | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DENN2- | LOAN2T | 2029 | Removed | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DENN2T | EERH2- | 2029 | Addition | 24.88 | 0 | OHL | 0.0561 | 0.8727 | 7.9683 | 1500 | 1500 | 1500 | 1500
DENN4- | KINN4- | 2029 | Addition | 16.1 | 0 | OHL | 0.0178 | 0.273 | 10.7108 | 2550 | 2420 | 2210 | 2420
DENN4- | KINN4- | 2029 | Addition | 16.1 | 0 | OHL | 0.0178 | 0.273 | 10.7108 | 2550 | 2420 | 2210 | 2420
DENN4- | LAMB4T | 2029 | Addition | 32.18 | 0 | OHL | 0.0661 | 0.6818 | 17.786 | 2000 | 1920 | 1790 | 1920
DEVM4- | WIYH4Q | 2029 | Change | 28.908 | 0 | OHL | 0.0586 | 0.5888 | 16.3967 | 1390 | 1280 | 1110 | 1280
DEVO1- | STIR1T | 2029 | Change | 5.8 | 5.816 | Composite | 0.3236 | 1.8724 | 7.2413 | 162 | 154 | 141 | 154
DONO1- | MIDM1- | 2029 | Addition | 0 | 1.065 | Cable | 0.0208 | 0.0978 | 1.4807 | 211 | 211 | 211 | 211
DUNB1Q | DUNB1S | 2029 | Change | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 133 | 133 | 133 | 133
DUNB1Q | INWI1Q | 2029 | Change | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 102 | 91 | 91 | 91
DUNB1R | DUNB1T | 2029 | Change | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 133 | 133 | 133 | 133
DUNB1R | INWI1R | 2029 | Change | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 102 | 91 | 91 | 91
DUNE1- | GALA1- | 2029 | Removed | 23.64 | 0 | OHL | 2.1456 | 5.5767 | 1.1477 | 164 | 151 | 127 | 151
DUNE1- | GALN1Q | 2029 | Addition | 12.64 | 0 | OHL | 0.3239 | 2.287 | 0.7972 | 482 | 460 | 420 | 460
DUNE1- | GALN1R | 2029 | Addition | 12.64 | 0 | OHL | 0.3239 | 2.287 | 0.7972 | 482 | 460 | 420 | 460
DUNE1- | SMEA1- | 2029 | Removed | 17.838 | 0.621 | Composite | 1.098 | 3.6602 | 1.7709 | 154 | 131 | 127 | 131
DUNE3- | KEIH3- | 2029 | Change | 0 | 4.746 | Cable | 5.1628 | 4.7962 | 0.3798 | 23 | 23 | 23 | 23
DUNE3- | POGB3- | 2029 | Change | 0 | 3.809 | Cable | 4.4533 | 3.8497 | 0.3048 | 57 | 57 | 57 | 57
ECCL1- | GALA1- | 2029 | Addition | 30.58 | 0 | OHL | 1.6249 | 6.7325 | 1.5989 | 242 | 232 | 214 | 232
ECCL1- | GALA1- | 2029 | Removed | 31.37 | 0 | OHL | 2.8482 | 7.3807 | 1.5285 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 2029 | Removed | 30.94 | 0 | OHL | 2.8144 | 7.1441 | 1.5364 | 132 | 123 | 106 | 123
ECCL1- | GALN1Q | 2029 | Addition | 41.14 | 0 | OHL | 1.8834 | 8.6227 | 2.2702 | 242 | 232 | 214 | 232
ECCL4A | GALN4- | 2029 | Addition | 30.4 | 0 | OHL | 0.0623 | 0.6546 | 16.3668 | 2000 | 1920 | 1790 | 1920
ECCL4A | TORN4- | 2029 | Removed | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
ECCL4B | GALN4- | 2029 | Addition | 30.4 | 0 | OHL | 0.0623 | 0.6546 | 16.3668 | 2000 | 1920 | 1790 | 1920
ECCL4B | TORN4- | 2029 | Removed | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
EERH2- | LOAN2- | 2029 | Removed | 45.82 | 0 | OHL | 0.1034 | 1.6072 | 14.6747 | 1500 | 1500 | 1500 | 1500
EKIS2- | STHA2B | 2029 | Change | 5.8 | 0 | OHL | 0.0245 | 0.2366 | 1.614 | 1372 | 1324 | 1228 | 1324
ELDE1Q | JOHN1Q | 2029 | Change | 0 | 4.37 | Cable | 0.1229 | 0.4314 | 4.832 | 1 | 1 | 1 | 1
ELDE1Q | NEIL1- | 2029 | Change | 3.82 | 0.18 | Composite | 0.1455 | 0.8324 | 0.4574 | 229 | 211 | 183 | 211
ELDE1R | JOHN1R | 2029 | Change | 0 | 4.37 | Cable | 0.1229 | 0.4314 | 4.832 | 1 | 1 | 1 | 1
ELDE1R | NEIL1- | 2029 | Change | 3.82 | 0.23 | Composite | 0.1461 | 0.8373 | 0.5271 | 229 | 211 | 183 | 211
ELVA1- | NLEI1- | 2029 | Addition | 14 | 0 | OHL | 0.7436 | 2.9782 | 0.7639 | 226 | 216 | 200 | 216
EUCH1- | LORG1- | 2029 | Addition | 3.5 | 0 | OHL | 0.2629 | 0.7701 | 0.1843 | 167 | 160 | 148 | 160
EWEH1Q | GRNA1- | 2029 | Change | 15.9 | 0.36 | Composite | 1.2138 | 3.4754 | 1.4335 | 241 | 241 | 241 | 241
FALL4- | SMEA4R | 2029 | Change | 31.1 | 0 | OHL | 0.0414 | 0.6133 | 18.3526 | 2473 | 2349 | 2148 | 2349
GALA1- | GALN1R | 2029 | Addition | 11 | 0 | OHL | 0.2819 | 1.9903 | 0.6938 | 482 | 460 | 420 | 460
GHPS1- | LETH1- | 2029 | Change | 0 | 3 | Cable | 0.0404 | 0.2597 | 9.3604 | 229 | 229 | 229 | 229
GHPS4- | REDS4- | 2029 | Addition | 25 | 0 | OHL | 0.0514 | 0.5412 | 13.4707 | 1995 | 1926 | 1787 | 1926
GHPS4- | REDS4- | 2029 | Addition | 25 | 0 | OHL | 0.0514 | 0.5412 | 13.4707 | 1995 | 1926 | 1787 | 1926
GLGL1B | SAKN1- | 2029 | Change | 0 | 9 | Cable | 0.2541 | 0.5842 | 11.0847 | 181 | 164 | 164 | 164
GLGL1B | SANQ1- | 2029 | Change | 0 | 4 | Cable | 0.0629 | 0.3444 | 6.5906 | 241 | 241 | 241 | 241
GLGL3- | GLMU3- | 2029 | Addition | 0 | 10 | Cable | 2.7669 | 8.7439 | 1.1735 | 40 | 38 | 38 | 38
GLLU1R | NETS1- | 2029 | Change | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49
GLNI1- | MOSM1A | 2029 | Change | 1.41 | 0.09 | Composite | 0.0651 | 0.2344 | 0.3797 | 229 | 229 | 229 | 229
GLNI1- | MOSM1B | 2029 | Change | 1.41 | 0.11 | Composite | 0.0654 | 0.2362 | 0.4421 | 171 | 171 | 171 | 171
GLNI1- | REDH1- | 2029 | Change | 10.547 | 0 | OHL | 0.9555 | 2.3056 | 0.552 | 161 | 156 | 145 | 156
GORG1Q | TELR1Q | 2029 | Change | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 72 | 72 | 72 | 72
GORG1R | TELR1R | 2029 | Change | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 72 | 72 | 72 | 72
HLND1- | WISH1- | 2029 | Addition | 17 | 1.01 | Composite | 1.3056 | 3.8061 | 2.1392 | 167 | 160 | 148 | 160
HOLM1T | QUAN1- | 2029 | Addition | 6 | 0 | OHL | 0.4559 | 1.2998 | 0.3171 | 284 | 278 | 270 | 278
HUCS4- | HUNE4- | 2029 | Change | 0 | 0.665 | Cable | 0.0003 | 0.0089 | 7.3943 | 1448 | 1448 | 1448 | 1448
HUCS4- | HUNE4- | 2029 | Change | 0 | 0.675 | Cable | 0.0003 | 0.009 | 7.5055 | 1448 | 1448 | 1448 | 1448
INWI1Q | TORN1- | 2029 | Change | 0 | 1.15 | Cable | 0.038 | 0.061 | 2.365 | 110 | 110 | 110 | 110
INWI1R | TORN1- | 2029 | Change | 0 | 1.12 | Cable | 0.038 | 0.061 | 2.365 | 110 | 110 | 110 | 110
JUNB1- | JUNV1- | 2029 | Change | 1 | 0 | OHL | 0 | 0.0001 | 0 | 2286 | 2286 | 2286 | 2286
KAIM2- | SMEA2- | 2029 | Change | 8.78 | 0 | OHL | 0.0374 | 0.3629 | 2.4323 | 1090 | 1030 | 925 | 1030
KINC2- | KINN2A | 2029 | Change | 1.9 | 0 | OHL | 0.0043 | 0.0666 | 0.6085 | 1390 | 1280 | 1110 | 1280
KINC2- | KINN2B | 2029 | Change | 0 | 1.9 | Cable | 0.0023 | 0.0168 | 17.1535 | 403 | 403 | 403 | 403
KINC2- | LOAN2Q | 2029 | Removed | 4.28 | 0 | OHL | 0.0186 | 0.1855 | 1.1454 | 765 | 620 | 620 | 620
KINC2- | LOAN2R | 2029 | Removed | 4.28 | 0 | OHL | 0.0186 | 0.1855 | 1.1454 | 765 | 620 | 620 | 620
KINC2- | MOSM2- | 2029 | Addition | 35.776 | 0 | OHL | 0.1612 | 1.5146 | 9.6208 | 1090 | 1030 | 925 | 1030
KINC2- | WFIE2- | 2029 | Addition | 33.449 | 0 | OHL | 0.1501 | 1.3961 | 9.079 | 1090 | 1030 | 925 | 1030
KNOK1- | MAHI1C | 2029 | Addition | 2.5 | 0.5 | Composite | 0.1407 | 0.5692 | 0.9179 | 241 | 230 | 210 | 230
LAMB2- | LAMB2T | 2029 | Removed | 0.001 | 0 | OHL | 0 | 0 | 0 | 1120 | 1060 | 990 | 1060
LAMB2- | WIYH2- | 2029 | Change | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9716 | 1380 | 1320 | 1230 | 1320
LAMB2T | WIYH2- | 2029 | Removed | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1380 | 1320 | 1230 | 1320
LAMB4T | WIYH4Q | 2029 | Addition | 17.88 | 0 | OHL | 0.0357 | 0.3452 | 10.5184 | 2000 | 1920 | 1790 | 1920
LOAN2- | LOAN2Q | 2029 | Removed | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | LOAN2R | 2029 | Removed | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | LOAN2T | 2029 | Removed | 0.001 | 0 | OHL | 0 | 0 | 0 | 1500 | 1500 | 1500 | 1500
LORG1- | SHRG1T | 2029 | Change | 10 | 0 | OHL | 0.7598 | 2.1663 | 0.5285 | 284 | 278 | 270 | 278
MAHI3- | TRLO3- | 2029 | Change | 8.722 | 5.5 | Composite | 12.1114 | 32.1139 | 0.6017 | 25 | 25 | 25 | 25
NECU1C | NOKY1- | 2029 | Change | 0 | 1.3 | Cable | 0.0084 | 0.0773 | 2.2771 | 242 | 242 | 242 | 242
NEIL2- | NEIL2D | 2029 | Change | 0 | 0.2 | Cable | 0.0002 | 0.0028 | 2.4328 | 820 | 736 | 674 | 736
NEIL2- | WIYH2R | 2029 | Change | 25.453 | 0 | OHL | 0.1093 | 1.0873 | 6.9047 | 1372 | 1324 | 1228 | 1324
NETH3- | WISH3T | 2029 | Change | 0 | 0.98 | Cable | 0.1354 | 0.45 | 0.2253 | 29 | 29 | 29 | 29
REDS1A | SPRB1- | 2029 | Addition | 18 | 0 | OHL | 1.3662 | 4.0108 | 0.9183 | 284 | 278 | 270 | 278
REDS1A | SPRB1- | 2029 | Addition | 18 | 0 | OHL | 1.3662 | 4.0108 | 0.9183 | 284 | 278 | 270 | 278
SMEA4Q | TORN4- | 2029 | Removed | 54.32 | 1.94 | Composite | 0.0742 | 1.1033 | 70.0791 | 1360 | 1280 | 1280 | 1280
SMEA4Q | WISH4- | 2029 | Change | 61.77 | 0 | OHL | 0.1313 | 1.2264 | 35.999 | 2778 | 2736 | 2667 | 2736
SMEA4R | WISH4- | 2029 | Change | 61.77 | 0 | OHL | 0.1313 | 1.2264 | 35.999 | 2778 | 2736 | 2667 | 2736
STHA4A | WISH4- | 2029 | Change | 11.6 | 0 | OHL | 0.0243 | 0.2192 | 7.0076 | 2778 | 2736 | 2667 | 2736
STHA4B | WISH4- | 2029 | Change | 11.6 | 0 | OHL | 0.0243 | 0.2192 | 7.0076 | 2778 | 2736 | 2667 | 2736
ARFO1- | KNSH1- | 2032 | Addition | 7 | 0 | OHL | 0.5259 | 1.5402 | 0.3686 | 199 | 191 | 178 | 191
ARRS1- | GRNA1- | 2032 | Addition | 19.2 | 0 | OHL | 1.0219 | 4.0809 | 1.0489 | 3 | 3 | 3 | 3
AUBU1- | MAYB1- | 2032 | Addition | 21 | 0 | OHL | 1.5776 | 4.6207 | 1.1059 | 167 | 160 | 148 | 160
COAL4- | STHA4B | 2032 | Change | 21.73 | 0 | OHL | 0.0463 | 0.4262 | 12.4959 | 2770 | 2770 | 2770 | 2770
CONL2Q | GLRO2- | 2032 | Addition | 2.14 | 0 | OHL | 0.0099 | 0.0977 | 0.5452 | 1096 | 1029 | 924 | 1029
CONL2R | GLRO2- | 2032 | Addition | 2.14 | 0 | OHL | 0.0099 | 0.0977 | 0.5452 | 1096 | 1029 | 924 | 1029
CONL4- | GLRB4- | 2032 | Addition | 12.54 | 0 | OHL | 0.0261 | 0.2255 | 7.8748 | 2770 | 2730 | 2660 | 2730
CONL4- | WFIE4- | 2032 | Addition | 9.94 | 0 | OHL | 0.0207 | 0.1787 | 6.242 | 2770 | 2730 | 2660 | 2730
CRUA2S | CRUA2A | 2032 | Addition | 0 | 0.4 | Cable | 0.0021 | 0.0086 | 1.5414 | 352 | 352 | 352 | 352
CRUA2T | CRUA2B | 2032 | Addition | 0 | 0.4 | Cable | 0.0021 | 0.0086 | 1.5414 | 352 | 352 | 352 | 352
ECCL1- | ORLA1- | 2032 | Addition | 2.2 | 0 | OHL | 0.1025 | 0.4194 | 0.5995 | 200 | 200 | 200 | 200
EKIL2Q | STHA2A | 2032 | Change | 4.79 | 0 | OHL | 0.0217 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965
EKIL2R | STHA2B | 2032 | Removed | 4.79 | 0 | OHL | 0.0216 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965
ELVA4- | GRNA4C | 2032 | Change | 65.54 | 0 | OHL | 0.1406 | 1.3109 | 37.3092 | 2770 | 2770 | 2770 | 2770
ELVA4- | MOFF4- | 2032 | Change | 23.5 | 0 | OHL | 0.0504 | 0.47 | 13.3784 | 2770 | 2770 | 2770 | 2770
GLLU1Q | KNSH1- | 2032 | Addition | 4 | 0 | OHL | 0.3653 | 0.9499 | 0.1945 | 49 | 49 | 49 | 49
GLLU1Q | NETS1- | 2032 | Removed | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49
GLLU1R | NETS1- | 2032 | Addition | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 57 | 57 | 57 | 57
GLRB2- | GLRO2- | 2032 | Removed | 14.68 | 0 | OHL | 0.0664 | 0.6181 | 3.956 | 1090 | 1030 | 925 | 1030
GLRO2- | WFIE2- | 2032 | Removed | 12.08 | 0 | OHL | 0.0547 | 0.5102 | 3.2488 | 1090 | 1030 | 925 | 1030
HAZE1- | HAZE1T | 2032 | Addition | 1.75 | 0 | OHL | 0.1313 | 0.3854 | 0.092 | 112 | 112 | 112 | 112
HAZE1T | REDS1A | 2032 | Addition | 0 | 7.48 | Cable | 0.5334 | 1.5447 | 1.3203 | 112 | 112 | 112 | 112
KINC2- | LOAN2S | 2032 | Addition | 4.28 | 0 | OHL | 0.0185 | 0.1856 | 1.1458 | 1372 | 1324 | 1229 | 1324
KINC4Q | LOAN4S | 2032 | Addition | 4.28 | 0 | OHL | 0.0088 | 0.0877 | 2.4242 | 1995 | 1926 | 1787 | 1926
MOSM2- | WFIE2- | 2032 | Removed | 8.243 | 0 | OHL | 0.0378 | 0.3641 | 2.1507 | 1090 | 1030 | 925 | 1030
MOSM4- | WFIE4- | 2032 | Addition | 8.243 | 0 | OHL | 0.0174 | 0.1577 | 4.9523 | 2770 | 2730 | 2660 | 2730
WFIB2- | WFIE2- | 2032 | Removed | 22.48 | 0 | OHL | 0.1014 | 0.933 | 6.1144 | 1090 | 1030 | 925 | 1030
WFIB4- | WFIE4- | 2032 | Addition | 22.48 | 0 | OHL | 0.0468 | 0.4042 | 14.1168 | 2770 | 2730 | 2660 | 2730
WFIE4- | WFIE4A | 2032 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0 | 2770 | 2770 | 2770 | 2770
AREX1- | AREX1A | 2033 | Change | 0 | 1.7 | Cable | 0.048 | 0.1103 | 2.0938 | 85 | 85 | 85 | 85
AYR-2Q | COYW2S | 2033 | Change | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 1190 | 1190 | 1190 | 1190
AYR-2R | COYW2T | 2033 | Change | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 955 | 955 | 955 | 955
BAGA1Q | BONN1- | 2033 | Change | 18.3 | 0 | OHL | 0.6862 | 3.8983 | 0.9904 | 242 | 223 | 192 | 223
BAGA1R | BONN1- | 2033 | Change | 18.4 | 0 | OHL | 0.69 | 3.9202 | 0.9957 | 242 | 223 | 192 | 223
BLAH1- | GLGL1Q | 2033 | Change | 13.6 | 0.375 | Composite | 0.5207 | 2.9382 | 1.1932 | 297 | 281 | 258 | 281
BLAH1- | GLGL1R | 2033 | Change | 13.6 | 0.375 | Composite | 0.5207 | 2.9382 | 1.1932 | 297 | 281 | 258 | 281
BLCW3- | BLKS3- | 2033 | Change | 0 | 2.801 | Cable | 0.3875 | 1.2246 | 0.6574 | 31 | 31 | 31 | 31
BONN1- | CUMB1Q | 2033 | Removed | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135
BONN1- | CUMB1R | 2033 | Removed | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135
BONN2- | CUMB2- | 2033 | Addition | 10.89 | 0 | OHL | 0.0474 | 0.4987 | 2.7708 | 1380 | 1320 | 1230 | 1320
BONN2- | DENN2T | 2033 | Addition | 3.25 | 0 | OHL | 0.0141 | 0.1488 | 0.8269 | 1380 | 1320 | 1230 | 1320
BONN2A | DENN2- | 2033 | Removed | 3.812 | 0.55 | Composite | 0.0183 | 0.1734 | 4.382 | 722 | 647 | 593 | 647
BONN2B | DENN2- | 2033 | Removed | 3.812 | 0.46 | Composite | 0.0181 | 0.1709 | 3.8346 | 722 | 647 | 593 | 647
BONN4- | KINN4- | 2033 | Addition | 19.1 | 0 | OHL | 0.0238 | 0.331 | 12.5409 | 2778 | 2736 | 2667 | 2736
BONN4- | WISH4- | 2033 | Addition | 40.36 | 0 | OHL | 0.0862 | 0.837 | 22.708 | 2770 | 2730 | 2660 | 2730
BROC1- | BROT1- | 2033 | Change | 0 | 0.22 | Cable | 0.0044 | 0.0183 | 0.3167 | 224 | 191 | 191 | 191
BROT1- | LINM1Q | 2033 | Change | 5.774 | 0 | OHL | 0.1373 | 1.3023 | 0.2972 | 266 | 266 | 266 | 266
BUSB2- | WLER2- | 2033 | Change | 0 | 12 | Cable | 0.0372 | 0.2829 | 51.3179 | 450 | 450 | 450 | 450
CCSS1- | COAL1B | 2033 | Change | 0 | 6.97 | Cable | 0.1096 | 0.6 | 11.4841 | 210 | 210 | 210 | 210
CCSS1- | GAWH1Q | 2033 | Change | 0 | 2.6 | Cable | 0.0409 | 0.2238 | 4.2839 | 210 | 210 | 210 | 210
CCSS3- | CUMH3- | 2033 | Change | 0 | 2.3 | Cable | 0.3182 | 1.0055 | 0.5398 | 28 | 28 | 28 | 28
CHAP1- | GRNA1- | 2033 | Change | 12.83 | 0.35 | Composite | 0.7983 | 3.0495 | 1.0029 | 198 | 186 | 168 | 186
CHAP1- | GRNA1- | 2033 | Change | 12.83 | 0.3 | Composite | 0.797 | 3.0442 | 0.9509 | 198 | 186 | 168 | 186
CLAU1- | MAHI1C | 2033 | Change | 0 | 4 | Cable | 0.0583 | 0.3646 | 5.0764 | 199 | 191 | 178 | 191
CLAW1- | NECU1- | 2033 | Change | 0 | 2.21 | Cable | 0.0438 | 0.2004 | 3.0848 | 182 | 182 | 182 | 182
CLYM2- | EKIL2Q | 2033 | Change | 5.62 | 0 | OHL | 0.0254 | 0.2391 | 1.4926 | 1120 | 1060 | 990 | 1060
CLYM2- | EKIL2R | 2033 | Removed | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060
CLYM4- | DENN4- | 2033 | Addition | 33.63 | 0 | OHL | 0.0359 | 0.5576 | 22.7874 | 2780 | 2570 | 2220 | 2570
CLYM4- | KINN4- | 2033 | Removed | 49.48 | 0 | OHL | 0.0528 | 0.8203 | 33.5272 | 2780 | 2570 | 2220 | 2570
CLYM4- | STHA4B | 2033 | Addition | 10.41 | 0 | OHL | 0.0223 | 0.2094 | 5.8496 | 2770 | 2730 | 2660 | 2730
COAL1A | KENN1- | 2033 | Change | 16 | 3.4 | Composite | 1.2963 | 3.7441 | 5.0291 | 140 | 124 | 124 | 124
COAL1B | CUMW1- | 2033 | Change | 0 | 11.1 | Cable | 0.3134 | 0.7205 | 14.5825 | 120 | 120 | 120 | 120
COAL1B | DONO1- | 2033 | Change | 0 | 4.806 | Cable | 0.0662 | 0.4137 | 6.9978 | 252 | 226 | 226 | 226
COAL4- | REDS4- | 2033 | Change | 11 | 0 | OHL | 0.0235 | 0.2158 | 6.3256 | 2770 | 2770 | 2770 | 2770
COAN4- | REDS4- | 2033 | Change | 11 | 0 | OHL | 0.0235 | 0.2158 | 6.3256 | 2770 | 2770 | 2770 | 2770
COAN4- | STHA4A | 2033 | Change | 21.79 | 0 | OHL | 0.0465 | 0.4275 | 12.5295 | 2770 | 2770 | 2770 | 2770
COCK4Q | GALN4- | 2033 | Change | 35.5 | 0 | OHL | 0.0727 | 0.7644 | 19.1125 | 1120 | 1060 | 990 | 1060
COCK4R | GALN4- | 2033 | Change | 35.5 | 0 | OHL | 0.0727 | 0.7644 | 19.1125 | 1120 | 1060 | 990 | 1060
COYL2- | NECU2- | 2033 | Change | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1490 | 1430 | 1320 | 1430
COYL2- | NECU2- | 2033 | Change | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1490 | 1430 | 1320 | 1430
CRDY3A | EWEH3- | 2033 | Change | 4.736 | 0.35 | Composite | 3.8899 | 14.1591 | 0.06 | 45 | 39 | 39 | 39
CRDY3B | EWEH3- | 2033 | Change | 4.775 | 0.35 | Composite | 3.9211 | 14.2732 | 0.0602 | 45 | 39 | 39 | 39
CRYR4- | FALL4- | 2033 | Change | 13.86 | 0 | OHL | 0.0182 | 0.2732 | 8.1821 | 2470 | 2350 | 2150 | 2350
CUMB2- | NEAR2S | 2033 | Addition | 6.11 | 0 | OHL | 0.0266 | 0.2798 | 1.5546 | 1380 | 1320 | 1230 | 1320
CURR2- | SIGH2Q | 2033 | Change | 1.54 | 1.7 | Composite | 0.0169 | 0.1036 | 6.0402 | 180 | 180 | 180 | 180
CURR2- | SIGH2R | 2033 | Change | 1.54 | 1.67 | Composite | 0.0168 | 0.103 | 5.941 | 180 | 180 | 180 | 180
DEVM4- | WIYH4Q | 2033 | Change | 28.908 | 0 | OHL | 0.0586 | 0.5888 | 16.3967 | 1120 | 1060 | 990 | 1060
DEVO1- | STIR1T | 2033 | Change | 5.8 | 5.816 | Composite | 0.3236 | 1.8724 | 7.2413 | 164 | 130 | 130 | 130
DONO1- | MIDM1- | 2033 | Change | 0 | 1.065 | Cable | 0.0208 | 0.0978 | 1.4807 | 211 | 190 | 190 | 190
DUNB1Q | DUNB1S | 2033 | Change | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 232 | 198 | 188 | 198
DUNB1Q | INWI1Q | 2033 | Change | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 115 | 104 | 104 | 104
DUNB1R | DUNB1T | 2033 | Change | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 232 | 198 | 188 | 198
DUNB1R | INWI1R | 2033 | Change | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 115 | 104 | 104 | 104
DUNE3- | KEIH3- | 2033 | Change | 0 | 4.746 | Cable | 5.1628 | 4.7962 | 0.3798 | 21 | 20 | 20 | 20
DUNE3- | POGB3- | 2033 | Change | 0 | 3.809 | Cable | 4.4533 | 3.8497 | 0.3048 | 21 | 20 | 20 | 20
EERH2- | NEAR2Q | 2033 | Removed | 15.34 | 0 | OHL | 0.077 | 0.632 | 4.283 | 950 | 885 | 760 | 885
EERH2T | NEAR2S | 2033 | Addition | 7.74 | 0 | OHL | 0.033 | 0.3199 | 2.1442 | 1380 | 1320 | 1230 | 1320
EERH2T | NEAR2T | 2033 | Addition | 7.74 | 0 | OHL | 0.033 | 0.3199 | 2.1442 | 1380 | 1320 | 1230 | 1320
EKIS2- | STHA2B | 2033 | Change | 5.8 | 0 | OHL | 0.0245 | 0.2366 | 1.614 | 1050 | 965 | 880 | 965
ELDE1Q | JOHN1Q | 2033 | Change | 0 | 4.37 | Cable | 0.1229 | 0.4314 | 4.832 | 149 | 149 | 149 | 149
ELDE1R | JOHN1R | 2033 | Change | 0 | 4.37 | Cable | 0.1229 | 0.4314 | 4.832 | 149 | 149 | 149 | 149
ELVA4- | REDS4- | 2033 | Change | 15.77 | 0 | OHL | 0.0336 | 0.3093 | 9.0686 | 2770 | 2770 | 2770 | 2770
ELVA4- | REDS4- | 2033 | Change | 15.77 | 0 | OHL | 0.0336 | 0.3093 | 9.0686 | 2770 | 2770 | 2770 | 2770
EWEH1Q | GRNA1- | 2033 | Change | 15.9 | 0.36 | Composite | 1.2138 | 3.4754 | 1.4335 | 295 | 295 | 295 | 295
FALL4- | SMEA4R | 2033 | Change | 31.1 | 0 | OHL | 0.0414 | 0.6133 | 18.3526 | 2520 | 2400 | 2190 | 2400
GAWH3- | HAHA3- | 2033 | Change | 0 | 5.07 | Cable | 1.7086 | 4.8419 | 0.5551 | 36 | 34 | 34 | 34
GHPS1- | LETH1- | 2033 | Change | 0 | 3 | Cable | 0.0404 | 0.2597 | 9.3604 | 200 | 200 | 200 | 200
GLGL1B | SAKN1- | 2033 | Change | 0 | 9 | Cable | 0.2541 | 0.5842 | 11.0847 | 166 | 166 | 166 | 166
GLGL1B | SANQ1- | 2033 | Change | 0 | 4 | Cable | 0.0629 | 0.3444 | 6.5906 | 283 | 277 | 269 | 277
GLLU1R | NETS1- | 2033 | Removed | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49
GLNI1- | MOSM1A | 2033 | Change | 1.41 | 0.09 | Composite | 0.0651 | 0.2344 | 0.3797 | 265 | 246 | 212 | 246
GLNI1- | MOSM1B | 2033 | Change | 1.41 | 0.11 | Composite | 0.0654 | 0.2362 | 0.4421 | 265 | 246 | 212 | 246
GLNI1- | REDH1- | 2033 | Change | 10.547 | 0 | OHL | 0.9555 | 2.3056 | 0.552 | 161 | 154 | 141 | 154
GNSH1- | KEOO1Q | 2033 | Change | 10.1 | 0.9 | Composite | 0.7816 | 2.2655 | 2.0167 | 272 | 231 | 231 | 231
GORG1Q | TELR1Q | 2033 | Change | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 24 | 24 | 24 | 24
GORG1R | TELR1R | 2033 | Change | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 24 | 24 | 24 | 24
GRNA4- | HAKB4B | 2033 | Change | 1.97 | 0 | OHL | 0.0042 | 0.0394 | 1.1215 | 2770 | 2770 | 2770 | 2770
HAKB4- | MOFF4C | 2033 | Change | 43.79 | 0 | OHL | 0.0939 | 0.8758 | 24.9293 | 2770 | 2770 | 2770 | 2770
HUCS4- | HUNE4- | 2033 | Change | 0 | 0.665 | Cable | 0.0003 | 0.0089 | 7.3943 | 1444 | 1444 | 1444 | 1444
HUCS4- | HUNE4- | 2033 | Change | 0 | 0.675 | Cable | 0.0003 | 0.009 | 7.5055 | 1444 | 1444 | 1444 | 1444
INWI1Q | TORN1- | 2033 | Change | 0 | 1.15 | Cable | 0.038 | 0.061 | 2.365 | 115 | 104 | 104 | 104
INWI1R | TORN1- | 2033 | Change | 0 | 1.12 | Cable | 0.038 | 0.061 | 2.365 | 115 | 104 | 104 | 104
JUNB1- | JUNV1- | 2033 | Change | 1 | 0 | OHL | 0 | 0.0001 | 0 | 1000 | 1000 | 1000 | 1000
KAIM2- | SMEA2- | 2033 | Change | 8.78 | 0 | OHL | 0.0374 | 0.3629 | 2.4323 | 1000 | 1000 | 1000 | 1000
KINC2- | MOSM2- | 2033 | Removed | 35.776 | 0 | OHL | 0.1612 | 1.5146 | 9.6208 | 1090 | 1030 | 925 | 1030
KINC2- | WFIE2- | 2033 | Removed | 33.449 | 0 | OHL | 0.1501 | 1.3961 | 9.079 | 1090 | 1030 | 925 | 1030
KINN4- | MOSM4- | 2033 | Addition | 36.996 | 0 | OHL | 0.0718 | 0.6743 | 23.0985 | 2770 | 2730 | 2660 | 2730
KINN4- | WFIE4- | 2033 | Addition | 34.639 | 0 | OHL | 0.0667 | 0.6224 | 21.8425 | 2770 | 2730 | 2660 | 2730
KNSH1- | NETS1- | 2033 | Addition | 18 | 0 | OHL | 1.6438 | 4.2747 | 0.8752 | 135 | 135 | 135 | 135
LORG1- | SHRG1T | 2033 | Change | 10 | 0 | OHL | 0.7598 | 2.1663 | 0.5285 | 284 | 279 | 270 | 279
MAHI3- | TRLO3- | 2033 | Change | 8.722 | 5.5 | Composite | 12.1114 | 32.1139 | 0.6017 | 40 | 30 | 30 | 30
NEAR2- | NEAR2T | 2033 | Addition | 7.6 | 0 | OHL | 0.0331 | 0.3408 | 1.9829 | 1380 | 1320 | 1230 | 1320
NEAR2- | WISH2- | 2033 | Change | 15.76 | 0 | OHL | 0.0685 | 0.7067 | 4.1118 | 1380 | 1320 | 1230 | 1320
NEAR2Q | WISH2- | 2033 | Removed | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 955 | 885 | 760 | 885
NECU1C | NOKY1- | 2033 | Change | 0 | 1.3 | Cable | 0.0084 | 0.0773 | 2.2771 | 261 | 261 | 261 | 261
NEIL2- | NEIL2D | 2033 | Change | 0 | 0.2 | Cable | 0.0002 | 0.0028 | 2.4328 | 500 | 500 | 500 | 500
NEIL2- | WIYH2R | 2033 | Change | 25.453 | 0 | OHL | 0.1093 | 1.0873 | 6.9047 | 1120 | 1060 | 990 | 1060
NETH3- | WISH3T | 2033 | Change | 0 | 0.98 | Cable | 0.1354 | 0.45 | 0.2253 | 37 | 36 | 36 | 36
SMEA4Q | WISH4- | 2033 | Change | 61.77 | 0 | OHL | 0.1313 | 1.2264 | 35.999 | 2770 | 2730 | 2660 | 2730
SMEA4R | WISH4- | 2033 | Change | 61.77 | 0 | OHL | 0.1313 | 1.2264 | 35.999 | 2770 | 2730 | 2660 | 2730
STHA4A | WISH4- | 2033 | Change | 11.6 | 0 | OHL | 0.0243 | 0.2192 | 7.0076 | 2770 | 2730 | 2660 | 2730
STHA4B | WISH4- | 2033 | Change | 11.6 | 0 | OHL | 0.0243 | 0.2192 | 7.0076 | 2770 | 2730 | 2660 | 2730
BONN1- | STIR1S | 2035 | Change | 3.3 | 13.05 | Composite | 0.2578 | 1.7865 | 22.5373 | 238 | 219 | 191 | 219
BONN1- | STIR1T | 2035 | Change | 3.3 | 13.05 | Composite | 0.2578 | 1.7865 | 22.5373 | 238 | 219 | 191 | 219
BRAP1- | ERSK1Q | 2035 | Change | 3.17 | 5.4 | Composite | 0.3963 | 1.0618 | 12.4517 | 121 | 110 | 106 | 110
COCK4Q | GALN4- | 2035 | Removed | 35.5 | 0 | OHL | 0.0727 | 0.7644 | 19.1125 | 1120 | 1060 | 990 | 1060
COYL4- | KILS4T | 2035 | Addition | 14.69 | 0 | OHL | 0.0299 | 0.2837 | 8.6417 | 2780 | 2740 | 2670 | 2740
COYL4- | NECU4- | 2035 | Addition | 14.3 | 0 | OHL | 0.0291 | 0.2762 | 8.4123 | 2030 | 1930 | 1770 | 1930
COYL4- | NECU4- | 2035 | Addition | 14.3 | 0 | OHL | 0.0291 | 0.2762 | 8.4123 | 2030 | 1930 | 1770 | 1930
COYW2S | KILS2- | 2035 | Removed | 13.37 | 0 | OHL | 0.0588 | 0.5269 | 3.8357 | 1500 | 1500 | 1500 | 1500
COYW2T | KILS2- | 2035 | Removed | 13.37 | 0 | OHL | 0.0588 | 0.5269 | 3.8357 | 1500 | 1500 | 1500 | 1500
CURR2- | GRMO2- | 2035 | Change | 42.88 | 0 | OHL | 0.185 | 1.7221 | 12.1108 | 1120 | 1060 | 990 | 1060
CURR2- | KINC2- | 2035 | Removed | 55.76 | 0 | OHL | 0.2531 | 2.2958 | 15.4272 | 1090 | 1030 | 925 | 1030
CURR4T | HARB4Q | 2035 | Addition | 17.7 | 0 | OHL | 0.0361 | 0.336 | 10.5766 | 2770 | 2730 | 2660 | 2730
DUMN4- | GHPS4- | 2035 | Addition | 60 | 0 | OHL | 0.0504 | 0.9714 | 41.8131 | 3076 | 2827 | 2411 | 2827
DUMN4- | GHPS4- | 2035 | Addition | 60 | 0 | OHL | 0.0504 | 0.9714 | 41.8131 | 3076 | 2827 | 2411 | 2827
DUMN4- | WYSE4- | 2035 | Addition | 25 | 0 | OHL | 0.021 | 0.4047 | 17.4221 | 3076 | 2827 | 2411 | 2827
DUMN4- | WYSE4- | 2035 | Addition | 25 | 0 | OHL | 0.021 | 0.4047 | 17.4221 | 3076 | 2827 | 2411 | 2827
ETTR4- | GALN4- | 2035 | Addition | 31 | 0 | OHL | 0.026 | 0.5019 | 21.6034 | 3464 | 3464 | 3320 | 3464
ETTR4- | TEVI4A | 2035 | Addition | 28 | 0 | OHL | 0.0235 | 0.4533 | 19.5128 | 3464 | 3464 | 3320 | 3464
ETTR4A | GALN4- | 2035 | Addition | 31 | 0 | OHL | 0.026 | 0.5019 | 21.6034 | 3464 | 3464 | 3320 | 3464
ETTR4A | TEVI4- | 2035 | Addition | 28 | 0 | OHL | 0.0235 | 0.4533 | 19.5128 | 3464 | 3464 | 3320 | 3464
GALN4- | HARB4Q | 2035 | Addition | 75.1 | 0 | OHL | 0.063 | 1.2159 | 52.336 | 3464 | 3464 | 3320 | 3464
GALN4- | HARB4R | 2035 | Addition | 75.1 | 0 | OHL | 0.063 | 1.2159 | 52.336 | 3464 | 3464 | 3320 | 3464
GHPS4- | NECU4- | 2035 | Addition | 0 | 26 | Cable | 0.0299 | 0.4721 | 16.2822 | 3820 | 3630 | 3320 | 3630
GHPS4- | NECU4- | 2035 | Addition | 0 | 26 | Cable | 0.0299 | 0.4721 | 16.2822 | 3820 | 3630 | 3320 | 3630
GRMO2- | KINC2- | 2035 | Addition | 14.96 | 0 | OHL | 0.0645 | 0.6008 | 4.2252 | 1120 | 1060 | 990 | 1060
GRMO2- | KINC2- | 2035 | Removed | 14.96 | 0 | OHL | 0.068 | 0.6184 | 4.1277 | 1050 | 965 | 880 | 965
HARB4Q | SMEA4Q | 2035 | Addition | 33.44 | 0 | OHL | 0.0695 | 0.624 | 20.276 | 2770 | 2730 | 2660 | 2730
HARB4Q | WISH4- | 2035 | Addition | 28.33 | 0 | OHL | 0.0602 | 0.5625 | 16.5105 | 2770 | 2730 | 2660 | 2730
HARB4R | KINN4- | 2035 | Addition | 42.04 | 0 | OHL | 0.0858 | 0.7974 | 25.1377 | 2770 | 2730 | 2660 | 2730
HARB4R | SMEA4R | 2035 | Addition | 33.44 | 0 | OHL | 0.0695 | 0.624 | 20.276 | 2770 | 2730 | 2660 | 2730
HARB4R | WISH4- | 2035 | Addition | 28.33 | 0 | OHL | 0.0602 | 0.5625 | 16.5105 | 2770 | 2730 | 2660 | 2730
KINC2- | LOAN2S | 2035 | Change | 0.36 | 0 | OHL | 0.0015 | 0.0147 | 0.1001 | 1372 | 1324 | 1229 | 1324
SMEA4Q | WISH4- | 2035 | Removed | 61.77 | 0 | OHL | 0.1313 | 1.2264 | 35.999 | 2770 | 2730 | 2660 | 2730
SMEA4R | WISH4- | 2035 | Removed | 61.77 | 0 | OHL | 0.1313 | 1.2264 | 35.999 | 2770 | 2730 | 2660 | 2730
TEVB4Q | TEVI4A | 2035 | Addition | 17 | 0 | OHL | 0.0143 | 0.2752 | 11.847 | 3464 | 3464 | 3320 | 3464
TEVB4R | TEVI4- | 2035 | Addition | 17 | 0 | OHL | 0.0143 | 0.2752 | 11.847 | 3464 | 3464 | 3320 | 3464
WCNB4Q | WYSE4- | 2035 | Addition | 7 | 0 | OHL | 0.0059 | 0.1133 | 4.8782 | 3464 | 3464 | 3320 | 3464
WCNB4R | WYSE4- | 2035 | Addition | 7 | 0 | OHL | 0.0059 | 0.1133 | 4.8782 | 3464 | 3464 | 3320 | 3464

## B-2-2c
B-2-2c - NGET Circuit Changes 2025/26 to 2035/36
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
BENR41 | NEWX41 | 2025 | Addition | 0 | 4.272 | Cable | 0.0029 | 0.0571 | 34.5413 | 1100 | 1100 | 1100 | 1100
BENR41 | WIMB41 | 2025 | Addition | 0 | 8.429 | Cable | 0.0058 | 0.1128 | 68.1528 | 1250 | 1250 | 1250 | 1250
BOLN41 | LHOR4A | 2025 | Addition | 28.1 | 0 | OHL | 0.0305 | 0.4887 | 18.5239 | 3102 | 2935 | 2765 | 2935
BOLN41 | NINF41 | 2025 | Removed | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
BOLN41 | NINF41 | 2025 | Change | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8859 | 3102 | 2935 | 2765 | 2935
BRLE41 | FLEE41 | 2025 | Change | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 3180 | 3000 | 2690 | 3000
BRLE41 | FLEE41 | 2025 | Change | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 3180 | 3000 | 2690 | 3000
CARR41 | DAIN41 | 2025 | Change | 2.545 | 0 | OHL | 0.004 | 0.0488 | 1.5263 | 3100 | 3100 | 3100 | 3100
CARR41 | DAIN41 | 2025 | Change | 3.352 | 0 | OHL | 0.0059 | 0.0653 | 1.9782 | 3102 | 3048 | 2958 | 3048
CARR42 | DAIN41 | 2025 | Change | 2.063 | 0 | OHL | 0.0032 | 0.0397 | 1.2352 | 1500 | 1500 | 1500 | 1500
COTT41 | KEAD4C | 2025 | Change | 34.628 | 0 | OHL | 0.054 | 0.673 | 20.467 | 3100 | 3050 | 2960 | 3050
COTT41 | KEAD4D | 2025 | Change | 34.479 | 0 | OHL | 0.0538 | 0.6702 | 20.3774 | 3100 | 3050 | 2960 | 3050
GART4B | KEAD41 | 2025 | Change | 5.689 | 0 | OHL | 0.0062 | 0.0989 | 3.7497 | 3420 | 3260 | 2980 | 3260
HAKB4- | HARK41 | 2025 | Change | 9.857 | 0 | OHL | 0.0157 | 0.1946 | 5.7661 | 2213 | 2126 | 1980 | 2126
HAKB4B | HARG41 | 2025 | Addition | 10.107 | 0 | OHL | 0.0161 | 0.1995 | 5.9123 | 2170 | 2084 | 1941 | 2084
HAKB4B | HARK41 | 2025 | Removed | 9.857 | 0 | OHL | 0.0176 | 0.1957 | 5.7308 | 2170 | 2084 | 1941 | 2084
HARG41 | HARK41 | 2025 | Addition | 0.1 | 0 | OHL | 0.0001 | 0.0019 | 0.0602 | 2771 | 2771 | 2771 | 2771
HARG41 | HUTT41 | 2025 | Addition | 81.544 | 0 | OHL | 0.127 | 1.5659 | 48.8916 | 2771 | 2771 | 2663 | 2771
HARK13 | JUNV1- | 2025 | Change | 1 | 0 | OHL | 1.194 | 2.729 | 0.743 | 199 | 191 | 178 | 191
HARK41 | HUTT41 | 2025 | Removed | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2663 | 2771
KLYN41 | NECT41 | 2025 | Addition | 30.347 | 0 | OHL | 0.0269 | 0.5209 | 20.404 | 2520 | 2520 | 2520 | 2520
KLYN41 | WALP41 | 2025 | Addition | 16.672 | 0 | OHL | 0.0148 | 0.286 | 11.2124 | 2520 | 2520 | 2520 | 2520
LHOR4B | NINF41 | 2025 | Addition | 23.2 | 0 | OHL | 0.0252 | 0.4035 | 15.2937 | 3102 | 2935 | 2765 | 2935
NECT41 | NECT4A | 2025 | Removed | 0 | 0 | Zero Length | 0 | 0 | 0 | 1364 | 1364 | 1250 | 1250
NECT41 | NECT4B | 2025 | Removed | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159
NECT41 | NORM41 | 2025 | Addition | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3326 | 3326 | 3317 | 3326
NECT41 | NORM41 | 2025 | Addition | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3326 | 3258 | 3060 | 3258
NECT41 | WALP41 | 2025 | Addition | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3326 | 3160 | 2971 | 3160
NECT4A | NORM41 | 2025 | Removed | 35.652 | 0 | OHL | 0.0316 | 0.6124 | 23.9626 | 3326 | 3326 | 3317 | 3326
NECT4A | WALP41 | 2025 | Removed | 43.459 | 0 | OHL | 0.0385 | 0.7464 | 29.2107 | 3326 | 3326 | 3317 | 3326
NECT4B | NORM41 | 2025 | Removed | 35.652 | 0 | OHL | 0.0316 | 0.6124 | 23.9626 | 3326 | 3258 | 3060 | 3258
NECT4B | WALP41 | 2025 | Removed | 43.459 | 0 | OHL | 0.0385 | 0.7464 | 29.2107 | 3326 | 3160 | 2971 | 3160
NEWX21 | WIMB21 | 2025 | Removed | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 827 | 827 | 779 | 779
NEWX21 | WIMB21 | 2025 | Removed | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 819 | 819 | 813 | 813
NEWX41 | WIMB41 | 2025 | Addition | 0 | 12.688 | Cable | 0.0087 | 0.1697 | 102.5891 | 1100 | 1100 | 1100 | 1100
SALH41 | SALH42 | 2025 | Addition | 0 | 0 | SSSC | 0 | 0.125 | 0 | 1831 | 1739 | 1588 | 1739
SUND41 | WYMO41 | 2025 | Change | 18.156 | 0 | OHL | 0.0196 | 0.302 | 12.5826 | 3180 | 3180 | 3180 | 3180
WIMB21 | WIMB2A | 2025 | Removed | 0 | 0 | Zero Length | 0 | 0 | 0 | 995 | 930 | 728 | 806
ALVE4A | INDQ41 | 2027 | Removed | 97.176 | 0 | OHL | 0.2121 | 1.9367 | 56.1415 | 1389 | 1284 | 1108 | 1284
ALVE4A | TAUN41 | 2027 | Removed | 73.293 | 0 | OHL | 0.117 | 1.477 | 42.0344 | 1389 | 1284 | 1108 | 1284
ALVE4B | INDQ41 | 2027 | Removed | 97.294 | 0 | OHL | 0.2123 | 1.9391 | 56.209 | 1389 | 1284 | 1108 | 1284
ALVE4B | TAUN42 | 2027 | Removed | 73.298 | 0 | OHL | 0.117 | 1.4771 | 42.0372 | 1389 | 1284 | 1108 | 1284
ALVE4A | INDQ41 | 2027 | Addition | 97.176 | 0 | OHL | 0.2121 | 1.9367 | 56.1415 | 1389 | 1284 | 1108 | 1284
ALVE4A | INDQ41 | 2027 | Addition | 97.294 | 0 | OHL | 0.2123 | 1.9391 | 56.2092 | 1389 | 1284 | 1108 | 1284
ALVE4A | TAUN41 | 2027 | Addition | 73.293 | 0 | OHL | 0.117 | 1.477 | 42.0344 | 1389 | 1284 | 1108 | 1284
ALVE4A | TAUN42 | 2027 | Addition | 73.437 | 0 | OHL | 0.1172 | 1.4799 | 42.117 | 1389 | 1284 | 1108 | 1284
BODE41 | CONQ41 | 2027 | Addition | 30.717 | 0.21 | Composite | 0.0335 | 0.5367 | 22.5401 | 2665 | 2561 | 2217 | 2561
BODE41 | CONQ42 | 2027 | Addition | 30.717 | 0.21 | Composite | 0.0335 | 0.5367 | 22.5401 | 2665 | 2561 | 2217 | 2561
BODE41 | GWYN4A | 2027 | Removed | 0 | 0.8 | Cable | 0.0008 | 0.0094 | 7.6404 | 1056 | 1056 | 980 | 980
BODE41 | GWYN4B | 2027 | Removed | 0.5 | 0 | OHL | 0.0005 | 0.0087 | 0.3284 | 2771 | 2695 | 2510 | 2695
BODE41 | PENT41 | 2027 | Addition | 49.211 | 0.8 | Composite | 0.0653 | 0.9665 | 36.8939 | 2779 | 2568 | 2217 | 2568
BODE41 | PENT41 | 2027 | Addition | 49.211 | 0.8 | Composite | 0.0653 | 0.9665 | 36.8939 | 2779 | 2568 | 2217 | 2568
BRIM2A | TOTT21 | 2027 | Change | 7.437 | 0.311 | Composite | 0.025 | 0.3106 | 5.4901 | 2310 | 2100 | 2030 | 2100
BRIM2A | WALX22 | 2027 | Change | 5.865 | 0 | OHL | 0.0193 | 0.2381 | 1.6636 | 2310 | 2100 | 2030 | 2100
BRIM2B | TOTT22 | 2027 | Change | 7.305 | 0.393 | Composite | 0.0247 | 0.3075 | 6.344 | 2310 | 2100 | 2030 | 2100
BRIM2B | WALX22 | 2027 | Change | 5.997 | 0 | OHL | 0.0198 | 0.2434 | 1.701 | 2310 | 2100 | 2030 | 2100
BRIM2C | TOTT22 | 2027 | Removed | 7.455 | 0.235 | Composite | 0.0344 | 0.3223 | 4.5788 | 1085 | 1031 | 925 | 1031
BRIM2C | WALX21 | 2027 | Removed | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIM2D | TOTT21 | 2027 | Removed | 7.455 | 0.384 | Composite | 0.0347 | 0.3264 | 6.1984 | 1085 | 1031 | 925 | 1031
BRIM2D | WALX21 | 2027 | Removed | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIM4C | HACK41 | 2027 | Addition | 13.209 | 0.527 | Composite | 0.0209 | 0.2597 | 13.6792 | 3100 | 3100 | 3100 | 3100
BRIM4C | WALX41 | 2027 | Addition | 5.97 | 0 | OHL | 0.0093 | 0.1145 | 3.5827 | 3100 | 3100 | 3100 | 3100
BRIM4D | HACK41 | 2027 | Addition | 13.209 | 0.676 | Composite | 0.021 | 0.2614 | 15.3056 | 3100 | 3100 | 3100 | 3100
BRIM4D | WALX41 | 2027 | Addition | 5.97 | 0 | OHL | 0.0093 | 0.1145 | 3.5827 | 3100 | 3100 | 3100 | 3100
BRLE41 | FLEE41 | 2027 | Change | 17.555 | 0 | OHL | 0.0156 | 0.3015 | 11.7995 | 3320 | 3320 | 3130 | 3320
BRLE41 | FLEE41 | 2027 | Change | 17.555 | 0 | OHL | 0.0156 | 0.3015 | 11.7995 | 3330 | 3160 | 2970 | 3160
BRLE41 | MELK41 | 2027 | Change | 81.569 | 0 | OHL | 0.1484 | 1.6229 | 47.2724 | 2240 | 1524 | 1524 | 1524
BRLE41 | MELK41 | 2027 | Change | 82.134 | 0 | OHL | 0.1493 | 1.6341 | 47.6022 | 2240 | 1524 | 1524 | 1524
CELL41 | CELL42 | 2027 | Addition | 0 | 0 | Series Compensation | 0 | 0.375 | 0 | 2420 | 2330 | 2170 | 2330
CELL41 | CELL43 | 2027 | Addition | 0 | 0 | Series Compensation | 0 | 0.125 | 0 | 2420 | 2330 | 2170 | 2330
CONQ41 | GWYN4B | 2027 | Removed | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 2665 | 2561 | 2217 | 2561
CONQ42 | GWYN4A | 2027 | Removed | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 2665 | 2561 | 2217 | 2561
COTT42 | COTT43 | 2027 | Addition | 0 | 0 | Series Compensation | 0 | 0.3125 | 0 | 3326 | 3160 | 2971 | 3160
CREB41 | CREB41 | 2027 | Addition | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 1386 | 1386 | 1386 | 1386
CREB41 | CREB41 | 2027 | Addition | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 1386 | 1386 | 1386 | 1386
CREB41 | CREB42 | 2027 | Addition | 14.835 | 0 | OHL | 0.0131 | 0.2548 | 9.9719 | 3075 | 3075 | 3075 | 3075
CREB41 | CREB42 | 2027 | Addition | 14.904 | 0 | OHL | 0.0132 | 0.256 | 10.0181 | 3075 | 3075 | 3075 | 3075
CREB41 | THTO41 | 2027 | Removed | 29.671 | 0 | OHL | 0.0263 | 0.5096 | 19.9438 | 3075 | 2876 | 2663 | 2876
CREB41 | THTO42 | 2027 | Removed | 29.809 | 0 | OHL | 0.0264 | 0.512 | 20.0362 | 3075 | 2876 | 2663 | 2876
CREB42 | THTO41 | 2027 | Addition | 14.835 | 0 | OHL | 0.0131 | 0.2548 | 9.9719 | 3075 | 3075 | 3075 | 3075
CREB42 | THTO42 | 2027 | Addition | 14.904 | 0 | OHL | 0.0132 | 0.256 | 10.0181 | 3075 | 3075 | 3075 | 3075
DISS4A | NORM41 | 2027 | Change | 29.7 | 0 | OHL | 0.0263 | 0.5101 | 19.9633 | 3326 | 3326 | 3320 | 3326
DRAX41 | EGGB42 | 2027 | Change | 11.188 | 0.64 | Composite | 0.0129 | 0.1991 | 15.0423 | 2089 | 2089 | 1878 | 1878
EGGB41 | MFSN41 | 2027 | Addition | 10.37 | 0 | OHL | 0.0091 | 0.1781 | 6.9831 | 3070 | 2830 | 2420 | 2830
EGGB41 | MONF4A | 2027 | Removed | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 1970 | 1970 | 1970 | 1970
EGGB42 | MFSN41 | 2027 | Addition | 10.37 | 0 | OHL | 0.0091 | 0.1781 | 6.9831 | 3070 | 2830 | 2420 | 2830
EGGB42 | MONF41 | 2027 | Removed | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 2779 | 2568 | 2217 | 2568
GRAI41 | WALE41 | 2027 | Addition | 1.68 | 0 | OHL | 0.0018 | 0.0292 | 1.1075 | 3326 | 3160 | 2633 | 2813
GWYD41 | TRAW41 | 2027 | Addition | 39.445 | 0 | OHL | 0.0615 | 0.7568 | 23.67 | 3102 | 3048 | 2958 | 3048
GWYD41 | TREU4A | 2027 | Addition | 25.573 | 0 | OHL | 0.0398 | 0.4907 | 15.3454 | 3102 | 3048 | 2958 | 3048
GWYN4A | PENT41 | 2027 | Removed | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568
GWYN4B | PENT41 | 2027 | Removed | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568
HACK21 | TOTT21 | 2027 | Removed | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 1093 | 1031 | 926 | 1031
HACK22 | TOTT22 | 2027 | Removed | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 1093 | 1031 | 926 | 1031
HAKB4- | HARG41 | 2027 | Addition | 10.107 | 0 | OHL | 0.0161 | 0.1995 | 5.9123 | 2213 | 2126 | 1980 | 2126
HAKB4- | HARK41 | 2027 | Removed | 9.857 | 0 | OHL | 0.0157 | 0.1946 | 5.7661 | 2213 | 2126 | 1980 | 2126
HAMB4A | STAH4A | 2027 | Change | 3.926 | 0 | OHL | 0.007 | 0.078 | 2.2826 | 1970 | 1870 | 1710 | 1870
HAMB4B | STAH4B | 2027 | Change | 3.926 | 0 | OHL | 0.007 | 0.078 | 2.2826 | 1970 | 1970 | 1970 | 1970
HARG41 | HARK41 | 2027 | Removed | 0.1 | 0 | OHL | 0.0001 | 0.0019 | 0.0602 | 2771 | 2771 | 2771 | 2771
HARG41 | HUTT41 | 2027 | Addition | 81.544 | 0 | OHL | 0.127 | 1.5659 | 48.8916 | 2771 | 2771 | 2771 | 2771
HARK21 | HARK21 | 2027 | Removed | 0 | 0.05 | Cable | 0.0001 | 0.0013 | 0.258 | 953 | 953 | 953 | 953
HARK21 | HARK23 | 2027 | Removed | 0 | 0 | SSSC | 0 | 1.8512 | 0 | 774 | 774 | 676 | 676
HARK21 | HARK24 | 2027 | Removed | 0 | 0 | SSSC | 0 | 3.7025 | 0 | 854 | 795 | 700 | 795
HARK41 | HUTT41 | 2027 | Removed | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2771 | 2771
HURS21 | NEWX21 | 2027 | Change | 0 | 18.504 | Cable | 0.027 | 0.5237 | 70.7162 | 1200 | 1200 | 1200 | 1200
HURS21 | NEWX21 | 2027 | Change | 0 | 18.442 | Cable | 0.0269 | 0.5219 | 70.4793 | 1200 | 1200 | 1200 | 1200
KINO41 | WALE41 | 2027 | Addition | 9.467 | 0.8 | Composite | 0.0104 | 0.1673 | 17.2184 | 3326 | 3160 | 2633 | 2813
KNAR21 | MONF22 | 2027 | Removed | 38.531 | 0.141 | Composite | 0.2716 | 1.7712 | 11.0429 | 551 | 513 | 443 | 513
KNAR21 | POPP21 | 2027 | Removed | 49.192 | 0 | OHL | 0.3299 | 2.3254 | 12.2192 | 551 | 512 | 442 | 512
KNAR21 | TADT2A | 2027 | Addition | 25 | 0 | OHL | 0.1224 | 1.0976 | 6.5267 | 1500 | 1500 | 1300 | 1300
KNAR21 | TADT2B | 2027 | Addition | 25 | 0 | OHL | 0.1224 | 1.0976 | 6.5267 | 1500 | 1500 | 1300 | 1500
MFSN2A | TADT2A | 2027 | Addition | 14.18 | 0 | OHL | 0.0694 | 0.6225 | 3.7019 | 1500 | 1500 | 1300 | 1500
MFSN2B | TADT2B | 2027 | Addition | 14.18 | 0.6 | Composite | 0.0705 | 0.6359 | 10.1219 | 1500 | 1500 | 1300 | 1500
MONF21 | POPP21 | 2027 | Removed | 37.84 | 0 | OHL | 0.208 | 2.0034 | 8.337 | 682 | 629 | 538 | 629
NORT41 | OBST4A | 2027 | Addition | 70.35 | 0 | OHL | 0.1279 | 1.4458 | 39.4518 | 2010 | 1910 | 1750 | 1910
NORT41 | OBST4B | 2027 | Addition | 70.35 | 0 | OHL | 0.1279 | 1.4458 | 39.4518 | 2009 | 1911 | 1746 | 1911
NORT41 | OSBA41 | 2027 | Removed | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911
NORT41 | OSBA42 | 2027 | Removed | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911
NORT41 | SPEN41 | 2027 | Change | 21.134 | 2 | Composite | 0.0276 | 0.4062 | 12.7287 | 2810 | 2700 | 2510 | 2700
NORT41 | SPEN42 | 2027 | Change | 21.134 | 2 | Composite | 0.0276 | 0.4062 | 12.7287 | 2810 | 2700 | 2510 | 2700
OBST4A | OSBA41 | 2027 | Addition | 13.35 | 0 | OHL | 0.0243 | 0.2744 | 7.4866 | 2009 | 1911 | 1746 | 1911
OBST4A | YORK4A | 2027 | Addition | 2.8 | 0 | OHL | 0.0051 | 0.0575 | 1.5702 | 1500 | 1500 | 1750 | 1300
OBST4B | OSBA42 | 2027 | Addition | 13.35 | 0 | OHL | 0.0243 | 0.2744 | 7.4866 | 2009 | 1911 | 1750 | 1911
OBST4B | YORK4B | 2027 | Addition | 2.8 | 0 | OHL | 0.0051 | 0.0575 | 1.5702 | 1500 | 1500 | 1750 | 1300
OSBA41 | THTO43 | 2027 | Change | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 3326 | 3160 | 2980 | 3160
OSBA42 | THTO42 | 2027 | Change | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 3326 | 3160 | 2980 | 3160
OVER21 | POPP21 | 2027 | Addition | 4.729 | 0 | OHL | 0.0257 | 0.2475 | 1.0505 | 680 | 540 | 540 | 680
OVER21 | POPP21 | 2027 | Addition | 4.634 | 0 | OHL | 0.0254 | 0.2439 | 1.0211 | 550 | 440 | 440 | 550
OVER21 | TADT2A | 2027 | Addition | 20.176 | 0 | OHL | 0.0988 | 0.8858 | 5.2674 | 1500 | 1500 | 1300 | 1500
OVER21 | TADT2B | 2027 | Addition | 20.176 | 0 | OHL | 0.0988 | 0.8858 | 5.2673 | 1500 | 1500 | 1300 | 1500
PELH41 | RYEH4A | 2027 | Change | 23.015 | 0 | OHL | 0.0202 | 0.3952 | 15.4966 | 3326 | 3326 | 3320 | 3326
PELH41 | RYEH4B | 2027 | Change | 23.439 | 0 | OHL | 0.0206 | 0.4024 | 15.7811 | 3326 | 3326 | 3320 | 3326
PEMB41 | POAB41 | 2027 | Addition | 74.6 | 0 | OHL | 0.081 | 1.2975 | 49.1773 | 2779 | 2568 | 2217 | 2568
PEMB41 | SWAN41 | 2027 | Change | 83.854 | 0 | OHL | 0.091 | 1.4585 | 55.2774 | 2779 | 2568 | 2217 | 2568
PEMB41 | WALH41 | 2027 | Removed | 217.727 | 5.468 | Composite | 0.2372 | 3.8063 | 207.4152 | 2779 | 2568 | 2217 | 2568
PENT41 | WYLF41 | 2027 | Removed | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568
PENT41 | WYLS41 | 2027 | Addition | 27.13 | 0 | OHL | 0.0294 | 0.4719 | 17.8844 | 2779 | 2568 | 2217 | 2568
PITS21 | WIBA21 | 2027 | Change | 0 | 2.324 | Cable | 0.0036 | 0.0621 | 13.8036 | 530 | 530 | 445 | 530
POAB41 | SWAN41 | 2027 | Addition | 9.35 | 0 | OHL | 0.0101 | 0.1626 | 6.1636 | 2779 | 2568 | 2217 | 2568
RYEH41 | RYEH4B | 2027 | Change | 0.137 | 0 | OHL | 0.0001 | 0.0024 | 0.0923 | 3326 | 3326 | 3320 | 3326
RYEH41 | WALX4A | 2027 | Change | 5.324 | 0 | OHL | 0.0047 | 0.0914 | 3.5851 | 3326 | 3326 | 3326 | 3326
RYEH4A | WALX4B | 2027 | Change | 5.461 | 0 | OHL | 0.0048 | 0.0938 | 3.6774 | 3326 | 3326 | 3326 | 3326
SPEN41 | STEW41 | 2027 | Change | 37.795 | 0.126 | Composite | 0.0498 | 0.7386 | 24.4993 | 2780 | 2670 | 2480 | 2670
SPEN42 | STEW41 | 2027 | Change | 37.795 | 0 | OHL | 0.0497 | 0.7368 | 22.4165 | 2780 | 2780 | 2480 | 2670
SWAN41 | WALH41 | 2027 | Addition | 133.752 | 5.468 | Composite | 0.146 | 2.3458 | 152.0578 | 2779 | 2568 | 2217 | 2568
TEMP22 | WIBA21 | 2027 | Change | 0 | 3.607 | Cable | 0.0055 | 0.0964 | 21.424 | 530 | 530 | 530 | 530
TRAW41 | TREU4A | 2027 | Removed | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5731 | 3102 | 3048 | 2958 | 3048
TRAW41 | TREU4B | 2027 | Change | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5726 | 3102 | 3048 | 2958 | 3048
WYLF41 | WYLS41 | 2027 | Addition | 8.11 | 0 | OHL | 0.0088 | 0.1411 | 5.3462 | 2779 | 2568 | 2217 | 2568
BARK41 | WHAM41 | 2029 | Change | 9.662 | 0 | OHL | 0.0151 | 0.191 | 5.623 | 3100 | 3100 | 3100 | 3100
BARK41 | WHAM41 | 2029 | Change | 9.662 | 0.124 | Composite | 0.0151 | 0.1915 | 10.4342 | 3100 | 3100 | 3100 | 3100
BRAI4A | BRFO41 | 2029 | Removed | 48.267 | 0 | OHL | 0.0449 | 0.8314 | 32.3122 | 3326 | 3326 | 3317 | 3326
BRAI4A | BRFO41 | 2029 | Addition | 41 | 8 | Composite | 0.0441 | 0.8075 | 127.9671 | 3326 | 3326 | 3320 | 3326
BRAI4B | BRFO41 | 2029 | Addition | 41 | 8 | Composite | 0.0442 | 0.8076 | 127.9635 | 3326 | 3326 | 3320 | 3326
BRAI4B | PELH41 | 2029 | Removed | 65.942 | 0 | OHL | 0.0648 | 1.1396 | 43.9331 | 2779 | 2568 | 2217 | 2568
BRFO41 | PELH41 | 2029 | Removed | 69.301 | 0 | OHL | 0.0655 | 1.1949 | 46.3271 | 3102 | 2935 | 2765 | 2935
BRFO41 | TWIN4A | 2029 | Addition | 28.419 | 0 | OHL | 0.0252 | 0.4881 | 19.1016 | 3820 | 3630 | 3320 | 3630
BRFO41 | TWIN4B | 2029 | Addition | 28.419 | 0 | OHL | 0.0252 | 0.4881 | 19.1016 | 3820 | 3630 | 3320 | 3630
BRIN21 | CHTE21 | 2029 | Removed | 22.464 | 0.22 | Composite | 0.0519 | 0.8305 | 9.3505 | 934 | 934 | 753 | 753
BRIN22 | CHTE21 | 2029 | Removed | 22.375 | 0 | OHL | 0.0513 | 0.8236 | 6.9689 | 1204 | 1115 | 1018 | 1115
BRIN41 | CHTE41 | 2029 | Addition | 22.375 | 0 | OHL | 0.0243 | 0.3892 | 14.7493 | 2810 | 2700 | 2510 | 2700
BRIN41 | CHTE41 | 2029 | Addition | 22.464 | 0.22 | Composite | 0.0245 | 0.3933 | 17.2091 | 2810 | 2700 | 2510 | 2700
BRLE41 | MELK41 | 2029 | Change | 77.5 | 4.4 | Composite | 0.1014 | 1.4577 | 154.835 | 2830 | 2770 | 2680 | 2770
BRLE41 | MELK41 | 2029 | Change | 77.5 | 4.4 | Composite | 0.1029 | 1.4603 | 101.331 | 2830 | 2770 | 2680 | 2770
CHTE21 | HIGM21 | 2029 | Removed | 43.651 | 0 | OHL | 0.1214 | 1.8002 | 12.2369 | 1381 | 1381 | 1375 | 1381
CHTE21 | HIGM21 | 2029 | Removed | 43.792 | 0 | OHL | 0.1218 | 1.806 | 12.2763 | 1381 | 1339 | 1258 | 1339
COTT41 | HIMB41 | 2029 | Addition | 7.099 | 0.25 | Composite | 0.0113 | 0.1388 | 9.876 | 3100 | 3050 | 2960 | 3050
COTT41 | STAY41 | 2029 | Removed | 27.788 | 0.5 | Composite | 0.0506 | 0.5544 | 21.5604 | 2213 | 2126 | 1980 | 2052
COTT42 | WBUR42 | 2029 | Change | 6.76 | 0 | OHL | 0.0096 | 0.1298 | 4.0616 | 3326 | 3160 | 2971 | 3160
COWL41 | MITY41 | 2029 | Change | 100.105 | 2.092 | Composite | 0.1293 | 1.8315 | 98.6831 | 1180 | 1132 | 877 | 979
COWL41 | WALH41 | 2029 | Change | 89.553 | 2.092 | Composite | 0.1112 | 1.627 | 92.3926 | 1180 | 1132 | 877 | 979
DINO41 | PENI4A | 2029 | Addition | 0 | 7.31 | Cable | 0.0051 | 0.0804 | 146.1 | 1623 | 1623 | 1571 | 1571
DINO41 | PENT41 | 2029 | Removed | 4.545 | 7.31 | Composite | 0.0088 | 0.1776 | 95.0951 | 1623 | 1623 | 1571 | 1571
ELST41 | ELST4A | 2029 | Removed | 0 | 0 | Series Reactor | 0.0125 | 1.1437 | 0 | 2000 | 2000 | 2000 | 2000
ELST41 | ELST4B | 2029 | Addition | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 2000 | 2000 | 2000 | 2000
ELST41 | ELST4B | 2029 | Addition | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 2000 | 2000 | 2000 | 2000
ELST41 | SJOW41 | 2029 | Addition | 0 | 20 | Cable | 0.014 | 0.176 | 244.29 | 1767 | 2640 | 2640 | 2640
ELST41 | SUND41 | 2029 | Change | 34.834 | 0 | OHL | 0.0549 | 0.6691 | 20.9253 | 2400 | 2300 | 2140 | 2300
ELST4A | ELST41 | 2029 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0 | 1590 | 1500 | 1346 | 1500
ELST4B | SUND42 | 2029 | Change | 34.706 | 0 | OHL | 0.0547 | 0.6666 | 20.848 | 3100 | 1732 | 1732 | 1732
FECK41 | MITY41 | 2029 | Change | 65.268 | 7.5 | Composite | 0.0997 | 1.2484 | 222.0437 | 2830 | 2770 | 2680 | 2770
FECK41 | WALH41 | 2029 | Change | 55.11 | 7.5 | Composite | 0.082 | 1.0511 | 215.9994 | 2830 | 2770 | 2680 | 2770
FOUX41 | PENI4A | 2029 | Addition | 23.025 | 0 | OHL | 0.0303 | 0.4488 | 13.6563 | 2780 | 2700 | 2510 | 2700
FOUX41 | TRAW41 | 2029 | Addition | 14.128 | 9.54 | Composite | 0.0248 | 0.3917 | 231.479 | 1830 | 1830 | 1830 | 1830
GRAI41 | TILB41 | 2029 | Change | 26.642 | 2.049 | Composite | 0.0267 | 0.4794 | 61.4717 | 2950 | 2950 | 2950 | 2950
GRAI41 | WALE41 | 2029 | Change | 1.68 | 0 | OHL | 0.0015 | 0.0288 | 1.1313 | 3326 | 3160 | 2633 | 2813
GREN41 | MARV4A | 2029 | Change | 26 | 0 | OHL | 0.0406 | 0.5007 | 15.5357 | 3100 | 3050 | 2960 | 3050
GREN41 | MARV4B | 2029 | Change | 26 | 0 | OHL | 0.0406 | 0.5007 | 15.5357 | 3100 | 3050 | 2960 | 3050
HAKB4- | HARG41 | 2029 | Change | 10.107 | 0 | OHL | 0.0175 | 0.1997 | 5.8779 | 3180 | 3130 | 3050 | 3130
HAKB4B | HARG41 | 2029 | Change | 10.107 | 0 | OHL | 0.0175 | 0.1997 | 5.8779 | 3180 | 3130 | 3050 | 3130
HAWP21 | NORT21 | 2029 | Removed | 30.238 | 0.459 | Composite | 0.0719 | 1.1367 | 14.2369 | 908 | 874 | 720 | 801
HAWP4A | NORT41 | 2029 | Change | 30.157 | 0 | OHL | 0.047 | 0.5786 | 18.0971 | 3100 | 3050 | 2960 | 3050
HAWP41 | NORT41 | 2029 | Addition | 30.157 | 0 | OHL | 0.047 | 0.5786 | 18.0971 | 3100 | 3050 | 2960 | 3050
HIGM21 | THUR2A | 2029 | Removed | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 626 | 591 | 535 | 591
HIGM4A | STOB41 | 2029 | Removed | 39.671 | 0 | OHL | 0.0722 | 0.7893 | 22.9886 | 2147 | 2056 | 1904 | 2056
HIGM41 | WBUR41 | 2029 | Removed | 14.852 | 0.229 | Composite | 0.0254 | 0.2958 | 13.2571 | 2212 | 2125 | 1979 | 2125
HIMB21 | THUR2A | 2029 | Addition | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 626 | 591 | 535 | 591
HIMB41 | STAY41 | 2029 | Addition | 20.939 | 0 | OHL | 0.0329 | 0.4037 | 12.4972 | 3100 | 3050 | 2960 | 3050
HIMB41 | STOB41 | 2029 | Addition | 39.671 | 0 | OHL | 0.0642 | 0.7694 | 23.5463 | 3100 | 3050 | 2960 | 3050
HIMB41 | WBUR41 | 2029 | Addition | 14.852 | 0.229 | Composite | 0.0224 | 0.2868 | 17.1381 | 3100 | 3050 | 2960 | 3050
KINO41 | TILB41 | 2029 | Change | 15.478 | 1.835 | Composite | 0.0149 | 0.2859 | 47.1231 | 2950 | 2950 | 2950 | 2950
MARV4A | SUND41 | 2029 | Change | 13.75 | 0 | OHL | 0.0215 | 0.2648 | 8.216 | 3100 | 3050 | 2960 | 3050
MARV4B | SUND42 | 2029 | Change | 13.955 | 1 | Composite | 0.0218 | 0.2688 | 8.3345 | 3100 | 3050 | 2960 | 3050
NORT41 | OBST4A | 2029 | Change | 70.35 | 0 | OHL | 0.0624 | 1.2083 | 47.2853 | 3326 | 3326 | 3320 | 3326
NORT41 | OBST4B | 2029 | Change | 70.35 | 0 | OHL | 0.0624 | 1.2083 | 47.2853 | 3326 | 3326 | 3320 | 3326
OBST4A | OSBA41 | 2029 | Change | 13.35 | 0 | OHL | 0.0118 | 0.2293 | 8.9731 | 3326 | 3326 | 3320 | 3326
OBST4B | OSBA42 | 2029 | Change | 13.35 | 0 | OHL | 0.0118 | 0.2293 | 8.9731 | 3326 | 3326 | 3320 | 3326
PELH41 | SUND42 | 2029 | Removed | 45.13 | 0 | OHL | 0.0487 | 0.752 | 31.2185 | 3180 | 3000 | 2692 | 3000
PELH41 | TWIN4A | 2029 | Addition | 40.882 | 0 | OHL | 0.0362 | 0.7022 | 27.4783 | 3100 | 3100 | 3100 | 3100
PELH41 | TWIN4B | 2029 | Addition | 40.823 | 0 | OHL | 0.0362 | 0.7012 | 27.4387 | 3820 | 3630 | 3320 | 3630
PELH41 | WYMO41 | 2029 | Change | 26.856 | 0 | OHL | 0.0291 | 0.4667 | 17.7225 | 2771 | 2771 | 2692 | 2771
PELH41 | WYMO41 | 2029 | Addition | 26.891 | 0 | OHL | 0.0292 | 0.4677 | 17.7269 | 3180 | 3180 | 3180 | 3180
PEMB41 | POAB41 | 2029 | Addition | 74.6 | 0 | OHL | 0.081 | 1.2975 | 49.1773 | 2779 | 2568 | 2217 | 2568
PEMB41 | SWAN41 | 2029 | Removed | 83.854 | 0 | OHL | 0.091 | 1.4585 | 55.2774 | 2779 | 2568 | 2217 | 2568
PENI4A | PENT41 | 2029 | Addition | 4.545 | 0 | OHL | 0.0049 | 0.0722 | 3.2978 | 2780 | 2570 | 2220 | 2570
PENT41 | TRAW41 | 2029 | Change | 41.698 | 9.71 | Composite | 0.0611 | 0.9304 | 251.71 | 1830 | 1830 | 1830 | 1830
POAB41 | SWAN41 | 2029 | Addition | 9.454 | 0 | OHL | 0.0103 | 0.1644 | 6.232 | 2779 | 2779 | 2779 | 2779
RATS41 | STAY4A | 2029 | Change | 43.614 | 0 | OHL | 0.0738 | 0.8539 | 25.6652 | 2147 | 2057 | 1905 | 2057
RATS41 | STOB41 | 2029 | Change | 26.72 | 0.179 | Composite | 0.0451 | 0.5238 | 21.6497 | 3100 | 3050 | 2960 | 3050
SUND41 | WYMO41 | 2029 | Change | 18.156 | 0 | OHL | 0.0197 | 0.3152 | 11.9934 | 3180 | 3180 | 3180 | 3180
SUND42 | WYMO41 | 2029 | Addition | 17.986 | 0 | OHL | 0.0195 | 0.3128 | 11.8566 | 3180 | 3180 | 3180 | 3180
BICF41 | SPLN41 | 2033 | Removed | 20.109 | 0 | OHL | 0.0191 | 0.355 | 13.187 | 3156 | 3032 | 2823 | 3032
BICF41 | WALP41 | 2033 | Removed | 37.775 | 0 | OHL | 0.0335 | 0.6488 | 25.3895 | 3189 | 3063 | 2853 | 3063
BICF41 | WEMA41 | 2033 | Addition | 14.35 | 0 | OHL | 0.0127 | 0.2465 | 9.6453 | 3156 | 3032 | 2823 | 3032
BICF41 | WEMA41 | 2033 | Addition | 14.35 | 0 | OHL | 0.0127 | 0.2465 | 9.6453 | 3189 | 3063 | 2853 | 3063
BISW21 | FECK21 | 2033 | Change | 22.83 | 0 | OHL | 0.09 | 0.9539 | 6.2893 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 2033 | Change | 24.226 | 0 | OHL | 0.0923 | 1.0003 | 6.768 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 2033 | Change | 27.111 | 0 | OHL | 0.1043 | 1.1209 | 7.5619 | 955 | 882 | 762 | 882
BISW21 | PENN21 | 2033 | Change | 30.172 | 0 | OHL | 0.1181 | 1.2598 | 8.3183 | 1040 | 1031 | 762 | 762
BRFO41 | EACS41 | 2033 | Addition | 8.9 | 16 | Composite | 0.0162 | 0.3836 | 207.0551 | 3820 | 3820 | 3820 | 3820
BRFO41 | NORM42 | 2033 | Addition | 66.8 | 1.9 | Composite | 0.0596 | 1.1743 | 68.8588 | 3326 | 3326 | 3320 | 3326
BRFO42 | EACS41 | 2033 | Addition | 8.9 | 15.5 | Composite | 0.016 | 0.3764 | 200.772 | 3820 | 3820 | 3820 | 3820
BRFO42 | NORM41 | 2033 | Addition | 66.8 | 1.9 | Composite | 0.0596 | 1.1743 | 68.8588 | 3326 | 3326 | 3320 | 3326
CANT41 | RICB41 | 2033 | Addition | 23.725 | 0 | OHL | 0.0379 | 0.4562 | 14.2669 | 2038 | 2038 | 1801 | 1801
CANT41 | RICB41 | 2033 | Addition | 23.725 | 0 | OHL | 0.0379 | 0.4562 | 14.2669 | 2038 | 2038 | 1801 | 1801
CANT41 | RICH41 | 2033 | Removed | 25 | 0 | OHL | 0.0399 | 0.4808 | 15.0336 | 2038 | 2038 | 1801 | 1801
CANT41 | RICH41 | 2033 | Removed | 25 | 0 | OHL | 0.0399 | 0.4808 | 15.0336 | 2038 | 2038 | 1801 | 1801
CARR41 | KEAR41 | 2033 | Change | 13.154 | 0 | OHL | 0.0207 | 0.265 | 7.5449 | 2212 | 2125 | 1979 | 2125
CARR41 | PEWO4A | 2033 | Change | 56.9 | 0 | OHL | 0.0837 | 1.1325 | 33.0539 | 2810 | 2810 | 2810 | 2810
CHTE41 | HIMB41 | 2033 | Addition | 43.651 | 0 | OHL | 0.0574 | 0.8509 | 25.8889 | 2810 | 2700 | 2510 | 2700
CHTE41 | HIMB42 | 2033 | Addition | 43.792 | 0 | OHL | 0.0576 | 0.8537 | 25.9723 | 2810 | 2700 | 2510 | 2700
CHUE4A | TILB41 | 2033 | Removed | 13.045 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2827 | 2827 | 2591 | 2591
CHUE4A | TILN41 | 2033 | Addition | 9.295 | 0 | OHL | 0.0145 | 0.179 | 5.554 | 2827 | 2827 | 2591 | 2591
CHUE4B | TILB41 | 2033 | Removed | 13.045 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2924 | 2924 | 2591 | 2591
CHUE4B | TILN41 | 2033 | Addition | 9.295 | 0 | OHL | 0.0145 | 0.179 | 5.554 | 2924 | 2924 | 2591 | 2591
COTT41 | MARH4B | 2033 | Change | 100.853 | 0 | OHL | 0.1672 | 1.9673 | 59.6151 | 2210 | 2210 | 2210 | 2210
COTT42 | STAY41 | 2033 | Change | 27.698 | 0 | OHL | 0.0437 | 0.5355 | 16.5245 | 2212 | 2125 | 1979 | 2125
CRBB41 | HIMB41 | 2033 | Addition | 73 | 9 | Composite | 0.1199 | 1.5123 | 141.9148 | 3326 | 3326 | 3320 | 3326
CRBB41 | HIMB41 | 2033 | Addition | 73 | 9 | Composite | 0.1199 | 1.5123 | 141.9148 | 3326 | 3326 | 3320 | 3326
EACS41 | TILN41 | 2033 | Addition | 81.3 | 4.7 | Composite | 0.0738 | 1.4637 | 113.8088 | 3820 | 3820 | 3820 | 3820
EACS41 | TILN41 | 2033 | Addition | 81.3 | 4.7 | Composite | 0.0738 | 1.4637 | 113.8088 | 3820 | 3820 | 3820 | 3820
ECLA41 | PAFB4A | 2033 | Change | 44.72 | 0 | OHL | 0.0697 | 0.858 | 26.8364 | 3100 | 1732 | 1732 | 1732
ECLA41 | PAFB4B | 2033 | Change | 44.886 | 0 | OHL | 0.07 | 0.8613 | 26.9323 | 3100 | 1524 | 1524 | 1524
EGGB41 | THOM41 | 2033 | Change | 28.07 | 0.197 | Composite | 0.0324 | 0.5191 | 20.9345 | 2217 | 2217 | 1801 | 1801
EGGB42 | STSB4B | 2033 | Change | 48.084 | 0 | OHL | 0.0537 | 0.8525 | 31.1991 | 2779 | 2568 | 2217 | 2568
ENDE41 | PAFB4A | 2033 | Change | 41.13 | 0 | OHL | 0.0616 | 0.7797 | 24.9939 | 3100 | 1732 | 1732 | 1732
ENDE41 | PAFB4B | 2033 | Change | 41.13 | 0 | OHL | 0.0616 | 0.7797 | 24.9939 | 3100 | 1732 | 1732 | 1732
EXET41 | TAUN41 | 2033 | Change | 38.147 | 0 | OHL | 0.0596 | 0.7346 | 22.7934 | 3100 | 3100 | 3100 | 3100
EXET41 | TAUN42 | 2033 | Change | 38.107 | 0 | OHL | 0.0595 | 0.7338 | 22.7696 | 3100 | 3100 | 3100 | 3100
FECK41 | IRON41 | 2033 | Change | 66.123 | 0 | OHL | 0.1175 | 1.3011 | 38.7257 | 3100 | 1524 | 1524 | 1524
FOUX41 | TRAW41 | 2033 | Change | 14.128 | 9.54 | Composite | 0.0217 | 0.3336 | 454.579 | 2473 | 2473 | 2473 | 2473
GREN41 | MARH4A | 2033 | Change | 28.74 | 0 | OHL | 0.0485 | 0.5625 | 16.9294 | 3100 | 3050 | 2960 | 3050
GREN41 | MARH4B | 2033 | Change | 28.56 | 0 | OHL | 0.0482 | 0.5591 | 16.8217 | 3100 | 3050 | 2960 | 3050
GRIW41 | LCNA41 | 2033 | Addition | 36 | 4 | Composite | 0.0329 | 0.6473 | 114.519 | 3326 | 3326 | 3320 | 3326
GRIW41 | LCNA41 | 2033 | Addition | 36 | 4 | Composite | 0.0326 | 0.64 | 159.6574 | 3326 | 3326 | 3320 | 3326
HINP41 | SHUR41 | 2033 | Change | 1.213 | 0 | OHL | 0.0019 | 0.0238 | 0.7104 | 3100 | 3050 | 2960 | 3050
HINP41 | SHUR41 | 2033 | Change | 1.2 | 0 | OHL | 0.0019 | 0.0235 | 0.7026 | 3100 | 3050 | 2960 | 3050
KEAR41 | PADI41 | 2033 | Change | 39.101 | 0 | OHL | 0.0553 | 0.7599 | 23.2874 | 2169 | 2084 | 1940 | 2084
KIBY21 | WASF2A | 2033 | Removed | 10.945 | 0 | OHL | 0.0414 | 0.4478 | 3.0891 | 1521 | 1461 | 1360 | 1461
KIBY21 | WASF2B | 2033 | Removed | 10.978 | 0 | OHL | 0.0415 | 0.4491 | 3.0984 | 1521 | 1461 | 1360 | 1461
KIBY41 | WASF41 | 2033 | Addition | 10.945 | 0 | OHL | 0.0141 | 0.2055 | 6.7539 | 1524 | 1524 | 1524 | 1524
KIBY41 | WASF41 | 2033 | Addition | 10.978 | 0 | OHL | 0.0142 | 0.2061 | 6.7742 | 1524 | 1524 | 1524 | 1524
LACK41 | SALH41 | 2033 | Change | 10.237 | 0.25 | Composite | 0.0183 | 0.2029 | 9.1816 | 3100 | 3100 | 3100 | 3100
LACK41 | THTO41 | 2033 | Change | 92.075 | 5.7 | Composite | 0.1451 | 1.8806 | 257.6996 | 3100 | 3050 | 2960 | 3050
LACK41 | THTO42 | 2033 | Change | 92.075 | 5.7 | Composite | 0.1451 | 1.8806 | 257.6996 | 3100 | 3050 | 2960 | 3050
LCNA41 | LCNB41 | 2033 | Addition | 3 | 0 | OHL | 0.0026 | 0.0515 | 2.0202 | 3326 | 3326 | 3320 | 3326
LCNA41 | LCNB41 | 2033 | Addition | 3 | 0 | OHL | 0.0026 | 0.0515 | 2.0202 | 3326 | 3326 | 3326 | 3326
LCNB41 | WEMA41 | 2033 | Addition | 63 | 7 | Composite | 0.0576 | 1.1328 | 200.4082 | 3326 | 3326 | 3320 | 3326
LCNB41 | WEMA41 | 2033 | Addition | 63 | 7 | Composite | 0.0576 | 1.1328 | 200.4082 | 3326 | 3326 | 3320 | 3326
MARH4A | STAY41 | 2033 | Change | 73.027 | 0 | OHL | 0.1233 | 1.4294 | 43.014 | 2514 | 2439 | 2314 | 2439
NORT21 | SALH21 | 2033 | Change | 12.178 | 0 | OHL | 0.0431 | 0.5178 | 3.2966 | 1381 | 1293 | 1197 | 1293
NORT41 | SALH42 | 2033 | Change | 12.206 | 0 | OHL | 0.0204 | 0.2452 | 6.9936 | 3100 | 3050 | 2960 | 3050
PADI41 | PEWO4B | 2033 | Change | 37.608 | 0 | OHL | 0.0475 | 0.7159 | 22.8474 | 2810 | 2810 | 2810 | 2810
PENT41 | TRAW41 | 2033 | Change | 41.698 | 9.71 | Composite | 0.058 | 0.8712 | 478.666 | 2473 | 2473 | 2473 | 2473
PEWO2C | WASF2A | 2033 | Removed | 23.481 | 0 | OHL | 0.0887 | 0.9606 | 6.6274 | 1521 | 1461 | 1360 | 1461
PEWO2D | WASF2B | 2033 | Removed | 23.521 | 0 | OHL | 0.0889 | 0.9623 | 6.6386 | 1521 | 1461 | 1360 | 1461
PEWO41 | WASF41 | 2033 | Addition | 23.481 | 0 | OHL | 0.0303 | 0.4409 | 14.4899 | 1524 | 1524 | 1524 | 1524
PEWO41 | WASF41 | 2033 | Addition | 23.521 | 0 | OHL | 0.0303 | 0.4416 | 14.5145 | 1524 | 1524 | 1524 | 1524
RICB41 | RICH41 | 2033 | Addition | 2.525 | 0 | OHL | 0.004 | 0.0486 | 1.5184 | 2038 | 2038 | 1801 | 1801
RICB41 | RICH41 | 2033 | Addition | 2.525 | 0 | OHL | 0.004 | 0.0486 | 1.5184 | 2038 | 2038 | 1801 | 1801
SELL4A | SELL4C | 2033 | Change | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 3100 | 3100 | 3100 | 3100
SELL4A | SELL4D | 2033 | Change | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 3100 | 3100 | 3100 | 3100
SELL4A | SELL4E | 2033 | Change | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 3100 | 3100 | 3100 | 3100
SELL4A | SELL4F | 2033 | Change | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 3100 | 3100 | 3100 | 3100
SHUR41 | TAUN41 | 2033 | Change | 27 | 0 | OHL | 0.0422 | 0.5208 | 16.1042 | 3100 | 3050 | 2960 | 3050
SHUR41 | TAUN42 | 2033 | Change | 27 | 0 | OHL | 0.0422 | 0.5208 | 16.1042 | 3100 | 3050 | 2960 | 3050
SPLN41 | WALP41 | 2033 | Removed | 29.234 | 0 | OHL | 0.0272 | 0.5117 | 19.3195 | 3189 | 3063 | 2853 | 3063
SPLN41 | WEMA41 | 2033 | Addition | 5.759 | 0 | OHL | 0.0064 | 0.1085 | 3.5417 | 3156 | 3032 | 2823 | 3032
SPLN41 | WEMA41 | 2033 | Addition | 5.759 | 0 | OHL | 0.0064 | 0.1085 | 3.5417 | 3189 | 3063 | 2853 | 3063
STAL4A | THOM41 | 2033 | Change | 69.271 | 6.952 | Composite | 0.0807 | 1.2858 | 150.8388 | 1442 | 1442 | 1314 | 1314
TILB41 | TILB42 | 2033 | Addition | 0 | 0 | Series Compensation | 0 | 1.25 | 0 | 3102 | 3048 | 2853 | 3048
TILB41 | TILB43 | 2033 | Addition | 0 | 0 | Series Compensation | 0 | 1.25 | 0 | 3102 | 3048 | 2958 | 3048
TILB41 | TILN41 | 2033 | Addition | 3.75 | 0.48 | Composite | 0.0062 | 0.0779 | 7.4801 | 2827 | 2827 | 2591 | 2591
TILB41 | TILN41 | 2033 | Addition | 3.75 | 0.48 | Composite | 0.0062 | 0.0779 | 7.4801 | 2924 | 2924 | 2591 | 2591
WALP41 | WALP42 | 2033 | Addition | 0.25 | 0 | OHL | 0.0002 | 0.0043 | 0.1683 | 3326 | 3326 | 3326 | 3326
WALP41 | WALP42 | 2033 | Addition | 0.25 | 0 | OHL | 0.0002 | 0.0043 | 0.1683 | 3326 | 3326 | 3326 | 3326
WALP41 | WEMA41 | 2033 | Addition | 23.475 | 0 | OHL | 0.0208 | 0.4032 | 15.7777 | 3189 | 3063 | 2853 | 3063
WALP41 | WEMA41 | 2033 | Addition | 23.425 | 0 | OHL | 0.0208 | 0.4023 | 15.7443 | 3189 | 3063 | 2853 | 3063
BRIN41 | THOM41 | 2035 | Change | 36.299 | 0 | OHL | 0.0319 | 0.6232 | 24.4435 | 3326 | 2660 | 2660 | 2660
BRIN41 | THOM41 | 2035 | Change | 36.299 | 0 | OHL | 0.0319 | 0.6232 | 24.4435 | 2660 | 2660 | 2660 | 2660
CARL41 | FOUR4A | 2035 | Addition | 48.004 | 0 | OHL | 0.0421 | 0.8242 | 32.3253 | 3370 | 2979 | 2979 | 2979
CARL41 | FOUR4B | 2035 | Addition | 48.004 | 0 | OHL | 0.0421 | 0.8242 | 32.3253 | 3370 | 2979 | 2979 | 2979
CARL41 | HARG41 | 2035 | Addition | 10 | 0.1 | Composite | 0.0156 | 0.2005 | 7.4303 | 2780 | 2670 | 2480 | 2670
CARL41 | HARG41 | 2035 | Addition | 10 | 0 | OHL | 0.0155 | 0.199 | 5.7773 | 2780 | 2780 | 2480 | 2670
CARL41 | QUER41 | 2035 | Addition | 105 | 12.5 | Composite | 0.0964 | 1.7967 | 374.8254 | 3100 | 2771 | 2771 | 2771
CARL41 | QUER41 | 2035 | Addition | 105 | 12.5 | Composite | 0.0964 | 1.7967 | 374.8254 | 3100 | 2771 | 2771 | 2771
CARL41 | TEVB4Q | 2035 | Addition | 16 | 4 | Composite | 0.0261 | 0.3428 | 196.2312 | 3100 | 3100 | 3100 | 3100
CARL41 | TEVB4R | 2035 | Addition | 16 | 4 | Composite | 0.0261 | 0.3428 | 196.2312 | 3100 | 3100 | 3100 | 3100
CHTE41 | RATS41 | 2035 | Addition | 40 | 5 | Composite | 0.0657 | 0.8265 | 78.5806 | 3100 | 3100 | 3100 | 3100
CHTE41 | RATS41 | 2035 | Addition | 40 | 5 | Composite | 0.0657 | 0.8265 | 78.5806 | 3100 | 3100 | 3100 | 3100
COTT41 | NERY41 | 2035 | Addition | 76.548 | 0 | OHL | 0.0831 | 1.3314 | 50.4611 | 2779 | 2569 | 2217 | 2569
COTT41 | RYHA4A | 2035 | Removed | 76.891 | 0 | OHL | 0.0682 | 1.3211 | 51.7563 | 3326 | 2790 | 3320 | 3320
COTT42 | NERY41 | 2035 | Addition | 76.473 | 0 | OHL | 0.083 | 1.3301 | 50.4119 | 2807 | 2696 | 2511 | 2696
COTT42 | RYHA4B | 2035 | Removed | 76.816 | 0 | OHL | 0.0681 | 1.3196 | 51.7119 | 2807 | 2696 | 2511 | 2696
DRAX41 | FENW4A | 2035 | Change | 13.443 | 0 | OHL | 0.0132 | 0.2323 | 8.9571 | 3326 | 3326 | 3320 | 3326
DRAX42 | THOM41 | 2035 | Change | 21.73 | 0 | OHL | 0.0297 | 0.3977 | 13.7397 | 2981 | 2867 | 2248 | 2505
EACS41 | EACS41 | 2035 | Addition | 0 | 0 | Zero Length | 0 | 0 | 0 | 2494 | 2494 | 2494 | 2494
EACS41 | EACS41 | 2035 | Addition | 0 | 0 | Zero Length | 0 | 0 | 0 | 2494 | 2494 | 2494 | 2494
EGGB41 | THOM41 | 2035 | Addition | 27.473 | 0 | OHL | 0.0305 | 0.5025 | 17.4336 | 2800 | 2800 | 2800 | 2800
EGGB41 | THOM41 | 2035 | Change | 28.07 | 0.197 | Composite | 0.0298 | 0.5047 | 21.4293 | 2217 | 2217 | 1801 | 1801
EGGB42 | STAL41 | 2035 | Addition | 71.798 | 6.952 | Composite | 0.0866 | 1.3455 | 151.9687 | 1442 | 1442 | 1314 | 1314
FIDF21 | FIDF21 | 2035 | Removed | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750
FIDF21 | FIDF21 | 2035 | Removed | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750
FIDF21 | FROD21 | 2035 | Removed | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213
FIDF21 | FROD22 | 2035 | Removed | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213
FIDF21 | RAIN21 | 2035 | Removed | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213
FIDF21 | RAIN21 | 2035 | Removed | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213
FIDF41 | FROD41 | 2035 | Addition | 9.145 | 0 | OHL | 0.0118 | 0.1717 | 5.6435 | 3490 | 3490 | 3490 | 3490
FIDF41 | FROD41 | 2035 | Addition | 9.145 | 0 | OHL | 0.0118 | 0.1717 | 5.6435 | 3490 | 3490 | 3490 | 3490
FIDF41 | RAIN41 | 2035 | Addition | 7.963 | 0 | OHL | 0.0103 | 0.1495 | 4.9141 | 3490 | 3490 | 3490 | 3490
FIDF41 | RAIN41 | 2035 | Addition | 7.963 | 0 | OHL | 0.0103 | 0.1495 | 4.9141 | 3490 | 3490 | 3490 | 3490
FOUR21 | HARK24 | 2035 | Removed | 55.711 | 0 | OHL | 0.3289 | 2.3608 | 15.2112 | 854 | 795 | 700 | 795
FOUR21 | STEW21 | 2035 | Removed | 27.731 | 0 | OHL | 0.1637 | 1.1751 | 7.5717 | 854 | 795 | 700 | 795
FOUR41 | FOUR4A | 2035 | Addition | 0.2 | 0 | OHL | 0.0002 | 0.0034 | 0.1347 | 3370 | 2979 | 2979 | 2979
FOUR41 | FOUR4B | 2035 | Addition | 0.2 | 0 | OHL | 0.0002 | 0.0034 | 0.1347 | 3370 | 2979 | 2979 | 2979
FOUR4A | STEW41 | 2035 | Addition | 27 | 0 | OHL | 0.0237 | 0.4636 | 18.1816 | 3370 | 2979 | 2979 | 2979
FOUR4B | STEW41 | 2035 | Addition | 27 | 0 | OHL | 0.0237 | 0.4636 | 18.1816 | 3370 | 2979 | 2979 | 2979
HARK23 | STEW21 | 2035 | Removed | 83.682 | 0.117 | Composite | 0.4944 | 3.549 | 23.7211 | 774 | 774 | 676 | 676
HEYS41 | QUER41 | 2035 | Addition | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3326 | 3299 | 3098 | 3299
HEYS41 | QUER4B | 2035 | Removed | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3326 | 3299 | 3098 | 3299
HUTT41 | QUER41 | 2035 | Addition | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048
HUTT41 | QUER41 | 2035 | Addition | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048
HUTT41 | QUER4A | 2035 | Removed | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048
HUTT41 | QUER4B | 2035 | Removed | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048
KIBY21 | RAIN21 | 2035 | Removed | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339
KIBY21 | RAIN21 | 2035 | Removed | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339
KIBY41 | RAIN41 | 2035 | Addition | 11.236 | 0 | OHL | 0.0145 | 0.211 | 6.9339 | 3490 | 3490 | 3490 | 3490
KIBY41 | RAIN41 | 2035 | Addition | 11.236 | 0 | OHL | 0.0145 | 0.211 | 6.9339 | 3490 | 3490 | 3490 | 3490
KIBY41 | WASF41 | 2035 | Change | 10.945 | 0 | OHL | 0.0141 | 0.2055 | 6.7539 | 3490 | 3490 | 3490 | 3490
KIBY41 | WASF41 | 2035 | Change | 10.978 | 0 | OHL | 0.0142 | 0.2061 | 6.7742 | 3490 | 3490 | 3490 | 3490
MARH41 | NERY41 | 2035 | Addition | 36 | 4 | Composite | 0.0477 | 0.7065 | 202.236 | 2780 | 2780 | 2780 | 2780
MARH41 | NERY41 | 2035 | Addition | 36 | 4 | Composite | 0.0477 | 0.7065 | 202.236 | 2780 | 2780 | 2780 | 2780
MIDL41 | QUER41 | 2035 | Addition | 9.704 | 0 | OHL | 0.0086 | 0.1667 | 6.5225 | 3326 | 3159 | 2971 | 3159
MIDL41 | QUER4A | 2035 | Removed | 9.704 | 0 | OHL | 0.0086 | 0.1667 | 6.5225 | 3326 | 3159 | 2971 | 3159
NERY41 | RYHA41 | 2035 | Addition | 0.343 | 0 | OHL | 0.0004 | 0.006 | 0.2261 | 2779 | 2569 | 2217 | 2569
NERY41 | RYHA42 | 2035 | Addition | 0.343 | 0 | OHL | 0.0004 | 0.006 | 0.2261 | 2807 | 2696 | 2511 | 2696
NERY41 | WEMA41 | 2035 | Addition | 36 | 4 | Composite | 0.0477 | 0.7065 | 202.236 | 2780 | 2780 | 2780 | 2780
NERY41 | WEMA41 | 2035 | Addition | 36 | 4 | Composite | 0.0477 | 0.7065 | 202.236 | 2780 | 2780 | 2780 | 2780
PEWO41 | QUER41 | 2035 | Addition | 31.939 | 0 | OHL | 0.0498 | 0.6128 | 19.1665 | 3102 | 3048 | 2853 | 3048
PEWO41 | QUER41 | 2035 | Addition | 32.087 | 0 | OHL | 0.05 | 0.6156 | 19.2551 | 3102 | 3048 | 2853 | 3048
PEWO41 | QUER4A | 2035 | Removed | 31.939 | 0 | OHL | 0.0498 | 0.6128 | 19.1665 | 3102 | 3048 | 2853 | 3048
PEWO41 | QUER4B | 2035 | Removed | 32.087 | 0 | OHL | 0.05 | 0.6156 | 19.2551 | 3102 | 3048 | 2853 | 3048
PEWO41 | WASF41 | 2035 | Change | 23.481 | 0 | OHL | 0.0303 | 0.4409 | 14.4899 | 3490 | 3490 | 3490 | 3490
PEWO41 | WASF41 | 2035 | Change | 23.521 | 0 | OHL | 0.0303 | 0.4416 | 14.5145 | 3490 | 3490 | 3490 | 3490
STAL41 | THOM41 | 2035 | Removed | 69.271 | 6.952 | Composite | 0.0807 | 1.2858 | 150.8388 | 1442 | 1442 | 1314 | 1314
THUR21 | THUR2A | 2035 | Change | 4.653 | 0 | OHL | 0.0488 | 0.1944 | 1.2745 | 675 | 675 | 675 | 675

## B-2-2d
B.2.2d - OFTO Circuit Changes 2025/26 to 2035/36
Wind Farm | Node 1 | Node 2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Interconnection Type | Rated DC Voltage (kV) | Rated AC Voltage (kV) | Rating (MVA)
Dogger Bank C East Offshore Wind Farm | DBCODC | DBCWDC | 2025 | Addition | 0 | 272 | Cable | TBC | TBC | TBC | HVDC | ±320 | N/A | 1200
| DBCO41 | LACK41 | 2025 | Addition | 0 | 2 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
Inch Cape Offshore Wind Farm | COCK21 | INCO21 | 2025 | Addition | 0 | 0.8 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| COCK21 | INCO22 | 2025 | Addition | 0 | 0.8 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| INCO2A | INCW21 | 2025 | Addition | 0 | 85.5 | Cable | 0.0044 | 0.01 | 297.7 | AC | N/A | 220 | 550
| INCO2A | INCW22 | 2025 | Addition | 0 | 85.5 | Cable | 0.0044 | 0.01 | 297.7 | AC | N/A | 220 | 550
Sofia Offshore Wind Farm | SOFW4A | SOFWD | 2025 | Addition | 0 | 227 | Cable | 0.2757 | 0 | 0 | HVDC | ±320 | N/A | 660
| SOFW4A | SOFWD | 2025 | Addition | 0 | 227 | Cable | 0.2757 | 0 | 0 | HVDC | ±320 | N/A | 660
Vanguard West Offshore Wind Farm | VGWO41 | BASWX1 | 2025 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | ±365 | N/A | 1320
| NECT41 | VGWO41 | 2025 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
East Anglia 3A Offshore Wind Farm | BRFO41 | EACO41 | 2027 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
Hornsea 4A-1 Offshore Wind Farm | CREB41 | HOWD41 | 2027 | Addition | 0 | 0.5 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| CREB42 | HOWD41 | 2027 | Addition | 0 | 0.5 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| HOWD21 | HOWR2C | 2027 | Addition | 0 | 95 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWD21 | HOWR2C | 2027 | Addition | 0 | 95 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWD21 | HOWR2C | 2027 | Addition | 0 | 95 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWR2C | HOWW2F | 2027 | Addition | 0 | 24 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWR2C | HOWW2F | 2027 | Addition | 0 | 24 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWR2C | HOWW2F | 2027 | Addition | 0 | 24 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Hornsea 3A-1 Offshore Wind Farm | NORM41 | HOWC41 | 2027 | Addition | 0 | 1.8 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| HOWC4X | HOWW4X | 2027 | Addition | 0 | 220 | Cable | TBC | TBC | TBC | HVDC | ±320 | N/A | 1320
Pentland Floating Offshore Windfarm | PEHE11 | Onshore 132 kV HV | 2027 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 132 | TBC
| Onshore 66 kV HV | Offshore 66 kV HV | 2027 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 66 | TBC
Seagreen 1A offshore windfarm | COCK21 | Onshore 275kV-1 | 2027 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2027 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Berwick 1 Offshore Wind Farm | BRNX4- | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BRNX4- | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BRNX4- | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2029 | Addition | 0 | 77.4 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-1 | Offshore 275kV-2 | 2029 | Addition | 0 | 77.4 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-1 | Offshore 275kV-3 | 2029 | Addition | 0 | 77.4 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Offshore 66kV-1 | Offshore 66kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 66 | TBC
| Offshore 66kV-2 | Offshore 66kV-3 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 66 | TBC
Berwick 2 Offshore Wind Farm | BRNX4- | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BRNX4- | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BRNX4- | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2029 | Addition | 0 | 72.3 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-1 | Offshore 275kV-2 | 2029 | Addition | 0 | 72.3 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-1 | Offshore 275kV-3 | 2029 | Addition | 0 | 72.3 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Offshore 66kV-1 | Offshore 66kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 66 | TBC
| Offshore 66kV-2 | Offshore 66kV-3 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 66 | TBC
Berwick Bank Offshore Wind Farm C | BLYT41 | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter station 400kV | Offshore Converter station | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | ±525 | N/A | 1800
Cenos Central Offshore Wind Farm | LACK41 | Onshore Converter HV | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter LV | Onshore DC Platform | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | ±300 | N/A | TBC
| Onshore AC Platform | Offshore AC Platform | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 300 | TBC
East Anglia 2A Offshore Wind Farm | BRFO41 | EABO41 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2029 | Addition | 0 | 95 | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
East Anglia 3B Offshore Wind Farm | Onshore Converter station 400kV | Offshore DC Platform | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | ±320 | N/A | 1320
East Anglia 1 North Offshore Wind Farm | FRIS41 | EANO41 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| EANO21 | EANW21 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| EANO21 | EANW21 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Elizabeth Yellow One Offshore Windfarm | PEWO41 | Onshore 400kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-3 | Offshore 275kV-3 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
EQUINOR NEW ENERGY LIMITED | NORM41 | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| NORM42 | Onshore 400kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Erebus Offshore Windfarm | PEMB11 | EOWF11 | 2029 | Addition | 0 | 2 | Cable | TBC | TBC | TBC | AC | N/A | 132 | TBC
| EOWF11 | EOWL11 | 2029 | Addition | 0 | 0 | Cable | TBC | TBC | TBC | AC | N/A | 132 | TBC
| EOWF61 | EOWF62 | 2029 | Addition | 0 | 50 | Cable | TBC | TBC | TBC | AC | N/A | 66 | TBC
Green Volt Offshore Wind Farm | PEHE41 | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| PEHE41 | Onshore 400kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore 220kV-2 | Offshore 220kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Hornsea 4A-2 Offshore Wind Farm | HOWD21 | HOWR2C | 2029 | Addition | 0 | 95 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWD21 | HOWR2C | 2029 | Addition | 0 | 95 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWR2C | HOWW2F | 2029 | Addition | 0 | 24 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWR2C | HOWW2F | 2029 | Addition | 0 | 24 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Hornsea 3A-2 Offshore Wind Farm | NORM41 | HOWC42 | 2029 | Addition | 0 | 1.8 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| HOWC4X | HOWW4X | 2029 | Addition | 0 | 220 | Cable | TBC | TBC | TBC | HVDC | ±320 | N/A | 1320
Morecambe Offshore Wind Farm | PEWO41 | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| PEWO42 | Onshore 400kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
North Sea B(Irish Sea) Offshore Substation | WYLA41 | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| WYLA42 | Onshore 400kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore 220kV-2 | Offshore 220kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
OWPL Offshore Windfarm | SPIT41 | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| SPIT42 | Onshore 400kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Project Elizabeth Offshore Windfarm | BODE41 | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BODE42 | Onshore 400kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Rampion Extension Windfarm | BOLN41 | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BOLN41 | Onshore 400kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore 220kV-2 | Offshore 220kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Salamander Offshore Wind Farm | PEHE11 | Onshore 132 kV HV | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 132 | TBC
| Onshore 66 kV HV | Offshore 66 kV HV | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 66 | TBC
Vanguard East Offshore Wind Farm | NECT41 | VGEO41 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter LV | VGEWX1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | ±365 | N/A | 1320
| Onshore AC Platform | Offshore AC Platform | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore AC Platform | Offshore AC Platform | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Awel Y Mor Extension Wind Farm | BODE41 | Onshore 400kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BODE41 | Onshore 400kV-2 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore 220kV-2 | Offshore 220kV-2 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Caledonia Wind Farm | GRNS41 | Onshore 400kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| GRNS41 | Onshore 400kV-2 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-3 | Offshore 275kV-3 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-4 | Offshore 275kV-4 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
East Anglia 2B Offshore Wind Farm | Onshore 220kV-2 | Offshore 220kV-2 | 2032 | Addition | 0 | 95 | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Five Estuaries Wind Farm | EAAW4 | Onshore 400kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore 220kV-2 | Offshore 220kV-2 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
GT R4 Wind Farm | WEMA41 | Onshore 400kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-3 | Offshore 275kV-3 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Llyr 1 Offshore Wind Farm | PEMB41 | Onshore 400kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
Llyr 2 Offshore Wind Farm | PEMB41 | Onshore 400kV-2 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
Machair Offshore Wind Farm | Onshore DC Switching Station | Offshore Converter station | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | ±525 | N/A | 2000
Marram Offshore Wind Farm | LOSD41 | Onshore 400kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter station 400kV-1 | Offshore Converter station -1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | TBC | N/A | 1500
North Falls Offshore Wind Farm | EAAW4 | Onshore 400kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
North Sea Offshore Substation | Onshore 400kV-1 | Onshore DC | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | ±365 | N/A | 1320
| North Humber Coastal 400kV | Onshore 400kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
Race Bank Extension Windfarm | MABL4 | Onshore 400kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| MABL4 | Onshore 400kV-2 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Spiorad na Mara offshore windfarm | LEWI41 | Onshore 400kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Talisk | LEWI41 | Onshore 400kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Alverdiscott 2 XL Offshore Windfarm | ALVE41 | Onshore 400kV-1 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| ALVE41 | Onshore 400kV-2 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Ayre Offshore Wind Farm | BANN41 | Onshore 400kV-1 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BANN41 | Onshore 400kV-2 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
BELLROCK OFFSHORE WINDFARM | SW_E1A | Onshore 275kV-1 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Buchan 01 Offshore Wind Farm | NEDE41 | Onshore 400kV-1 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| NEDE41 | Onshore 400kV-2 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Gatroben Offshore Wind Farm | HAWP41 | Onshore Converter HV | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter LV | Onshore DC Platform | 2035 | Addition | 0 | 166 | Cable | TBC | TBC | TBC | HVDC | ±320 | N/A | TBC
| Onshore AC Platform | Offshore AC Platform | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore AC Platform | Offshore AC Platform | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Llywelyn Extension Offshore Wind Farm | ALVE41 | Onshore 400kV-1 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| ALVE41 | Onshore 400kV-2 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Llywelyn Floating Offshore Wind Farm | PEMB41 | Onshore 400kV-1 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
Morven Offshore Wind Farm | HAWP41 | Onshore Converter HV | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter LV | Onshore DC Platform | 2035 | Addition | 0 | 166 | Cable | TBC | TBC | TBC | HVDC | ±320 | N/A | TBC
| Onshore AC Platform | Offshore AC Platform | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore AC Platform | Offshore AC Platform | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Morven Extension Offshore Wind Farm | HAWP41 | Onshore Converter HV | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter LV | Onshore DC Platform | 2035 | Addition | 0 | 166 | Cable | TBC | TBC | TBC | HVDC | ±320 | N/A | TBC
| Onshore AC Platform | Offshore AC Platform | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore AC Platform | Offshore AC Platform | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Muir Mhor Offshore Wind Farm | NEDE41 | Onshore 400kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| NEDE41 | Onshore 400kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore 220kV-2 | Offshore 220kV-2 | 2029 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
NPI A offshore wind farm | EAAW4 | Onshore 400kV-1 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Ossian Offshore Wind farm | LINC41 | Onshore 400kV-1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| WEMA41 | Onshore 400kV-2 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter station 400kV-1 | Offshore Converter station -1 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | ±525 | N/A | 2000
| Onshore Converter station 400kV-2 | Offshore Converter station -2 | 2032 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | ±525 | N/A | 2000
Stromar Offshore Wind Farm | GRNS41 | Onshore 400kV-1 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| GRNS41 | Onshore 400kV-2 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore 220kV-2 | Offshore 220kV-2 | 2035 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
HND | R4_1_1 | Birkhill Wood | 2031 | Addition | 0 | 163 | Cable | TBC | TBC | TBC | HVDC | ±525 | N/A | 1440
| R4_2_1 | Birkhill Wood | 2031 | Addition | 0 | 208 | Cable | TBC | TBC | TBC | HVDC | ±525 | N/A | 1440
| PA_2 | Blyth | 2029 | Addition | 0 | 145.01 | Cable | TBC | TBC | TBC | HVDC | ±525 | N/A | 1800
| Ballantrae | SW_W1 | 2032 | Addition | 0 | 173.6 | Cable | TBC | TBC | TBC | HVDC | ±525 | N/A | 2000

## B-3-1a
B-3-1a - SHE Transmission Transformers for 2024/25
Node 1 | Node 2 | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA)
ABNE1Q | ABNE3- | 1.05 | 27.98 | 0 | 60
ABNE1R | ABNE3- | 1.05 | 28.5 | 0 | 60
AIGA1Q | AIGA5- | 1.76 | 44.89 | 0 | 22.5
ALNE1Q | ALNE3J | 0.365 | 26 | 0 | 120
ALNE1R | ALNE3J | 0.365 | 26 | 0 | 120
ANSU1- | ANSU3- | 0.817 | 27.121 | 0 | 45
ARBR1Q | ARBR3- | 0.7 | 28.29 | 0 | 45
ARBR1R | ARBR3- | 0.7 | 28.29 | 0 | 45
ARDK1- | ARDK3K | 0.807 | 24.876 | 0 | 45
ARMO1J | ARMO3- | 0.615 | 17.82 | -0.026 | 60
BEAU1J | BEAU1P | 0.177 | 3.6 | 0 | 150
BEAU1J | BEAU2J | 0.1486 | 5.3035 | -0.0006 | 360
BEAU1J | BEAU2J | 0.6786 | 12.1644 | -0.0009 | 120
BEAU1J | BEAU3- | 1.04 | 27.73 | 0 | 45
BEAU1K | BEAU1Q | 0.177 | 3.6 | 0 | 150
BEAU1K | BEAU3- | 1.04 | 27.73 | 0 | 45
BEAU2J | BEAU1J | 0.1486 | 5.3035 | -0.002 | 360
BEAU2J | BEAU1J | 0.6786 | 12.1644 | 0 | 120
BEAU2K | BEAU1K | 0.1486 | 5.3035 | -0.002 | 360
BEAU2K | BEAU1K | 0.1486 | 5.3035 | -0.002 | 360
BEAU2K | BEAU4- | 0.0374 | 1.5937 | -0.0004 | 1200
BEAU4- | BEAU2J | 0.0376 | 1.5954 | -0.001 | 1200
BEAU4- | BEAU2K | 0.0374 | 1.5937 | -0.001 | 1200
BEIN11 | BEIN31 | 0.36 | 18 | 0 | 120
BERB2Q | BERB3- | 0.42 | 20 | 0 | 120
BHLA11 | BHLA31 | 0.36 | 18 | 0 | 120
BLHI1J | BLHI2J | 0.1486 | 5.3035 | -0.0006 | 360
BLHI1K | BLHI2K | 0.1506 | 5.3034 | -0.0006 | 360
BLHI4- | BLHI2J | 0.0264 | 1.5331 | -0.001 | 1200
BLHI4- | BLHI2K | 0.0262 | 1.5331 | -0.001 | 1200
BOAG1Q | BOAG3- | 0.611 | 24.993 | 0 | 60
BOAG1R | BOAG3- | 0.605 | 24.826 | 0 | 60
BRCW2J | BRCW3- | 0.42 | 20 | 0 | 120
BRCW2K | BRCW3- | 0.42 | 20 | 0 | 120
BRID1Q | BRID3- | 0.633 | 28.76 | 0 | 60
BRID1R | BRID3- | 0.637 | 28.943 | 0 | 60
BROA1Q | BROA3- | 1.19 | 39 | 0 | 30
BROR1- | BROR3- | 0.763 | 25.144 | 0 | 45
BUMU1Q | BUMU3- | 0.366 | 25.37 | -0.034 | 90
BUMU1R | BUMU3- | 0.376 | 25.42 | -0.035 | 90
CAAD1Q | CAAD3- | 0.3042 | 24.7991 | -0.0083 | 120
CAAD1Q | CAAD3J | 0.2621 | 24.6736 | -0.0222 | 120
CAAD1R | CAAD3- | 0.3042 | 24.7991 | -0.0083 | 120
CAAD1R | CAAD3J | 0.2621 | 24.6736 | -0.0222 | 120
CAIN2- | CAIN3J | 0.36 | 18 | 0 | 120
CASS1Q | CASS3- | 1.518 | 39.871 | 0 | 30
CEAN1Q | CEAN5- | 1.182 | 36.714 | 0 | 30
CHAR1- | CHAR3- | 0.407 | 26.975 | 0 | 90
CHAR1R | CHAR3- | 0.407 | 26.975 | 0 | 90
CLAC1Q | CLAC5J | 0.75 | 25 | 0 | 60
CLAY1Q | CLAY3- | 0.87 | 24.92 | 0 | 60
CLAY1R | CLAY3- | 0.87 | 24.92 | 0 | 60
CLUN1Q | CLUN5J | 0.71 | 19.53 | 0 | 60
CLUN1R | CLUN5K | 0.71 | 19.55 | 0 | 60
COGA1- | COGA3- | 0.324 | 17.9 | 0 | 90
CONN1J | CONN2J | 0.143 | 5.3036 | -0.0006 | 360
CORI1J | CORI3- | 0.5 | 25 | 0 | 90
CORI1J | CORI3J | 1 | 20 | 0 | 90
COUA1Q | COUA3- | 0.2143 | 25.0741 | -0.0067 | 120
COUA1R | COUA3- | 0.2151 | 25.1241 | -0.0092 | 120
CRAI1- | CRAI3- | 1.78 | 29.9 | 0 | 30
CRAI1Q | CRAI3- | 1.75 | 30.27 | 0 | 30
CRAR1R | CRAR3- | 0.36 | 18 | 0 | 90
CREA1- | CREA3- | 0.36 | 18 | 0 | 120
CRSS1J | CRSS1Q | 0.0582 | 2.145 | 0 | 240
CRSS1J | CRSS2A | 0.2466 | 9.0008 | -0.0005 | 240
CRSS1J | CRSS3- | 0.3629 | 18.0297 | -0.0123 | 90
CRSS1K | CRSS1R | 0.0582 | 2.1492 | 0 | 240
CRSS1K | CRSS2B | 0.2459 | 9.0175 | -0.0005 | 240
CULL1Q | CULL5- | 1.46 | 37.6 | 0 | 25
DAAS2- | DAAS3- | 0.417 | 20 | 0 | 120
DEAN1Q | DEAN5- | 1.01 | 25.1 | 0 | 40
DORE11 | DORE31 | 0.21 | 9.89 | 0 | 120
DORE12 | DORE32 | 0.21 | 9.89 | 0 | 120
DOUN1- | DOUN2- | 0.2112 | 7.7054 | -0.0005 | 240
DOUN1- | DOUN2- | 0.2237 | 7.9135 | -0.0006 | 240
DOUN1- | DOUN3- | 0.4676 | 26.1 | 0 | 90
DOUN1- | DOUN3- | 0.434 | 25.95 | 0 | 90
DUBE1Q | DUBE3- | 1.52 | 39.4 | 0 | 30
DUDH1Q | DUDH3- | 0.78 | 24.93 | 0 | 60
DUDH1R | DUDH3- | 0.78 | 23.93 | 0 | 60
DUGR1Q | DUGR3- | 0.617 | 17.65 | -0.029 | 60
DUNM1- | DUNM3- | 0.172 | 17.9 | 0 | 120
DUNO1Q | DUNO3- | 2 | 24.49 | 0 | 45
DUNO1R | DUNO3- | 2 | 24.5801 | 0 | 45
DYCE1Q | DYCE3- | 0.4015 | 24.819 | -0.0194 | 90
DYCE1R | DYCE3- | 0.3974 | 24.7301 | -0.0007 | 90
EDIN1- | EDIN3- | 0.558 | 16.991 | 0 | 60
ELGI1Q | ELGI3- | 0.63 | 27.98 | 0 | 90
ELGI1R | ELGI3- | 0.63 | 27.78 | 0 | 90
ERRO1A | ERRO1J | 0.04 | 1.942 | 0 | 240
ERRO1B | ERRO1K | 0.04 | 1.942 | 0 | 240
ERRO1J | ERRO1T | 0.068 | 3.73 | 0 | 150
ERRO1J | ERRO5L | 0.72 | 26.6 | 0 | 60
ERRO1K | ERRO5J | 0.72 | 26.6 | 0 | 60
FAAR1Q | FAAR3J | 0.9 | 28.34 | 0 | 90
FAAR1R | FAAR3K | 0.9 | 28.34 | 0 | 90
FARI1J | FARI2J | 0.4989 | 8.2933 | -0.038 | 120
FARI1K | FARI2K | 0.4955 | 8.3186 | -0.038 | 120
FASN2- | FASN3- | 0.42 | 20 | 0 | 120
FASN2- | FASN3- | 0.42 | 20 | 0 | 120
FAUG1- | FAUG2J | 0.2606 | 7.7039 | -0.0005 | 240
FAUG1- | FAUG2K | 0.2629 | 7.7038 | -0.0005 | 240
FAUG1- | FAUG4J | 0.2149 | 8.0138 | -0.013 | 240
FAUG1- | FAUG4J | 0.3185 | 8.4523 | -0.013 | 240
FAUG1J | FAUG4J | 0.108 | 3.957 | -0.0007 | 480
FAUG1K | FAUG4K | 0.108 | 3.957 | -0.0007 | 480
FAUG1Q | FAUG3- | 0.5 | 25 | 0 | 90
FERO1- | FERO3- | 0.3697 | 10.5 | 0 | 90
FETT1- | FETT2R | 0.217 | 4.2737 | -0.0006 | 240
FETT1- | FETT3S | 0.6 | 20 | 0 | 120
FIDD1B | FIDD1R | 0.11 | 4.11 | 0 | 150
FIDD1Q | FIDD3- | 0.4567 | 26.23 | 0 | 90
FIDD1R | FIDD3- | 0.4562 | 26.084 | 0 | 90
FINL1Q | FINL5- | 0.96 | 27.11 | 0 | 45
FRAS1Q | FRAS3- | 0.642 | 26.904 | 0 | 45
FRAS1R | FRAS3- | 0.642 | 26.904 | 0 | 45
FWIL1Q | FWIL3- | 0.499 | 24.995 | 0 | 120
FWIL1R | FWIL3- | 0.499 | 24.995 | 0 | 120
FYRI1J | FYRI2J | 0.0967 | 3.8863 | -0.0006 | 480
FYRI1K | FYRI2K | 0.0971 | 3.8738 | -0.0006 | 480
GLDO1G | GLDO8- | 0.206 | 10.681 | 0 | 120
GLEN1Q | GLEN5- | 0.55 | 21.94 | 0 | 70
GLFA1- | GLFA3- | 1.111 | 28 | 0 | 90
GORW2- | GORW3- | 0.258 | 20.06 | 0 | 120
GRIF1S | GRIF36 | 0.248 | 16.298 | 0 | 120
GRIF1T | GRIF38 | 0.247 | 16.248 | 0 | 120
GRUB1Q | GRUB3- | 0.499 | 24.995 | 0 | 90
GRUB1R | GRUB3- | 0.499 | 24.995 | 0 | 90
INGA1Q | INGA5- | 1.287 | 25 | 0 | 30
INNE1J | INNE3- | 0.89 | 27.87 | 0 | 60
INNE1K | INNE3- | 0.9 | 28 | 0 | 60
INNE1L | INNE3- | 0.427 | 26.774 | 0 | 90
INVB2A | INVR1- | 0.2217 | 4.3026 | -0.0071 | 240
INVB2B | INVR1- | 0.2164 | 4.257 | -0.0066 | 240
KEIT1- | KEIT2Q | 0.2735 | 8.6123 | -0.0007 | 240
KEIT1- | KEIT2R | 0.3328 | 8.9105 | -0.0389 | 240
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90
KEIT1- | KEIT3A | 0.4281 | 25.8965 | 0 | 90
KEIT1- | KEIT3A | 0.499 | 24.995 | 0 | 90
KIIN1- | KIIN3- | 0.772 | 24.877 | 0 | 45
KIIN1- | KIIN3- | 0.769 | 24.521 | 0 | 45
KILO1- | KILO3- | 0.88 | 27.78 | 0 | 45
KINT1- | KINT2J | 0.3771 | 10.1929 | -0.018 | 240
KINT1- | KINT2K | 0.3751 | 10.2314 | -0.0147 | 240
KINT1- | KINT2K | 0.6786 | 12.1477 | -0.0009 | 120
KINT1- | KINT3- | 1.04 | 27.65 | 0 | 60
KINT1- | KINT3- | 0.78 | 25 | 0 | 60
KINT1- | KINT3- | 0.456 | 26.107 | 0 | 90
KINT2J | KINT4K | 0.0253 | 1.2081 | -0.0005 | 1200
KINT2K | KINT4J | 0.0252 | 1.1997 | -0.0005 | 1200
KIOR1Q | KIOR5- | 1.78 | 45.42 | 0 | 22.5
KNOC1J | KNOC2J | 0.2216 | 4.311 | -0.0076 | 240
KNOC1J | KNOC2K | 0.2205 | 4.3319 | -0.0006 | 240
LAIR1- | LAIR3- | 0.425 | 24.674 | 0 | 90
LOCB1J | LOCB2J | 0.2181 | 8.1262 | -0.0007 | 240
LOCB1K | LOCB2K | 0.22 | 8.197 | -0.0007 | 240
LOCH1- | LOCH5J | 1.968 | 79.976 | -0.0008 | 36
LOCH1- | LOCH5K | 1.968 | 79.976 | -0.0008 | 36
LUIC1Q | LUIC5J | 0.763 | 37.548 | 0 | 45
LUIC1R | LUIC5K | 0.7668 | 37.548 | 0 | 45
LUNA1Q | LUNA3- | 0.435 | 25.018 | 0 | 90
LUNA1R | LUNA3- | 0.3145 | 29.6083 | -0.0222 | 120
LYND1Q | LYND3- | 0.78 | 24.3 | 0 | 60
LYND1R | LYND3- | 0.78 | 24.73 | 0 | 60
MACD1Q | MACD3- | 0.83 | 18.89 | 0 | 90
MACD1R | MACD3- | 0.83 | 18.89 | 0 | 90
MELG1J | MELG4J | 0.108 | 3.957 | -0.0007 | 480
MELG1K | MELG4K | 0.106 | 3.957 | -0.0007 | 480
MELG4J | MELG8J | 0.25 | 12 | 0 | 100
MELG4J | MELG8K | 0.25 | 12 | 0 | 100
MILC1R | MILC3- | 0.78 | 24.83 | 0 | 60
MILC1S | MILC3- | 0.88 | 28.13 | 0 | 60
MILW1Q | MILW3- | 0.439 | 24.896 | 0 | 90
MOSS1Q | MOSS5- | 1.192 | 36.847 | 0 | 30
MOSS1R | MOSS5- | 1.2267 | 36.913 | 0 | 30
MYBS1S | MYBS3J | 0.5 | 25 | 0 | 120
MYBS1S | MYBS3K | 0.3837 | 24.98 | 0 | 120
MYBS1S | MYBS3M | 0.2645 | 24.6069 | -0.024 | 120
MYBS1T | MYBS3J | 0.5 | 25 | 0 | 120
MYBS1T | MYBS3K | 0.3837 | 24.98 | 0 | 120
MYBS1T | MYBS3N | 0.2578 | 24.757 | -0.024 | 120
NAIR1Q | NAIR3- | 1.06 | 28.6 | 0 | 60
NAIR1R | NAIR3- | 1.05 | 28.6 | 0 | 60
NANT1Q | NANT5- | 1.47 | 56.67 | 0 | 30
ORRI1Q | ORRI3- | 0.564 | 16.824 | 0 | 60
ORRI1R | ORRI5- | 2.17 | 48.75 | 0 | 20
PEHE1- | PEHE1- | 0.2649 | 9.2254 | -0.0005 | 240
PEHE1- | PEHE2Q | 0.4842 | 9.9549 | -0.0178 | 240
PEHE1- | PEHE2R | 0.3423 | 8.8892 | -0.0364 | 240
PEHE1- | PEHS5- | 2.58 | 42.33 | 0 | 15
PEHE2J | PEHE4J | 0.026 | 1.533 | -0.0005 | 1200
PEHE2K | PEHE4K | 0.026 | 1.533 | -0.0005 | 1200
PEHE2R | PEHE1- | 0.3423 | 8.8892 | -0.0364 | 240
PEHG1Q | PEHG3- | 1.05 | 28.53 | 0 | 45
PEHG1R | PEHG3- | 1.05 | 28.4 | 0 | 45
PERS1Q | PERS2Q | 0.3363 | 8.9062 | -0.0412 | 240
PERS1Q | PERS3- | 0.407 | 26.975 | 0 | 90
PERS1R | PERS2R | 0.3341 | 8.8645 | -0.0419 | 240
PERS1R | PERS3- | 0.407 | 26.975 | 0 | 90
PORA1T | PORA3- | 1.803 | 29.812 | 0 | 30
PORA1U | PORA3- | 1.803 | 29.812 | 0 | 30
QUOI1- | QUOI5- | 1.34 | 33.13 | 0 | 30
RANN1Q | RANN3Q | 0.43 | 24.66 | 0 | 90
RANN1R | RANN3Q | 0.43 | 24.66 | 0 | 90
REDM1Q | REDM3- | 0.91 | 27 | 0 | 60
REDM1R | REDM3- | 0.9 | 27.83 | 0 | 60
ROTI3- | ROTI4J | 0.556 | 25 | 0 | 120
ROTI3- | ROTI4K | 0.556 | 25 | 0 | 120
SFEE1C | SFEE5- | 1.8333 | 76.6667 | -0.0121 | 36
SFEE1D | SFEE5- | 1.8333 | 76.6667 | -0.0121 | 36
SFIL1Q | SFIL5- | 1.99 | 39.48 | 0 | 25
SHIN1- | SHIN3- | 0.425 | 26.05 | 0 | 90
SHIN1- | SHIN3- | 0.437 | 26.22 | 0 | 90
SHIN1- | SHIN5- | 1.4823 | 80.16 | 0 | 40
SLOY1L | SLOY5L | 0.79 | 23.08 | 0 | 50
SLOY1M | SLOY5M | 0.79 | 22.9 | 0 | 50
SLOY1N | SLOY5N | 0.79 | 22.98 | 0 | 50
SLOY1P | SLOY5P | 0.8 | 23.2 | 0 | 50
SPIT1J | SPIT2J | 0.218 | 8.185 | -0.0007 | 240
SPIT1J | SPIT2J | 0.218 | 8.23 | -0.0007 | 240
SPIT1K | SPIT2K | 0.131 | 4.99 | -0.0006 | 360
SPIT1M | SPIT2K | 0.129 | 4.99 | -0.0006 | 360
STRB2- | STRB3W | 0.251 | 19.873 | 0 | 120
STRI1Q | STRI3- | 0.407 | 26.975 | 0 | 90
STRI1R | STRI3- | 0.407 | 26.975 | 0 | 90
STRL1- | STRL3P | 0.2 | 17.74 | -0.01 | 120
STRL1- | STRL3Q | 0.2 | 17.65 | -0.01 | 120
STRL1- | STRL3R | 0.2 | 17.67 | -0.01 | 120
STRW1- | STRW3- | 0.05 | 18 | 0 | 90
TARL1Q | TARL3- | 2.42 | 41 | 0 | 30
TARL1R | TARL3- | 2.13 | 38.53 | 0 | 30
TAYN1Q | TAYN3- | 0.315 | 28.787 | 0 | 90
TAYN1R | TAYN3- | 0.315 | 28.787 | 0 | 90
TEAL1- | TEAL2J | 0.3619 | 10.1602 | -0.0118 | 180
TEAL1- | TEAL2K | 0.2564 | 11.7305 | -0.0131 | 180
TEAL1- | TEAL2K | 0.5506 | 11.8761 | -0.0008 | 180
TEAL2A | TEAL2J | 0.005 | 1.185 | 0 | 700
TEAL2B | TEAL2K | 0.005 | 1.185 | 0 | 700
THUS1J | THUS2J | 0.0985 | 3.9363 | -0.0005 | 480
THUS1J | THUS3- | 0.2621 | 24.6736 | -0.022 | 120
THUS1K | THUS2K | 0.1 | 3.9362 | -0.0006 | 480
THUS1K | THUS3- | 0.2614 | 24.7403 | -0.02 | 120
TOMT1J | TOMT2J | 0.098 | 3.905 | -0.0006 | 480
TOMT1K | TOMT2K | 0.098 | 3.905 | -0.0006 | 480
TUMB1Q | TUMB5- | 1.63 | 77.76 | 0 | 21
TUMB1R | TUMB5- | 1.63 | 77.76 | 0 | 21
TUMM1J | TUMM2J | 0.259 | 7.7457 | -0.0005 | 240
TUMM1K | TUMM2K | 0.2595 | 7.829 | -0.0005 | 240
WIOW1Q | WIOW3- | 0.88 | 24.5 | 0 | 60
WIOW1R | WIOW3- | 0.88 | 24.5 | 0 | 60
WOHI1Q | WOHI3- | 0.62 | 27.24 | 0 | 90
WOHI1R | WOHI3- | 0.61 | 27.31 | 0 | 90

## B-3-1b
B-3-1b - SPT Transformers for 2024/25
Node1 | Node2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
AIKE3A | WESE1- | 0.5667 | 13.2333 | 0 | 90
AIKE3B | WESE1- | 0.5667 | 13.2333 | 0 | 90
AREC1- | AREC3- | 0.4634 | 24.4456 | -0.0064 | 60
AREC1- | AREC3A | 0.3886 | 16.84 | -0.0241 | 90
AREC1- | AREC3B | 0.3915 | 16.7288 | -0.0227 | 90
AYR-2Q | AYR-3- | 0.4868 | 20.2441 | 0 | 120
AYR-2R | AYR-3- | 0.2752 | 25.1818 | -0.0142 | 120
BAGA1Q | BAGA3- | 0.741 | 27.0343 | 0 | 90
BAGA1R | BAGA3- | 0.741 | 27.2233 | 0 | 90
BAIN1Q | BAIN3- | 0.5545 | 26.2275 | -0.0056 | 60
BAIN1R | BAIN3- | 0.491 | 26.2454 | -0.0056 | 60
BERW1Q | BERW3- | 0.9683 | 26.4656 | -0.0061 | 60
BERW1R | BERW3- | 0.7912 | 26.5549 | -0.0061 | 60
BLAH1- | BLAH3A | 0.3363 | 27.798 | -0.0152 | 90
BLAH1- | BLAH3A | 0.3386 | 27.9313 | -0.0106 | 90
BLAH1- | BLAH3B | 0.3394 | 27.9424 | -0.015 | 90
BLAH1- | BLAH3B | 0.342 | 28.0646 | -0.0103 | 90
BLCW1- | BLCW3- | 0.3083 | 16.9083 | -0.0283 | 90
BLKL1- | BLKL3A | 0.0943 | 18.6775 | 0 | 90
BLKL1- | BLKL3B | 0.0955 | 18.6553 | 0 | 90
BLLX1- | BLLX3- | 0.2833 | 16.8643 | -0.0133 | 90
BONN1- | BONN3- | 0.4288 | 27.1188 | -0.0146 | 90
BONN1- | BONN3- | 0.4334 | 27.5521 | -0.0092 | 90
BONN2A | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BONN2B | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BPGR3J | GRMO2- | 0.3876 | 19.4628 | -0.0275 | 120
BPGR3K | GRMO2- | 0.3093 | 18.8225 | -0.0373 | 120
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BROX1Q | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
BROX1R | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
CAFA1Q | CAFA5R | 1.0894 | 32.6818 | 0 | 30
CATY1Q | CATY3- | 1.015 | 25.8801 | -0.1318 | 60
CATY1R | CATY3- | 1.0164 | 25.6132 | -0.0966 | 60
CCSS1- | CCSS3- | 0.273 | 13.8306 | -0.0276 | 120
CHAP1- | CHAP3- | 0.4338 | 27.5299 | -0.0175 | 90
CHAP1- | CHAP3- | 0.4294 | 27.5633 | -0.0188 | 90
CHAS2Q | CHAS3C | 0.4875 | 18.1601 | -0.1331 | 120
CHAS2R | CHAS3A | 0.5214 | 27.5617 | -0.1031 | 120
CLYM2- | CLYM3A | 0.4722 | 20.2028 | -0.1542 | 120
CLYM2- | CLYM3B | 0.4917 | 19.994 | -0.1425 | 120
CLYN2Q | CLYN3A | 0.3432 | 13.0038 | -0.0115 | 120
CLYN2Q | CLYN3B | 0.3423 | 12.9455 | -0.0108 | 120
CLYN2Q | CLYN3C | 0.3414 | 13.0205 | -0.0094 | 120
CLYN2Q | CLYN3D | 0.3472 | 12.9954 | -0.0133 | 120
CLYS2R | CLYS3A | 0.3406 | 12.9789 | -0.0112 | 120
CLYS2R | CLYS3X | 0.3475 | 13.0037 | -0.0112 | 120
COAL4- | COAL1A | 0.1055 | 6.777 | -0.0931 | 360
COAL4- | COAL1A | 0.1258 | 9.7909 | -0.0801 | 240
COAL4- | COAL1B | 0.1258 | 9.7909 | -0.0801 | 240
COAL4- | COAL1B | 0.0914 | 6.4382 | -0.0751 | 360
COAT2Q | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COAT2R | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COCK2- | COCK3- | 0.2841 | 27.8235 | -0.0171 | 120
COCK2- | COCK3- | 0.4792 | 18.7022 | -0.2214 | 120
COCK4Q | COCK2- | 0.0135 | 1.6479 | -0.3338 | 1000
COCK4R | COCK2- | 0.013 | 1.5999 | -0.2252 | 1000
COYL1- | COYL3- | 0.9944 | 20.8596 | -0.0881 | 60
COYL1- | COYL3- | 0.9217 | 21.6804 | 0 | 60
COYL2- | COYL1- | 0.1035 | 8.6744 | -0.051 | 240
COYL2- | COYL1- | 0.1036 | 8.7952 | -0.0513 | 240
CROO1Q | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1Q | CROO3K | 0.9748 | 26.6155 | -0.0058 | 60
CROO1R | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1R | CROO3K | 0.9758 | 26.6321 | -0.0063 | 60
CRYR1- | CRYR31 | 0.2951 | 16.6641 | -0.2002 | 120
CRYR1- | CRYR32 | 0.2951 | 16.6641 | -0.2002 | 120
CRYR4- | CRYR1- | 0.1496 | 10.0489 | -0.0583 | 240
CRYR4- | CRYR1A | 0.1217 | 9.8451 | -0.067 | 240
CUMB1Q | CUMB3- | 0.7407 | 29.324 | -0.129 | 90
CUMB1R | CUMB3- | 0.741 | 27.111 | 0 | 90
CUPA1Q | CUPA3- | 0.4473 | 26.3962 | -0.0195 | 90
CUPA1R | CUPA3- | 0.4518 | 26.4517 | -0.0195 | 90
CURR1A | CURR5- | 3.225 | 79.0009 | 0 | 30
CURR1B | CURR5- | 3.23 | 79.0007 | 0 | 30
CURR2- | CURR1A | 0.1079 | 8.5702 | -0.0341 | 240
CURR2- | CURR1A | 0.1148 | 8.4492 | -0.073 | 240
CURR2- | CURR1B | 0.1205 | 8.4741 | -0.084 | 240
DALM1- | DALM3- | 0.447 | 27.333 | 0 | 90
DALM1- | DALM3- | 0.469 | 27.3326 | 0 | 90
DALM2Q | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DALM2R | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DENN2- | DENN1- | 0.1452 | 8.6093 | -0.1299 | 240
DENN4- | DENN2- | 0.0164 | 1.6449 | -0.1161 | 1000
DESA1Q | DESA3- | 0.2828 | 16.831 | -0.0195 | 90
DEVM1- | DEVM3- | 1.0878 | 19.9704 | -1.7577 | 60
DEVM1- | DEVM3- | 1.0869 | 20.0038 | -1.8609 | 60
DEVM4- | DEVM1- | 0.1335 | 8.3739 | -0.1562 | 240
DEVM4- | DEVM1- | 0.1338 | 8.3739 | -0.2103 | 240
DEVO1- | DEVO3- | 0.74 | 29.6674 | 0 | 90
DEVO1- | DEVO3- | 0.4705 | 26.4736 | -0.0191 | 90
DEWP2Q | DEWP3- | 0.2932 | 21.048 | -0.093 | 120
DEWP2R | DEWP3- | 0.2936 | 21.0667 | -0.079 | 120
DONO1- | DONO3A | 0.1922 | 14.207 | -0.0113 | 120
DRCR1Q | DRCR3- | 0.5273 | 27.0838 | -0.0105 | 90
DRCR1R | DRCR3- | 0.5227 | 26.8727 | -0.0109 | 90
DRUM2Q | DRUM3- | 0.3963 | 23.9134 | -0.0247 | 120
DRUM2R | DRUM3- | 0.3917 | 24.4135 | -0.0224 | 120
DUMF1- | DUMF3A | 0.367 | 11.7276 | 0 | 90
DUMF1- | DUMF3B | 0.375 | 11.794 | 0 | 90
DUMF1- | DUMF3I | 0.766 | 20.5657 | 0 | 60
DUNB1Q | DUNB3A | 0.8069 | 21.4849 | -0.3294 | 60
DUNB1R | DUNB3A | 0.8069 | 21.4849 | -0.3294 | 60
DUNB1S | DUNB3B | 0.4121 | 28.9304 | -0.0087 | 90
DUNB1T | DUNB3B | 0.3569 | 28.82 | -0.0089 | 90
DUNE1- | DUNE3- | 0.4271 | 19.5731 | -0.0091 | 90
DUNE1- | DUNE3- | 0.4249 | 19.3175 | -0.0084 | 90
DUNF1Q | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNF1R | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNH1S | DUNH3- | 0.3428 | 28.2868 | -0.0105 | 90
DUNH1T | DUNH3- | 0.3495 | 28.1867 | -0.0166 | 90
EAST1Q | EAST5- | 4.1511 | 74.885 | -0.1943 | 15
ECCL1- | ECCL3- | 1.054 | 26.8827 | 0 | 60
ECCL1- | ECCL3- | 1.04 | 26.7314 | 0 | 60
ECCL4A | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
ECCL4B | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
EERH2- | EERH3- | 0.2569 | 25.607 | -0.0414 | 120
EERH2- | EERH3- | 0.306 | 18.0724 | -0.0486 | 120
EKIL2S | EKIL3A | 0.303 | 17.9224 | -0.0436 | 120
EKIL2T | EKIL3B | 0.303 | 17.8441 | -0.0485 | 120
EKIS2- | EKIS3A | 0.4948 | 24.3283 | -0.2487 | 120
EKIS2- | EKIS3B | 0.4773 | 24.2453 | -0.2651 | 120
ELDE1Q | ELDE3- | 0.9136 | 19.8123 | -0.3053 | 60
ELDE1R | ELDE3- | 0.9136 | 19.9791 | -0.3053 | 60
ELVA1- | ELVA3A | 0.4635 | 24.1789 | -0.0101 | 60
ELVA2R | ELVA1- | 0.0984 | 5.8325 | -0.2121 | 360
ELVA4- | ELVA2Q | 0.0309 | 3.2879 | -0.8983 | 500
ELVA4- | ELVA2R | 0.031 | 3.2859 | -0.8082 | 500
ERSK1Q | ERSK3- | 0.5259 | 26.8282 | -0.0075 | 60
ERSK1R | ERSK3- | 0.5296 | 27.1115 | -0.0073 | 60
EWEH1Q | EWEH3- | 0.2827 | 16.8532 | -0.0191 | 90
FALL4- | FALL3A | 0.2564 | 16.6647 | 0 | 120
FALL4- | FALL3B | 0.2564 | 16.6647 | 0 | 120
FINN1Q | FINN3- | 0.5198 | 26.0837 | -0.0091 | 90
FINN1R | FINN3- | 0.5221 | 25.9836 | -0.0092 | 90
GALA1- | GALA3- | 0.4311 | 25.9297 | -0.0244 | 90
GALA1- | GALA3- | 0.4452 | 26.6074 | -0.0132 | 90
GAWH1Q | GAWH3- | 0.2843 | 16.9754 | -0.0173 | 90
GIFF2Q | GIFF3A | 0.4958 | 18.4517 | -0.196 | 120
GIFF2R | GIFF3B | 0.4868 | 18.3352 | -0.2147 | 120
GLGL1Q | GLGL3- | 0.3327 | 27.8536 | -0.0092 | 90
GLGL1R | GLGL3- | 0.3349 | 27.9091 | -0.0086 | 90
GLLE1- | GLLE5- | 2.3889 | 72.9609 | 0 | 30
GLLU1Q | GLLU3- | 0.961 | 24.5329 | 0 | 60
GLLU1R | GLLU3- | 1.069 | 25.0839 | 0 | 60
GLNI1- | GLNI3- | 0.6998 | 27.8134 | -0.1093 | 90
GLNI1- | GLNI3- | 0.6894 | 27.7692 | -0.1102 | 90
GLRO2- | GLRO3A | 0.479 | 24.4953 | 0 | 120
GLRO2- | GLRO3B | 0.4763 | 24.412 | 0 | 120
GORG1Q | GORG3- | 0.7875 | 26.555 | -0.0062 | 60
GORG1R | GORG3- | 0.8167 | 26.9876 | -0.0071 | 60
GOVA1Q | GOVA3- | 0.5223 | 26.1503 | -0.0083 | 90
GOVA1R | GOVA3- | 0.5155 | 26.1727 | -0.0108 | 90
GRMO2- | GRMO3C | 0.4781 | 25.1621 | -0.0871 | 120
GRMO2- | GRMO3C | 0.4985 | 25.2451 | -0.0869 | 120
GRNA4- | GRNA1- | 0.1472 | 10.0573 | -0.0558 | 240
GRNA4- | GRNA1- | 0.1252 | 9.7909 | -0.081 | 240
HADH1- | HADH3- | 0.438 | 13.3003 | 0 | 120
HAGR1Q | HAGR3- | 0.5381 | 25.2943 | -0.0108 | 60
HAGR1R | HAGR3- | 0.5478 | 25.8775 | -0.008 | 60
HARE1- | HARE3A | 0.2433 | 16.789 | -0.0205 | 90
HARE1- | HARE3B | 0.2411 | 16.8111 | -0.0205 | 90
HAWI1- | HAWI3- | 1.0278 | 25.6127 | -0.1152 | 60
HAWI1- | HAWI3- | 1.0136 | 25.8802 | -0.1316 | 60
HELE1Q | HELE3- | 0.9544 | 20.8615 | 0 | 60
HELE1R | HELE3- | 0.6843 | 28.6252 | -0.0082 | 60
HUER4- | HUER1- | 0.1122 | 9.3465 | -0.2007 | 360
HUER4- | HUER1- | 0.1134 | 9.4715 | -0.1992 | 360
HUNF1Q | HUNF3- | 0.8042 | 16.5638 | -0.06 | 60
HUNF1R | HUNF3- | 0.7893 | 16.4144 | -0.0596 | 60
HUNN4A | HUNN2A | 0.0538 | 2.9466 | -0.0947 | 240
HUNN4B | HUNN2B | 0.0537 | 2.9441 | -0.0946 | 240
INKE1Q | INKE3- | 0.6185 | 23.7697 | 0 | 90
INKE1R | INKE3- | 0.6222 | 23.7696 | 0 | 90
JOHN1Q | JOHN3- | 0.7058 | 27.8077 | -0.0092 | 60
JOHN1R | JOHN3- | 0.7078 | 27.9911 | -0.013 | 60
KAIM2- | KAIM3A | 0.4944 | 20.244 | -0.245 | 120
KAIM2- | KAIM3B | 0.4972 | 19.1602 | -0.2454 | 120
KENE3- | MIDM1- | 0.3875 | 17.9673 | -0.0311 | 70
KENN1- | KENN3- | 0.1922 | 14.207 | -0.0113 | 120
KEOO1- | KEOO5- | 2.9 | 71.608 | -0.028 | 30
KIER1Q | KIER3- | 0.4314 | 27.1188 | -0.0087 | 90
KIER1R | KIER3- | 0.7227 | 25.3341 | 0 | 90
KILB1Q | KILB3- | 0.9214 | 23.8656 | -0.6492 | 60
KILB1Q | KILB5- | 4.3575 | 97.6528 | -0.0539 | 20
KILB1R | KILB3- | 0.8919 | 23.8333 | -0.6287 | 60
KILB1R | KILB5- | 4.3825 | 97.2012 | -0.059 | 20
KILG2- | KILG3A | 0.1883 | 12.5319 | -0.0338 | 120
KILG2- | KILG3B | 0.1869 | 12.5153 | -0.028 | 120
KILG2- | KILG3C | 0.1866 | 12.4236 | -0.0359 | 120
KILS2- | KILS1- | 0.143 | 8.6447 | -0.1299 | 240
KILS2- | KILS3- | 0.4823 | 24.1619 | -0.2177 | 120
KILS2- | KILS3- | 0.5013 | 24.0114 | -0.1726 | 120
KILS4- | KILS2- | 0.018 | 1.6069 | -0.5085 | 1000
KILS4- | KILS2- | 0.0134 | 1.6649 | -0.5095 | 1000
KILS4T | KILS2- | 0.0148 | 1.6509 | -0.1193 | 1000
KILT2Q | KILT3A | 0.5378 | 28.745 | -0.0524 | 120
KILT2R | KILT3A | 0.5378 | 28.745 | -0.0524 | 120
KILW1Q | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
KILW1R | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
KYPE1- | KYPE3- | 0.1922 | 14.207 | -0.0113 | 120
KYPE1- | KYPE3A | 0.3076 | 16.875 | -0.0289 | 90
LEVE1Q | LEVE3- | 0.979 | 20.6001 | 0 | 60
LEVE1R | LEVE3- | 0.944 | 20.7502 | 0 | 60
LING1Q | LING3- | 0.7346 | 29.6576 | -0.1478 | 90
LING1R | LING3- | 0.7309 | 28.7685 | -0.109 | 90
LINM1Q | LINM3- | 0.4309 | 27.7078 | -0.0186 | 90
LINM1R | LINM3- | 0.4283 | 27.73 | -0.0186 | 90
MAHI2- | MAHI1- | 0.1284 | 8.6824 | -0.2535 | 240
MAHI2- | MAHI3- | 0.2928 | 12.1973 | -0.0267 | 120
MAYB1- | MAYB3- | 1.84 | 33.2825 | 0 | 30
MAYB1- | MAYB3- | 1.84 | 34.3174 | 0 | 30
MIDM1- | MIDM3- | 0.4664 | 13.6087 | -0.0075 | 60
MOFF1- | MOFF3A | 0.4635 | 24.1789 | -0.0101 | 60
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOSH1Q | MOSH5J | 1.1896 | 19.9646 | 0 | 37
MOSH1R | MOSH5K | 1.1896 | 19.9646 | 0 | 37
MOSM1A | MOSM3Q | 1.4321 | 26.6282 | 0 | 45
MOSM1B | MOSM3R | 1.4321 | 26.6282 | 0 | 45
MOSM2- | MOSM1A | 0.151 | 8.332 | -0.1299 | 240
MOSM2- | MOSM1B | 0.157 | 8.7486 | -0.1299 | 240
NEAR2Q | NEAR3- | 0.4856 | 18.2435 | -0.1614 | 120
NEAR2R | NEAR3- | 0.4856 | 18.1602 | -0.1723 | 120
NECU2- | NECU1- | 0.1173 | 8.6992 | -0.0311 | 240
NECU2- | NECU1- | 0.1173 | 8.5659 | -0.0322 | 240
NECU2- | NECU1- | 0.1167 | 8.7367 | -0.0297 | 240
NECU2- | NECU1Q | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1R | 0.1164 | 8.5534 | -0.0287 | 240
NEIL2- | NEIL1- | 0.1509 | 8.4778 | -0.1862 | 240
NEIL2- | NEIL1- | 0.1457 | 8.5196 | -0.1979 | 240
NEIL4Q | NEIL1C | 0.1122 | 9.3882 | -0.2007 | 360
NEIL4Q | NEIL2C | 0.0181 | 1.6169 | -0.4986 | 1000
NEIL4R | NEIL2D | 0.0133 | 1.6749 | -0.3581 | 1000
NETS1- | NETS3- | 0.8311 | 28.2878 | -0.0097 | 60
NOKY1- | NOKY3A | 0.1922 | 14.207 | -0.0113 | 120
NOKY1- | NOKY3B | 0.1922 | 14.207 | -0.0113 | 120
PAIS1S | PAIS3- | 0.5609 | 26.1773 | -0.004 | 60
PAIS1T | PAIS3- | 0.7736 | 20.352 | -0.216 | 60
PART1Q | PART3- | 0.9103 | 21.2972 | 0 | 60
PART1R | PART3- | 0.93 | 21.5299 | 0 | 60
POOB2Q | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
POOB2R | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
PORD2Q | PORD3- | 0.3702 | 18.3296 | -0.1621 | 120
PORD2R | PORD3- | 0.3698 | 18.3963 | -0.1357 | 120
REDH1- | REDH3- | 0.6267 | 27.5484 | 0 | 60
REDH1- | REDH3- | 0.94 | 20.7787 | 0 | 90
SACO1Q | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1Q | SACO3K | 0.9542 | 21.1451 | 0 | 60
SACO1R | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1R | SACO3K | 0.9683 | 21.4114 | 0 | 60
SAKN1- | SAKN3- | 0.325 | 9.9364 | -0.0113 | 120
SANX1Q | SANX3- | 0.7366 | 27.1233 | -0.009 | 60
SANX1R | SANX3- | 0.7377 | 27.19 | -0.0098 | 60
SHRU2Q | SHRU3A | 0.535 | 28.5617 | -0.0629 | 120
SHRU2R | SHRU3B | 0.2914 | 23.7232 | -0.0252 | 120
SIGH2Q | SIGH3A | 0.4564 | 27.5518 | -0.032 | 180
SIGH2R | SIGH3A | 0.4281 | 27.53 | -0.0372 | 180
SMEA2- | SMEA1- | 0.1271 | 8.7241 | -0.043 | 240
SMEA4R | SMEA2- | 0.0134 | 1.6639 | -0.2312 | 1000
SPAV1Q | SPAV3- | 0.728 | 26.6656 | 0 | 90
SPAV1R | SPAV3- | 0.728 | 26.6656 | 0 | 90
STHA2A | STHA3- | 0.4557 | 30.1188 | -0.0331 | 90
STHA2B | STHA3- | 0.4917 | 19.994 | -0.1424 | 114
STHA4A | STHA2A | 0.018 | 1.7059 | -0.2252 | 1000
STHA4B | STHA2B | 0.0134 | 1.6949 | -2.0384 | 1000
STIR1S | STIR3- | 0.6 | 27.5446 | 0 | 90
STIR1T | STIR3- | 0.503 | 27.1331 | 0 | 90
STLE1Q | STLE3S | 0.4217 | 25.741 | -0.028 | 87
STLE1R | STLE3S | 0.4235 | 25.6743 | -0.0254 | 87
TELR1Q | TELR3- | 0.9688 | 26.4656 | -0.0572 | 60
TELR1R | TELR3- | 0.6325 | 28.5763 | -0.0081 | 60
TONG1- | TONG3- | 0.533 | 26.9114 | -0.0078 | 60
TONG1- | TONG3- | 0.5309 | 27.0615 | -0.008 | 60
TONG1- | TONG5- | 1.6834 | 33.9917 | -0.01 | 30
TONG1- | TONG5- | 1.6721 | 34.0924 | -0.0269 | 30
TONG1R | TONG1- | 0.0267 | 1.3331 | 0 | 90
TONG1R | TONG1Q | 0.0125 | 2.5 | 0 | 90
TORN4- | TORN1- | 0.1674 | 8.0399 | -0.0509 | 240
TORN4- | TORN1- | 0.1688 | 8.0816 | -0.0663 | 240
WFIE1A | WFIE3- | 0.6617 | 28.7591 | -0.0062 | 60
WFIE1B | WFIE3- | 0.6619 | 28.6257 | -0.0112 | 60
WFIE2- | WFIE1A | 0.1408 | 8.6113 | -0.1827 | 240
WFIE2- | WFIE1B | 0.1264 | 8.7366 | -0.1602 | 240
WGEO2Q | WGEO3- | 0.4889 | 18.2518 | -0.2083 | 120
WGEO2R | WGEO3- | 0.4911 | 18.3268 | -0.2083 | 90
WHHO2Q | WHHO3- | 0.4128 | 24.9549 | -0.0345 | 120
WHHO2R | WHHO3- | 0.5236 | 20.1599 | -0.1959 | 120
WHTL1S | WHTL3- | 2 | 27.1108 | 0 | 45
WHTL1T | WHTL3- | 2 | 27.1108 | 0 | 45
WISH2- | WISH1- | 0.1297 | 8.8874 | -0.2192 | 215
WISH2- | WISH3- | 0.4944 | 20.1606 | -0.2477 | 120
WISH2- | WISH3- | 0.4824 | 24.1285 | -0.2277 | 120
WISH2- | WISH3S | 0.4382 | 19.1617 | -0.195 | 120
WISH2- | WISH3T | 0.4889 | 18.3268 | -0.1166 | 120
WISH4- | WISH2- | 0.0163 | 1.6529 | -0.0792 | 1000
WISH4- | WISH2- | 0.0134 | 1.6849 | -0.0814 | 1000
WIYH2- | WIYH1- | 0.1568 | 8.4569 | -0.3494 | 240
WIYH2- | WIYH1- | 0.1524 | 8.457 | -0.3487 | 240
WIYH2- | WIYH1- | 0.0987 | 8.8078 | -0.0518 | 240
WIYH4Q | WIYH2- | 0.0133 | 1.6699 | -0.3581 | 1000
WLEE2- | WLEE3A | 0.2583 | 12.2648 | -0.0357 | 120
WLEE2- | WLEE3B | 0.2592 | 12.1922 | -0.0271 | 120
WLEE2- | WLEE3C | 0.26 | 12.3048 | -0.0301 | 120
WLEX2- | WLEX3A | 0.2306 | 12.2562 | -0.0292 | 120
WLEX2- | WLEX3B | 0.2306 | 12.2728 | -0.0271 | 120
WLEX2- | WLEX3C | 0.2306 | 12.2728 | -0.0275 | 120

## B-3-1c
B-3-1c - NGET Transformer for 2024/25
Node1 | Node2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ABHA4A | ABHA11 | 0.1658 | 8.4025 | -1.5604 | 275
ABHA4B | ABHA12 | 0.1658 | 8.4025 | -1.5604 | 264
ABTH21 | ABTH11 | 0.1366 | 8.0648 | -0.0471 | 279
ABTH21 | ABTH12 | 0.1646 | 8.0383 | -0.1808 | 211
ABTH21 | ABTH13 | 0.0977 | 8.1994 | -1.7127 | 212
ALDW21 | ALDW31 | 0.4848 | 24.6692 | -0.018 | 135
ALDW21 | ALDW31 | 0.3543 | 25.4142 | -0.4983 | 135
ALDW21 | ALDW31 | 0.7076 | 26.5771 | -0.0784 | 83
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 98
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 98
ALVE4A | ALVE11 | 0.1118 | 8.3874 | -0.0906 | 278
ALVE4B | ALVE11 | 0.1621 | 8.0984 | -0.0747 | 275
AMEM4A | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 270
AMEM4A | AMEM11 | 0.1303 | 7.8698 | -0.4285 | 240
AMEM4B | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 255
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 278
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 277
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 278
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 268
BARK21 | BARW31 | 0.618 | 29.2635 | -0.2527 | 109
BARK21 | BARW32 | 0.618 | 29.2635 | -0.2527 | 110
BARK22 | BARK11 | 0.1221 | 8.0467 | -0.0391 | 217
BARK22 | BARK11 | 0.1183 | 8.3927 | -0.2368 | 240
BARK22 | BARW31 | 0.618 | 29.2635 | -0.2527 | 110
BARK22 | BARW32 | 0.618 | 29.2635 | -0.2527 | 109
BARK22 | BARW32 | 0.492 | 19.4438 | -0.4018 | 100
BARK41 | BARK21 | 0.0268 | 2.7989 | -0.3188 | 817
BARK41 | BARK22 | 0.0268 | 2.7989 | -0.3188 | 817
BEDD21 | BEDD11 | 0.167 | 7.9774 | -0.2092 | 258
BEDD21 | BEDD12 | 0.1067 | 8.0868 | -0.034 | 264
BEDD21 | BEDT1A | 0.1007 | 8.1333 | -0.2371 | 133
BEDD22 | BEDD12 | 0.1067 | 8.0868 | -0.034 | 273
BEDD23 | BEDD11 | 0.167 | 7.9774 | -0.2092 | 273
BEDD23 | BEDT1B | 0.2264 | 12.2479 | -0.6062 | 126
BEDD4A | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 797
BEDD4A | BEDD23 | 0.0258 | 2.6799 | -1.2431 | 797
BEDD4B | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 800
BEDD4B | BEDD22 | 0.0258 | 2.6805 | -1.2431 | 950
BESW21 | BESW11 | 0.1004 | 8.1994 | -0.2371 | 240
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 273
BESW21 | BESW12 | 0.1411 | 8.6331 | -0.2264 | 267
BESW21 | BESW12 | 0.1411 | 8.6331 | -0.2264 | 267
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 278
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 274
BIGG41 | BIGG11 | 0.148 | 8.1678 | -0.3849 | 240
BIGG41 | BIGG11 | 0.148 | 8.1678 | -0.3849 | 240
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BISW21 | BISW11 | 0.0918 | 8.7537 | -0.0575 | 278
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 240
BLYT21 | BLYT1A | 0.1666 | 8.378 | -0.1047 | 278
BLYT21 | BLYT1B | 0.1666 | 8.378 | -0.1047 | 278
BLYT21 | BLYT61 | 0.2275 | 10.8456 | -0.0697 | 209
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 138
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 138
BLYT41 | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1148
BLYT41 | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1148
BODE41 | SASA11 | 0.1311 | 7.9055 | -0.1016 | 240
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 310
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 309
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 276
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 277
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 309
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 278
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 278
BRAI4A | BRAI11 | 0.1373 | 8.1976 | -0.1719 | 240
BRAI4B | BRAI11 | 0.1307 | 7.9515 | -0.1098 | 278
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW4A | BRAW21 | 0.0175 | 1.5879 | -4.0069 | 1094
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 272
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 271
BRFO41 | BRFO11 | 0.1307 | 7.9515 | -0.1098 | 240
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 267
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 267
BRIM2A | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 263
BRIM2B | BRIM11 | 0.1266 | 8.6449 | -1.9406 | 274
BRIM2C | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 262
BRIM2D | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 262
BRIN41 | BRIN21 | 0.0146 | 1.609 | -1.8746 | 1117
BRIN41 | BRIN22 | 0.0133 | 1.5936 | -1.2059 | 1100
BRLE41 | BRLE11 | 0.103 | 7.9231 | -0.0638 | 275
BRLE41 | BRLE12 | 0.1471 | 8.4008 | -0.1719 | 253
BRLE41 | BRLE13 | 0.1471 | 8.4008 | -0.1719 | 253
BRLE41 | BRLE14 | 0.103 | 7.9231 | -0.0638 | 270
BRLE41 | BRLE1A | 0.1303 | 7.8698 | -0.4285 | 263
BRLE41 | BRLE1B | 0.1303 | 7.8698 | -0.4285 | 263
BRWA41 | BRWA11 | 0.1047 | 8.2285 | -0.0886 | 240
BRWA42 | BRWA11 | 0.1047 | 8.2285 | -0.0886 | 240
BURW41 | BURW11 | 0.1059 | 8.3327 | -0.671 | 264
BURW41 | BURW11 | 0.1056 | 8.2208 | -0.6711 | 264
BURW41 | BURW11 | 0.1347 | 7.9905 | -0.1259 | 278
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 279
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 279
BUSH21 | BUSH11 | 0.1048 | 8.8443 | -0.0335 | 278
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 279
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 279
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 278
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 279
BUST4A | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100
BUST4B | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100
CANT41 | CANT13 | 0.1509 | 8.2849 | -0.3279 | 264
CANT41 | CANT14 | 0.1658 | 8.426 | -0.2939 | 264
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 211
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 211
CAPE21 | CAPE11 | 0.196 | 8.3446 | -0.7059 | 198
CAPE21 | CAPE1A | 0.1366 | 8.0648 | -0.0471 | 279
CAPE21 | CAPE1B | 0.171 | 8.8392 | -0.0268 | 211
CAPE4A | CAPE21 | 0.0178 | 1.5995 | -1.2431 | 845
CAPE4B | CAPE21 | 0.0185 | 1.614 | -0.5638 | 886
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 278
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 278
CARR21 | CARR11 | 0.1927 | 8.5256 | -0.5357 | 211
CARR21 | CARR11 | 0.1681 | 8.3396 | -1.4878 | 201
CARR21 | CARR12 | 0.1927 | 8.5256 | -0.5357 | 211
CARR21 | CARR12 | 0.2264 | 12.2479 | -0.6062 | 129
CARR21 | CARR12 | 0.2847 | 12.2467 | -1.4346 | 120
CARR41 | CARR11 | 0.1372 | 8.0197 | -0.1238 | 272
CARR4A | CARR21 | 0.0185 | 1.614 | -0.5638 | 886
CARR4B | CARR21 | 0.0185 | 1.614 | -0.5638 | 886
CELL41 | CELL11 | 0.1658 | 8.4025 | -1.5604 | 280
CELL41 | CELL11 | 0.1307 | 7.9515 | -0.1098 | 278
CELL41 | CELL11 | 0.1658 | 8.4025 | -1.5604 | 274
CELL41 | CELL12 | 0.1373 | 8.1976 | -0.1719 | 278
CELL41 | CELL12 | 0.1658 | 8.4025 | -1.5604 | 278
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 254
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 253
CHSI21 | CHSI11 | 0.167 | 7.9774 | -0.2092 | 255
CHSI21 | CHSI11 | 0.1411 | 8.6331 | -0.2264 | 249
CHSI21 | CHSI1A | 0.0978 | 8.1332 | -0.0252 | 153
CHSI21 | CHSI1B | 0.1411 | 8.6331 | -1.598 | 240
CHTE21 | CHTE11 | 0.1594 | 8.6081 | -0.2215 | 261
CHTE21 | CHTE11 | 0.1545 | 7.6337 | -0.562 | 240
CHTE21 | CHTE12 | 0.0918 | 8.7537 | -0.0575 | 278
CHTE21 | CHTE12 | 0.1545 | 7.6337 | -0.562 | 251
CILF41 | CILF2A | 0.017 | 1.6132 | -5.1203 | 750
CILF41 | CILF2B | 0.017 | 1.6132 | -5.1203 | 750
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR11 | 0.1229 | 8.3873 | -0.1147 | 269
CITR41 | CITR11 | 0.1132 | 8.2492 | -0.1115 | 278
CITR41 | CITR12 | 0.1264 | 7.974 | -0.1303 | 277
CITR41 | CITR12 | 0.1132 | 8.2492 | -0.1115 | 278
CONQ41 | CONQ11 | 0.1044 | 7.8701 | -0.103 | 261
CONQ41 | CONQ11 | 0.1036 | 7.8606 | -0.1003 | 259
CONQ41 | CONQ12 | 0.1045 | 7.8806 | -0.0998 | 263
CONQ41 | CONQ13 | 0.1057 | 7.9352 | -0.339 | 240
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 273
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 272
COVE21 | COVE12 | 0.1623 | 8.097 | -1.5978 | 266
COVE21 | COVE12 | 0.1004 | 8.1994 | -0.2371 | 240
COWL41 | COWL11 | 0.1307 | 7.9515 | -0.1098 | 278
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 269
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 274
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB2A | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB2A | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB2B | 0.0176 | 1.5826 | -0.1148 | 750
CREB41 | CREB2B | 0.0176 | 1.5826 | -0.1148 | 750
CULJ4A | CULJ31 | 0.069 | 25 | 0 | 90
CULJ4A | CULJ32 | 0.069 | 25 | 0 | 90
CULJ4A | CULJ33 | 0.069 | 25 | 0 | 90
DIDC41 | MILP31 | 0.2087 | 15.2319 | -0.2971 | 150
DIDC41 | MILP31 | 0.2099 | 15.2986 | -0.2971 | 150
DRAK41 | DRAK11 | 0.1303 | 7.8698 | -0.4285 | 278
DRAK41 | DRAK11 | 0.1044 | 7.881 | -0.0832 | 240
DRAK41 | DRAK21 | 0.0178 | 1.5995 | -1.2431 | 849
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 277
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 274
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 206
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 206
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 440
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 440
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EASO41 | EASO12 | 0.103 | 7.9231 | -0.0638 | 263
EASO41 | LITB11 | 0.1018 | 7.841 | -0.432 | 240
EASO4A | EASO11 | 0.103 | 7.9231 | -0.0638 | 263
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 264
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 263
ECLA41 | ECLA12 | 0.1139 | 8.1036 | -2.059 | 278
ECLA41 | ECLA12 | 0.0997 | 8.0088 | -0.093 | 264
ELLA21 | ELLA11 | 0.1221 | 8.0467 | -0.0391 | 272
ELLA21 | ELLA11 | 0.1681 | 8.3396 | -1.4878 | 198
ELLA21 | ELLA12 | 0.1221 | 8.0467 | -0.0391 | 279
ELLA21 | ELLA12 | 0.1722 | 8.4551 | -0.2968 | 211
ELST21 | ELST12 | 0.1221 | 8.0467 | -0.0391 | 279
ELST21 | ELST13 | 0.1985 | 8.1167 | -0.4624 | 189
ELST21 | ELST13 | 0.1954 | 8.0796 | -0.2295 | 189
ELST22 | ELST11 | 0.1031 | 8.1045 | -0.0494 | 212
ELST22 | ELST11 | 0.1923 | 8.081 | -1.4418 | 187
ELST41 | ELST12 | 0.1039 | 7.8456 | -0.9345 | 240
ELST41 | ELST22 | 0.0181 | 1.5835 | -3.6502 | 1201
ELST4B | ELST21 | 0.0176 | 1.5828 | -0.1018 | 1137
ENDE41 | ENDE11 | 0.1303 | 7.8698 | -0.4285 | 278
ENDE41 | ENDE11 | 0.1118 | 8.3874 | -0.0906 | 278
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 274
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 273
EXET41 | EXET11 | 0.1307 | 7.9515 | -0.1098 | 278
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 278
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 269
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 268
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 268
FAWL41 | FAWL11 | 0.105 | 8.1922 | -0.1118 | 268
FECK21 | FECK61 | 0.3142 | 15.7855 | -1.1826 | 139
FECK41 | FECK21 | 0.0161 | 1.6372 | -0.0621 | 1100
FECK41 | FECK61 | 0.1832 | 14.0317 | -0.1803 | 199
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 194
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 194
FERR21 | FERR11 | 0.1147 | 8.673 | -0.0358 | 278
FERR21 | FERR61 | 0.237 | 10.8633 | -0.263 | 204
FERR23 | FERR11 | 0.1147 | 8.673 | -0.0358 | 278
FERR23 | FERR61 | 0.237 | 10.8633 | -0.263 | 203
FERR2A | FERR11 | 0.0918 | 8.7537 | -0.0575 | 278
FERR4A | FERR22 | 0.0133 | 1.5936 | -1.2059 | 1100
FERR4A | FERR23 | 0.0186 | 1.5729 | -7.729 | 1113
FIDF21 | FIDF11 | 0.1392 | 8.4361 | -0.781 | 271
FIDF21 | FIDF12 | 0.1594 | 8.6081 | -0.2215 | 261
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE11 | 0.1368 | 8.5406 | -0.262 | 232
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 274
FLEE41 | FLEE11 | 0.1372 | 8.0197 | -0.1238 | 278
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279
FOUR21 | FOUR31 | 0.306 | 19.9977 | -0.5499 | 100
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 45
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 45
FROD21 | FROD11 | 0.1927 | 8.5256 | -0.5357 | 211
FROD22 | FROD11 | 0.1392 | 8.4361 | -0.781 | 269
FROD41 | FROD11 | 0.054 | 4.8906 | -0.1253 | 499
FROD41 | FROD21 | 0.0176 | 1.5828 | -0.1018 | 1000
FROD41 | FROD22 | 0.0132 | 1.6756 | -0.4337 | 1063
FROD41 | WEAV71 | 0.0032 | 0.0205 | -0.1224 | 80
FROD41 | WEAV71 | 0.0032 | 0.0205 | -0.1224 | 80
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 263
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 263
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 279
GREN41 | GREN11 | 0.1312 | 7.9156 | -0.537 | 278
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 278
GREN41 | GREN12 | 0.1557 | 8.3736 | -0.4146 | 279
GREN41 | GREN12 | 0.1035 | 7.8472 | -0.0758 | 274
GRIW41 | GRIW11 | 0.1658 | 8.4025 | -1.5604 | 273
GRIW41 | GRIW12 | 0.1658 | 8.4025 | -1.5604 | 268
HACK2A | HACK61 | 0.2793 | 13.3304 | -0.6737 | 191
HACK2B | HACK61 | 0.2793 | 13.3304 | -0.6737 | 191
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK2A | 0.0182 | 1.5763 | -0.0904 | 1210
HACK41 | HACK2B | 0.0182 | 1.5763 | -0.0904 | 1210
HAMH41 | HAMH2A | 0.0175 | 1.5879 | -4.0069 | 1147
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 278
HAMH41 | LEMR11 | 0.1118 | 8.3874 | -0.0906 | 263
HAMH41 | LEMR11 | 0.1118 | 8.3874 | -0.0906 | 263
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 263
HARK21 | HARK11 | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK11 | 0.2264 | 12.2479 | -0.6062 | 137
HARK21 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK13 | 0.1147 | 8.673 | -0.0358 | 222
HARK41 | HARK21 | 0.0376 | 2.3797 | -3.9009 | 519
HARK41 | HARK21 | 0.0376 | 2.3797 | -3.9009 | 547
HARK41 | HARK21 | 0.0292 | 2.402 | -0.2732 | 438
HARK41 | HARK21 | 0.0192 | 2.6599 | -0.1528 | 950
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 127
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 127
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 192
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 191
HAWP4A | HAWP21 | 0.0132 | 1.6756 | -0.4337 | 1063
HEYS41 | HEYS11 | 0.122 | 8.1963 | -0.2446 | 277
HEYS41 | HEYS11 | 0.1658 | 8.4025 | -1.5604 | 275
HEYS41 | HEYS11 | 0.1372 | 8.0197 | -0.1238 | 278
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240
HIGM41 | HIGM21 | 0.0186 | 1.5729 | -7.729 | 1044
HIGM41 | HIGM4A | 0.0002 | 0.2873 | 0 | 2750
HINP41 | HINP21 | 0.0363 | 2.4397 | -2.1073 | 539
HINP41 | HINP22 | 0.0376 | 2.3797 | -3.9009 | 539
HUMR41 | HUMR31 | 0.6667 | 22.467 | -0.1612 | 90
HUMR41 | HUMR31 | 0.6667 | 22.256 | -0.1612 | 90
HURS21 | HURS1B | 0.1221 | 8.0467 | -0.0391 | 279
HURS21 | HURS1C | 0.1382 | 8.1742 | -0.1786 | 279
HURS21 | HURS1D | 0.1392 | 8.4361 | -0.781 | 279
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 265
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 264
HUTT41 | HUTT71 | 0.0032 | 0.0208 | 0 | 80
HUTT41 | HUTT71 | 0.0032 | 0.0208 | 0 | 80
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143
INDQ41 | INDQ11 | 0.1302 | 8.4532 | -10.3672 | 278
INDQ41 | INDQ11 | 0.1303 | 7.8698 | -0.4285 | 278
INDQ41 | INDQ11 | 0.1278 | 8.0061 | -0.2276 | 256
INDQ41 | INDQ11 | 0.1471 | 8.4008 | -0.1719 | 254
IROA21 | IROA11 | 0.1221 | 8.0467 | -0.0391 | 279
IROA21 | IROA11 | 0.1366 | 8.0648 | -0.0471 | 279
IROA21 | IROA12 | 0.1053 | 8.0652 | -0.0304 | 217
IROA21 | IROA12 | 0.1685 | 7.8148 | -1.385 | 210
IROA21 | IROA13 | 0.1266 | 8.6449 | -1.9406 | 250
IROA21 | IROA13 | 0.1685 | 7.8148 | -1.385 | 210
IRON41 | IRON11 | 0.1557 | 8.3736 | -0.4146 | 278
IRON41 | IRON12 | 0.1557 | 8.3736 | -0.4146 | 277
IRON41 | IRON13 | 0.1372 | 8.0197 | -0.1238 | 278
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 279
IVER21 | IVER11 | 0.1221 | 8.0467 | -0.0391 | 279
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 265
IVER21 | IVER61 | 0.2856 | 11.1999 | -2.5672 | 153
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125
IVER22 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 279
IVER22 | IVER61 | 0.2856 | 11.1999 | -2.5672 | 153
IVER4A | IVER21 | 0.0176 | 1.5828 | -0.1018 | 1135
IVER4A | IVER22 | 0.0133 | 1.5936 | -1.2059 | 1100
IVER4B | IVER21 | 0.0326 | 2.3798 | -3.9003 | 572
IVER4B | IVER2A | 0.0132 | 1.4627 | -2.0624 | 841
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 110
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 110
KEAD41 | KEAD11 | 0.1621 | 8.0984 | -0.0747 | 256
KEAD41 | KEAD11 | 0.1302 | 8.4532 | -10.3672 | 274
KEAD42 | KEAD11 | 0.1118 | 8.3874 | -0.0906 | 278
KEAD4C | KEAD41 | 0.0002 | 0.4178 | 0 | 2750
KEAD4D | KEAD41 | 0.0002 | 0.2873 | 0 | 2750
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1041 | 8.1035 | -0.0269 | 280
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR41 | KEAR21 | 0.0117 | 1.591 | -4.4806 | 1098
KEAR41 | KEAR21 | 0.0175 | 1.5879 | -4.0069 | 1000
KEMS41 | KEMS11 | 0.1658 | 8.426 | -0.2939 | 268
KEMS41 | KEMS11 | 0.1139 | 8.1036 | -2.059 | 264
KEMS41 | KEMS4A | 0.0071 | 0.2875 | 0 | 2750
KEMS41 | KEMS4B | 0.0071 | 0.2875 | 0 | 2750
KEMS41 | SHEE11 | 0.1621 | 8.0984 | -0.0747 | 236
KIBY21 | KIBY11 | 0.1221 | 8.0467 | -0.0391 | 279
KIBY21 | KIBY11 | 0.1221 | 8.0467 | -0.0391 | 279
KIBY21 | KIBY11 | 0.1392 | 8.4361 | -0.781 | 279
KIBY21 | KIBY11 | 0.1594 | 8.6081 | -0.2215 | 261
KIBY21 | KIBY11 | 0.1681 | 8.3396 | -1.4878 | 211
KINO41 | KINO11 | 0.1301 | 7.8864 | -0.5157 | 278
KINO41 | KINO11 | 0.1758 | 8.1226 | -0.2746 | 274
KIRK21 | KIRK11 | 0.1366 | 8.0648 | -0.0471 | 279
KIRK21 | KIRK11 | 0.1147 | 8.673 | -0.0358 | 264
KIRK21 | KIRK11 | 0.097 | 8.0997 | -0.027 | 266
KIRK21 | KIRK2A | 0.002 | 0.9802 | 0 | 760
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KNAR21 | KNAR11 | 0.1441 | 8.6238 | -0.2707 | 240
KNAR21 | KNAR11 | 0.1441 | 8.6238 | -0.2707 | 240
LACK21 | GRTO61 | 0.262 | 16.5813 | -0.4096 | 133
LACK21 | GRTO61 | 0.262 | 16.5813 | -0.4096 | 133
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 128
LACK21 | LACK61 | 0.4736 | 16.5344 | -0.54 | 126
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 126
LACK41 | LACK21 | 0.0175 | 1.5879 | -4.0069 | 1100
LACK41 | LACK21 | 0.0174 | 1.598 | -0.1503 | 1154
LACK41 | LACK2A | 0.0152 | 1.6463 | -0.1118 | 1185
LACK41 | LACK2B | 0.0182 | 1.5763 | -0.0904 | 1210
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 278
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 278
LALE21 | LALE11 | 0.1954 | 8.0796 | -0.2295 | 201
LALE21 | LALE11 | 0.196 | 8.3446 | -0.7059 | 200
LALE21 | LALE31 | 0.4848 | 24.6692 | -0.018 | 120
LALE21 | LALE31 | 0.4848 | 24.6692 | -0.018 | 120
LAND41 | LAND11 | 0.1372 | 8.0197 | -0.1238 | 278
LAND41 | LAND11 | 0.148 | 7.4973 | -0.3849 | 278
LAND42 | LAND11 | 0.1057 | 7.9352 | -0.339 | 263
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 278
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 278
LEGA41 | LEGA11 | 0.1175 | 8.6648 | -0.4173 | 263
LEGA41 | LEGA11 | 0.1303 | 7.8698 | -0.4285 | 278
LEGA4A | LEGA41 | 0.001 | 0.35 | 0 | 2002
LEGA4B | LEGA41 | 0.001 | 0.35 | 0 | 2002
LEIS4A | LEIS11 | 0.1057 | 7.8601 | -0.432 | 272
LISD21 | LISD11 | 0.1221 | 8.0467 | -0.0391 | 279
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 266
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 266
LISD21 | LISD11 | 0.1266 | 8.6449 | -1.9406 | 262
LITT41 | LITT11 | 0.1621 | 8.0984 | -0.0747 | 240
LITT41 | LITT11 | 0.0997 | 8.0088 | -0.093 | 240
LITT41 | LITT11 | 0.103 | 7.9231 | -0.0638 | 278
LITT41 | LITT2A | 0.014 | 2.6567 | -0.1528 | 1028
LITT41 | LITT2B | 0.014 | 2.6567 | -0.1528 | 1028
LOVE41 | LOVE11 | 0.1303 | 7.8698 | -0.4285 | 278
LOVE41 | LOVE11 | 0.1042 | 7.831 | 0 | 274
LOVE41 | LOVE12 | 0.1758 | 8.1226 | -0.2746 | 274
LOVE41 | LOVE12 | 0.1847 | 8.1296 | -0.2979 | 269
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 113
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 113
MACC41 | MACC21 | 0.018 | 1.6146 | -1.5533 | 884
MAGA21 | GRAN61 | 0.1642 | 10.921 | -0.0326 | 207
MAGA21 | GRAN61 | 0.1757 | 10.5541 | -0.0326 | 205
MANN41 | MANN11 | 0.1759 | 7.9134 | -0.267 | 279
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 272
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 272
MANN41 | MANN11 | 0.1326 | 8.774 | -0.7141 | 259
MANN41 | MANN11 | 0.1303 | 7.8698 | -0.4285 | 278
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK11 | 0.1041 | 7.8535 | -0.0851 | 265
MELK41 | MELK2A | 0.017 | 1.6132 | -5.1203 | 750
MELK41 | MELK2B | 0 | 1.692 | 0 | 886
MILH2A | MILH11 | 0.1266 | 8.6449 | -1.9406 | 264
MILH2A | MILH11 | 0.179 | 8.3648 | -4.7616 | 211
MILH2B | MILH12 | 0.1266 | 8.6449 | -1.9406 | 264
MILH2B | MILH12 | 0.1004 | 8.1994 | -0.2371 | 240
MITY41 | MITY11 | 0.1139 | 8.1036 | -2.059 | 263
MITY41 | MITY11 | 0.122 | 8.1963 | -0.2446 | 274
MITY41 | MITY12 | 0.1057 | 7.9352 | -0.339 | 263
MITY41 | MITY12 | 0.1812 | 9.1787 | -0.1253 | 278
MONF41 | MONF21 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF41 | MONF22 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF4A | MONF21 | 0.0176 | 1.5828 | -0.1018 | 1138
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 270
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 269
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 267
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 270
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120
NEEP4A | NEEP21 | 0.021 | 1.669 | -12.6082 | 1100
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 279
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 279
NEWX21 | NEWX11 | 0.1053 | 8.0451 | -0.0277 | 280
NEWX21 | NEWX61 | 0.2188 | 10.8367 | -0.1908 | 180
NEWX21 | NEWX61 | 0.3204 | 14.3298 | -0.2424 | 180
NEWX21 | NEWX62 | 0.2972 | 12.4333 | -0.1533 | 209
NEWX21 | NEWX62 | 0.1868 | 10.9484 | -0.0207 | 180
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 268
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 261
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 269
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 260
NHYD2A | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 187
NHYD2B | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 187
NHYD2B | NHYD61 | 0.2364 | 13.3312 | -0.1908 | 180
NINF41 | NINF11 | 0.1303 | 7.8698 | -0.4285 | 278
NINF41 | NINF11 | 0.1658 | 8.4025 | -1.5604 | 273
NINF41 | NINF12 | 0.1658 | 8.4025 | -1.5604 | 273
NINF41 | NINF12 | 0.1054 | 7.888 | -0.0784 | 259
NORL2A | NORL31 | 0.545 | 19.7925 | -0.1407 | 114
NORL2B | NORL31 | 0.545 | 19.7925 | -0.1407 | 114
NORM41 | NORM11 | 0.1264 | 8.4534 | -0.357 | 277
NORM41 | NORM11 | 0.1307 | 7.9515 | -0.1098 | 240
NORM41 | NORM12 | 0.1118 | 8.3874 | -0.0906 | 278
NORM41 | NORM1A | 0.1509 | 7.9378 | -0.9251 | 253
NORM41 | NORM1B | 0.1509 | 7.9378 | -0.9251 | 267
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 262
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 262
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 240
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 280
NORT41 | NORT21 | 0.0186 | 1.5729 | -7.729 | 1136
NORT41 | NORT21 | 0.0117 | 1.591 | -4.4806 | 1133
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 252
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 253
NURS4A | NURS11 | 0.103 | 7.9231 | -0.0638 | 262
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 279
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 279
OCKH21 | OCKH11 | 0.179 | 8.3648 | -4.7616 | 202
OCKH21 | OCKH2A | 0.0104 | 0.867 | -4.0354 | 760
OFFE21 | OFFE31 | 0.5135 | 18.2228 | -0.5477 | 115
OFFE21 | OFFE32 | 0.5135 | 18.2228 | -0.5477 | 113
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 261
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 261
OLDB2A | OLDB11 | 0.1004 | 8.3615 | -0.2374 | 261
OLDB4A | OLDB21 | 0.0146 | 1.609 | -1.8746 | 1172
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 269
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 269
OSBA42 | OSBA11 | 0.1372 | 8.0197 | -0.1238 | 278
PADI41 | PADI11 | 0.1373 | 8.1976 | -0.1719 | 274
PADI41 | PADI11 | 0.1051 | 7.8585 | -0.0834 | 262
PELH41 | PELH11 | 0.1175 | 8.6648 | -0.4173 | 264
PELH41 | PELH12 | 0.1175 | 8.6648 | -0.4173 | 264
PEMB41 | PEMB11 | 0.1658 | 8.4025 | -1.5604 | 276
PEMB41 | PEMB11 | 0.1471 | 8.4008 | -0.1719 | 275
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN21 | PENN11 | 0.1441 | 8.6238 | -0.2707 | 266
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN4A | PENN21 | 0.0176 | 1.5828 | -0.1018 | 1138
PENN4B | PENN21 | 0.0132 | 1.6756 | -0.4337 | 1063
PENT41 | PENT11 | 0.1471 | 8.4008 | -0.1719 | 257
PENT41 | PENT11 | 0.1621 | 8.0984 | -0.0747 | 255
PEWO2A | PENW11 | 0.1594 | 8.6081 | -0.2215 | 261
PEWO2B | PENW11 | 0.1594 | 8.6081 | -0.2215 | 261
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENW11 | 0.1311 | 7.9055 | -0.1016 | 278
PEWO41 | PEWO2A | 0.0189 | 1.6132 | -0.7226 | 1129
PEWO41 | PEWO2A | 0.0178 | 1.5995 | -1.2431 | 845
PEWO41 | PEWO2B | 0.0175 | 1.5879 | -4.0069 | 1139
PEWO41 | PEWO2B | 0.021 | 1.669 | -12.6082 | 876
PEWO41 | PEWO4A | 0.0046 | 0.2858 | -16.2245 | 2750
PEWO41 | PEWO4B | 0.0071 | 0.2875 | -16.2245 | 2750
PITS21 | PITS31 | 0.4975 | 20.4439 | -0.2606 | 110
PITS21 | PITS31 | 0.4975 | 20.4439 | -0.2606 | 110
PITS21 | PITS32 | 0.2998 | 20.1311 | -0.3705 | 120
PITS21 | PITS32 | 0.2998 | 20.1311 | -0.3705 | 120
POPP21 | POPP31 | 0.4905 | 24.145 | -0.1894 | 110
POPP21 | POPP31 | 0.2731 | 30.5821 | -0.0312 | 110
PYLE21 | PYLE11 | 0.1366 | 8.0648 | -0.0471 | 279
PYLE21 | PYLE11 | 0.2009 | 8.1596 | -0.5003 | 211
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 211
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 270
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 273
RATS41 | RATS11 | 0.1042 | 7.841 | -0.0895 | 240
RATS41 | RATS11 | 0.1047 | 8.2285 | -0.0886 | 262
RATS41 | RATS12 | 0.1373 | 8.1976 | -0.1719 | 278
RATS41 | RATS12 | 0.1278 | 8.0061 | -0.2276 | 277
RATS41 | RATS2A | 0.0146 | 1.609 | -1.8746 | 1125
RAYL41 | RAYM11 | 0.1309 | 7.8656 | -0.4549 | 262
RAYL41 | RAYM11 | 0.1045 | 7.8618 | -0.0882 | 240
RAYL41 | RAYM11 | 0.1035 | 7.8568 | -0.0758 | 240
RAYL41 | RAYM11 | 0.1303 | 7.8698 | -0.4285 | 262
REBR21 | REBR32 | 0.665 | 28.1922 | -0.151 | 111
REBR22 | REBR31 | 0.3375 | 30.6481 | -0.1769 | 132
REBR22 | REBR31 | 0.665 | 28.1922 | -0.151 | 112
RICH41 | RICH11 | 0.1186 | 7.8741 | -0.3958 | 240
RICH41 | RICH11 | 0.1181 | 7.9033 | -0.3958 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 278
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 278
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 278
ROCH21 | ROCH12 | 0.1183 | 8.3927 | -0.2368 | 140
ROCH4A | ROCH21 | 0.0098 | 1.5863 | -0.0631 | 1100
ROCK41 | ROCK1A | 0.054 | 4.8906 | -0.1253 | 460
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 267
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 267
RYEH41 | RYEH13 | 0.1372 | 8.0197 | -0.1238 | 253
RYEH42 | RYEH12 | 0.1055 | 8.2414 | -0.0848 | 267
RYEH43 | RYEH11 | 0.1326 | 8.774 | -0.7141 | 260
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 211
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 211
SAFO41 | SAFO11 | 0.1054 | 8.1656 | -0.1095 | 240
SAFO41 | SAFO11 | 0.1054 | 8.1606 | -0.1098 | 240
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 256
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 256
SELL4A | SELL11 | 0.0996 | 8.0568 | -1.1981 | 275
SELL4A | SELL11 | 0.0996 | 8.0568 | -1.1981 | 273
SELL4A | SELL12 | 0.103 | 7.9231 | -0.0638 | 270
SELL4A | SELL13 | 0.1621 | 8.0984 | -0.0747 | 256
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 115
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 114
SHRE4B | SHRE11 | 0.1057 | 7.9352 | -0.339 | 240
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 267
SIZE41 | SIZE12 | 0.103 | 7.9231 | -0.0638 | 268
SIZE41 | SIZE1A | 0.103 | 7.9231 | -0.0638 | 268
SIZE41 | SIZE1B | 0.103 | 7.9231 | -0.0638 | 269
SJOW21 | LODR61 | 0.3062 | 11.0235 | -0.4552 | 198
SJOW21 | SJOW13 | 0.167 | 7.9774 | -0.2092 | 249
SJOW41 | LODR61 | 0.1529 | 12.1324 | -0.0623 | 273
SJOW41 | LODR61 | 0.1403 | 12.3367 | -0.6356 | 240
SJOW41 | LODR62 | 0.1455 | 13.3242 | -0.0759 | 240
SJOW41 | LODR62 | 0.1307 | 7.9515 | -0.1098 | 268
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 271
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 272
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 271
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 270
SJOW41 | SJOW13 | 0.1055 | 8.1881 | -0.0865 | 240
SJOW41 | SJOW21 | 0.0224 | 2.5703 | -0.5831 | 804
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 264
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 278
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 270
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 240
SMAN21 | SMAN11 | 0.1052 | 8.2077 | -0.6621 | 279
SMAN21 | SMAN11 | 0.1441 | 8.6238 | -0.2707 | 266
SMAN21 | SMAN12 | 0.1441 | 8.6238 | -0.2707 | 266
SMAN21 | SMAN12 | 0.1221 | 8.0467 | -0.0391 | 279
SPEN41 | SPEN11 | 0.1293 | 7.8614 | -0.537 | 278
SPEN41 | SPEN11 | 0.1305 | 7.8823 | -0.5369 | 278
SPEN42 | SPEN11 | 0.1315 | 7.8822 | -0.5369 | 278
SSHI22 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 110
SSHI22 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 110
STAH4A | STAH11 | 0.122 | 8.1963 | -0.2446 | 274
STAH4B | STAH11 | 0.1046 | 7.8493 | -0.0881 | 271
STAL21 | STAL11 | 0.2188 | 8.097 | -1.9861 | 280
STAL21 | STAL11 | 0.1221 | 8.0467 | -0.0391 | 279
STAL21 | STAL11 | 0.1681 | 8.3396 | -1.4878 | 198
STAL21 | STAL11 | 0.1954 | 8.0796 | -0.2295 | 189
STAL4A | STAL21 | 0.0146 | 1.609 | -1.8746 | 1117
STAY41 | STAY4A | 0.0002 | 0.4178 | -13.831 | 2695
STAY41 | STYC11 | 0.103 | 7.9231 | -0.0638 | 266
STAY41 | STYC12 | 0.1046 | 7.8493 | -0.0881 | 271
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 138
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW21 | STEN11 | 0.0933 | 8.4245 | -0.0567 | 179
STEW21 | STES11 | 0.1366 | 8.0648 | -0.0471 | 274
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW41 | STEW21 | 0.0211 | 1.6463 | -14.2471 | 1172
STEW41 | STEW21 | 0.0107 | 1.5596 | -0.0734 | 1165
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 274
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 271
STSB4B | STSB4A | 0.0003 | 0.1825 | 0 | 1999
SUND41 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 252
SUND41 | SUND11 | 0.13 | 7.8739 | -0.5372 | 278
SUND41 | SUND31 | 0.2106 | 15.2133 | -0.0768 | 150
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 254
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 250
SWAN22 | SWAN11 | 0.1646 | 8.0383 | -0.1808 | 211
SWAN22 | SWAN11 | 0.1923 | 8.2361 | -0.4425 | 211
SWAN41 | SWAN11 | 0.1303 | 7.8698 | -0.4285 | 256
SWAN41 | SWAN12 | 0.1303 | 7.8698 | -0.4285 | 256
SWAN41 | SWAN21 | 0.0182 | 1.5763 | -0.0904 | 1210
SWAN4A | SWAN22 | 0.0178 | 1.5995 | -1.2431 | 851
SWAN4B | SWAN12 | 0.1307 | 7.9515 | -0.1098 | 263
TAUN41 | TAUN11 | 0.1049 | 8.1792 | -0.1104 | 274
TAUN42 | TAUN11 | 0.1459 | 8.045 | -0.2605 | 279
TEMP21 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 76
TEMP22 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 76
THOM21 | THOM61 | 0.3985 | 16.203 | -0.4431 | 122
THOM41 | THOM21 | 0.0189 | 1.6132 | -0.7226 | 879
THOM41 | THOM21 | 0.0185 | 1.614 | -0.5638 | 879
THOM42 | THOM2A | 0.0152 | 1.6463 | -0.1118 | 1100
THOM42 | THOM61 | 0.1844 | 13.1765 | -0.0474 | 180
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 209
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 209
THUR21 | THUR61 | 0.1699 | 10.8431 | -0.0403 | 200
TILB21 | TILB11 | 0.1004 | 8.1994 | -0.2371 | 240
TILB21 | TILB12 | 0.1 | 8.0952 | -0.2374 | 240
TILB41 | TILB13 | 0.1307 | 7.9515 | -0.1098 | 240
TILB41 | TILB14 | 0.1303 | 7.8698 | -0.4285 | 278
TILB4A | TILB21 | 0.0376 | 2.1949 | -10.6848 | 1153
TILB4B | TILB21 | 0.0117 | 1.591 | -4.4806 | 1102
TINP21 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 111
TINP21 | TINP32 | 0.5083 | 24.0899 | -0.1921 | 135
TINP22 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 111
TINP22 | TINP32 | 0.5083 | 24.0899 | -0.1921 | 120
TODP21 | TODP61 | 0.3931 | 16.4953 | -2.1281 | 139
TODP21 | TODP61 | 0.459 | 16.6187 | -0.1963 | 101
TOTT21 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 265
TOTT22 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 265
TOTT23 | TOTT12 | 0.1688 | 8.3316 | -1.1711 | 265
TOTT24 | TOTT12 | 0.179 | 8.3648 | -4.7616 | 198
TRAW21 | TRAW11 | 0.1004 | 8.1994 | -0.2371 | 240
TRAW21 | TRAW11 | 0.0937 | 8.437 | -0.1095 | 150
TRAW41 | TRAW21 | 0.0132 | 1.6756 | -0.4337 | 966
TRAW41 | TRAW21 | 0.021 | 1.669 | -12.6082 | 888
TREM21 | TREM31 | 0.4636 | 17.894 | -0.1238 | 116
TREM21 | TREM31 | 0.593 | 20.7915 | -0.122 | 115
TYNE21 | TYNE11 | 0.1221 | 8.0467 | -0.0391 | 279
TYNE21 | TYNE11 | 0.1411 | 8.6331 | -0.2264 | 267
TYNE21 | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 44
TYNE2A | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 44
UPPB21 | UPPB31 | 0.4636 | 17.894 | -0.1238 | 113
UPPB21 | UPPB31 | 0.5107 | 17.9527 | -0.2251 | 113
UPPB22 | UPPB11 | 0.0979 | 8.4411 | -0.0271 | 262
UPPB22 | UPPB11 | 0.097 | 8.457 | -0.0263 | 222
USKM21 | ALST31 | 0.5135 | 18.2228 | -0.5477 | 116
USKM21 | ALST32 | 0.5107 | 17.9527 | -0.2251 | 116
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 263
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 279
USKM21 | USKM12 | 0.1221 | 8.0467 | -0.0391 | 263
WALH41 | PORH11 | 0.1471 | 8.4008 | -0.1719 | 253
WALH41 | PORH11 | 0.103 | 7.9231 | -0.0638 | 275
WALH41 | PORH11 | 0.1372 | 8.0197 | -0.1238 | 278
WALH41 | PORH11 | 0.1036 | 7.8597 | -0.0784 | 274
WALP41 | WALP11 | 0.1042 | 7.891 | -0.4318 | 274
WALP41 | WALP11 | 0.1304 | 7.9364 | -0.479 | 278
WALP41 | WALP11 | 0.1509 | 8.2849 | -0.3279 | 275
WALP41 | WALP11 | 0.1621 | 8.0984 | -0.0747 | 275
WALP41 | WALP11 | 0.1759 | 7.9134 | -0.4285 | 274
WALX4A | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1136
WALX4A | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1136
WALX4B | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1137
WALX4B | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1137
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 278
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 278
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 264
WASF2A | WASF1A | 0.197 | 7.9698 | -0.2553 | 207
WASF2B | WASF1B | 0.197 | 7.9698 | -0.2553 | 207
WATS21 | WATS11 | 0.1382 | 8.1742 | -0.1786 | 279
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 127
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 126
WATS22 | WATS11 | 0.1392 | 8.4361 | -0.781 | 266
WATS22 | WATS11 | 0.1923 | 8.081 | -1.4418 | 189
WBOL21 | WBOL61 | 0.1809 | 10.9763 | -0.023 | 180
WBOL21 | WBOL61 | 0.4736 | 16.5344 | -0.54 | 134
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 127
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 127
WBUR41 | WBUR11 | 0.1056 | 8.2208 | -0.6711 | 274
WBUR42 | WBUR11 | 0.1175 | 8.6648 | -0.4173 | 263
WBUR42 | WBUR12 | 0.1175 | 8.6648 | -0.4173 | 265
WHAM41 | WHAM11 | 0.1057 | 7.9352 | -0.339 | 264
WHAM41 | WHAM11 | 0.103 | 7.9231 | -0.0638 | 263
WHAM41 | WHAM12 | 0.103 | 7.9231 | -0.0638 | 271
WHAM41 | WHAM12 | 0.1057 | 7.9352 | -0.339 | 263
WHAM41 | WHAM4A | 0.001 | 0.35 | 0 | 2000
WHAM41 | WHAM4B | 0.001 | 0.35 | 0 | 2000
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHSO21 | WHSO2A | 0.005 | 0.463 | 0 | 750
WHSO21 | WHSO31 | 0.4435 | 14.3532 | -0.577 | 100
WHSO21 | WHSO31 | 0.4435 | 14.3532 | -0.577 | 100
WHSO21 | WHSO32 | 0.4435 | 14.3131 | -0.577 | 100
WHSO22 | WHSO2B | 0.005 | 0.463 | 0 | 750
WHSO22 | WHSO32 | 0.4435 | 14.3532 | -0.577 | 100
WHSO41 | WHSO22 | 0.0185 | 1.614 | -0.5638 | 886
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 114
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 114
WIEN2A | WIEN11 | 0.1 | 8.1202 | -0.2373 | 240
WIEN2B | WIEN11 | 0.1366 | 8.0648 | -0.0471 | 279
WILE41 | WILL11 | 0.1046 | 7.8493 | -0.0881 | 271
WILE41 | WILL11 | 0.1303 | 7.8698 | -0.4285 | 269
WILE41 | WILL11 | 0.1056 | 8.2208 | -0.6711 | 686
WILE41 | WILL12 | 0.1035 | 8.3458 | -0.0962 | 278
WILT2A | GRST61 | 0.3151 | 12.4456 | -0.1391 | 207
WILT2B | GRST61 | 0.3151 | 12.4456 | -0.1391 | 207
WILT2C | GRST61 | 0.2275 | 10.8456 | -0.0697 | 198
WILT2D | GRST61 | 0.2972 | 12.4333 | -0.1533 | 206
WIMB21 | WIMB12 | 0.167 | 7.9774 | -0.2092 | 255
WIMB41 | WIMB11 | 0.1354 | 7.753 | -0.4285 | 240
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB11 | 0.1366 | 7.753 | -0.4285 | 240
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB21 | 0.014 | 2.6567 | -0.1528 | 950
WIMB41 | WIMB21 | 0.014 | 2.6567 | -0.1528 | 950
WISD21 | WISD11 | 0.1845 | 7.8956 | -0.1938 | 240
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 257
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 240
WISD21 | WISD11 | 0.0723 | 8.433 | -0.2375 | 240
WISD21 | WISD2A | 0.002 | 0.6673 | 0 | 750
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 200
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 201
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 200
WISD41 | WISD21 | 0.0152 | 1.6463 | -0.1118 | 949
WISD42 | WISD21 | 0.0152 | 1.6463 | -0.1118 | 949
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 130
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 130
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 129
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 129
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 199
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 199
WMEL21 | WMEL12 | 0.1923 | 8.2361 | -0.4425 | 197
WTHU4A | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WTHU4B | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WWEY21 | WWEY11 | 0.2188 | 8.097 | -1.9861 | 280
WWEY21 | WWEY12 | 0.1382 | 8.4614 | -0.1786 | 250
WWEY22 | WWEY11 | 0.1007 | 8.1333 | -0.2371 | 240
WWEY22 | WWEY12 | 0.1382 | 8.4489 | -0.1786 | 240
WWEY4A | WWEY21 | 0.017 | 1.6132 | -5.1203 | 750
WWEY4A | WWEY22 | 0.0185 | 1.614 | -0.5638 | 886
WWEY4B | WWEY21 | 0.0178 | 1.5995 | -1.2431 | 845
WWEY4B | WWEY2A | 0.0178 | 1.5995 | -1.2431 | 845
WYLF41 | WYLF11 | 0.1509 | 8.2849 | -0.3279 | 276
WYLF41 | WYLF11 | 0.1229 | 8.3873 | -0.1147 | 269
WYMO41 | WYMO11 | 0.1509 | 8.2849 | -0.3279 | 273
WYMO41 | WYMO11 | 0.1303 | 7.8698 | -0.4285 | 273

## B-3-1d
B.3.1d- OFTO Transformers for 2024/25
OFTO | Site | Node 1 | Node 2 | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA) | Voltage Ratio (kV)
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSW11 | BOSW31 | 0.316 | 15.0833 | 0 | 120 | 132/33
TC Beatrice OFTO Limited | Beatrice Offshore Wind Farm | BEAT41 | BEAT21 | 0.054 | 5.009 | 0 | 320 | 400/220
|  | BEAT41 | BEAT22 | 0.054 | 5.009 | 0 | 320 | 400/220
|  | BEIW21 | BEIW31 | 0.076 | 5.65 | 0 | 310 | 220/33
|  | BEIW22 | BEIW32 | 0.076 | 5.65 | 0 | 310 | 220/33
Diamond Transmission Partners BBE Limited | Burbo Bank Extension Wind Farm | BBWO41 | BBWO21 | 0.0141 | 11.9334 | -0.3558 | 200 | 400/220
|  | BBWO41 | BBWO21 | 0.0141 | 11.9334 | -0.3558 | 200 | 400/220
|  | BBWW21 | BBWW31 | 0.11508 | 6.0889 | -0.8147 | 200 | 220/34
|  | BBWW21 | BBWW32 | 0.11573 | 6.0739 | -0.8147 | 200 | 220/34
DOGGERBANK OFFSHORE WIND FARM PROJECT 1 PROJCO LIMITED | Dogger Bank B Offshore Wind Farm | DBBO41 | DBBODC | 0.07 | 3.52 | 0 | 426 | 400/379
|  | DBBWDC | DBBW61 | 0.001 | 5.72 | 0 | 664 | 392/66
| Dogger Bank A Offshore Wind Farm | DBAWD | DBAW61 | 0.001 | 5.72 | 0 | 664 | 392/66
|  | DBAO41 | DBAOD | 0.001 | 3.52 | 0 | 426 | 400/379
TC Dudgeon OFTO plc | Dudgeon Offshore Wind Farm | DUDW11 | DUDW31 | 0.13 | 6 | 0 | 200 | 132/33
|  | DUDW12 | DUDW32 | 0.13 | 6 | 0 | 200 | 132/33
|  | NECT41 | DUDO11 | 0.09 | 6 | -0.2956 | 200 | 400/132
|  | NECT41 | DUDO12 | 0.09 | 6 | -0.2956 | 200 | 400/132
East Anglia One Limited | East Anglia Offshore Wind Farm | BRST41 | BRST21 | 0.0296 | 3.44 | 0 | 400 | 400/220
|  | BRST42 | BRST22 | 0.0296 | 3.44 | 0 | 400 | 400/220
|  | EAAW21 | EAAW61 | 0.1037 | 7.035 | 0 | 200 | 220/66
|  | EAAW21 | EAAW63 | 0.1037 | 7.035 | 0 | 200 | 220/66
|  | EAAW22 | EAAW62 | 0.1037 | 7.035 | 0 | 200 | 220/66
|  | EAAW22 | EAAW64 | 0.1037 | 7.035 | 0 | 200 | 220/66
Diamond Transmission Partners Galloper Limited | Galloper Offshore Wind Farm | GANW11 | GANW31 | 0.378 | 12.122 | 0 | 90 | 132/33
|  | GANW11 | GANW33 | 0.378 | 12.122 | 0 | 90 | 132/33
|  | GANW12 | GANW32 | 0.378 | 12.222 | 0 | 90 | 132/33
|  | GANW12 | GANW34 | 0.378 | 12.222 | 0 | 90 | 132/33
Greater Gabbard OFTO Plc | Greater Gabbard Offshore Wind Farm | GREG14 | GREG3A | 0.411 | 23.33 | 0 | 90 | 132/33
|  | GREG14 | GREG3B | 0.411 | 23.33 | 0 | 90 | 132/33
|  | GREG11 | GREG31 | 0.4 | 23.44 | 0 | 90 | 132/33
|  | GREG11 | GREG32 | 0.4 | 23.44 | 0 | 90 | 132/33
|  | GREG12 | GREG33 | 0.4 | 23.44 | 0 | 90 | 132/33
|  | GREG12 | GREG34 | 0.4 | 23.44 | 0 | 90 | 132/33
|  | GREG13 | GREG35 | 0.4 | 23.44 | 0 | 90 | 132/33
|  | GREG13 | GREG36 | 0.4 | 23.44 | 0 | 90 | 132/33
TC Gunfleet Sands OFTO Limited | Gunfleet Sands Offshore Wind Farm | GUNS11 | GUNS31 | 0.2372 | 8.5717 | 0 | 120 | 132/33
|  | GUNS11 | GUNS32 | 0.2372 | 8.5717 | 0 | 120 | 132/33
Gwynt y Môr OFTO plc | Gwynt Y Mor Offshore Wind Farm | BODE41 | GWYO11 | 0.054688 | 3.5313 | 0 | 320 | 400/132
|  | BODE41 | GWYO12 | 0.054688 | 3.5313 | 0 | 320 | 400/132
|  | GWAW11 | GWAW31 | 0.15625 | 11.3313 | 0 | 160 | 132/33
|  | GWAW12 | GWAW32 | 0.15625 | 11.3625 | 0 | 160 | 132/33
|  | GWBW11 | GWBW31 | 0.15625 | 11.3438 | 0 | 160 | 132/33
|  | GWBW12 | GWBW32 | 0.15625 | 11.375 | 0 | 160 | 132/33
Diamond Transmission Partners Hornsea One Limited | Hornsea One Offshore Wind Farm | HOWA41 | HOWA21 | 0.016279 | 2.6767 | 0 | 430 | 400/220
|  | HOWA41 | HOWA21 | 0.016279 | 2.6744 | 0 | 430 | 400/220
|  | HOWA41 | HOWA21 | 0.016279 | 2.6744 | 0 | 430 | 400/220
|  | HOWW2A | HOWW3A | 0.0875 | 5.9042 | 0 | 240 | 220/34
|  | HOWW2A | HOWW3A | 0.0875 | 5.9042 | 0 | 240 | 220/34
|  | HOWW2B | HOWW3B | 0.0875 | 5.925 | 0 | 240 | 220/34
|  | HOWW2B | HOWW3B | 0.0875 | 5.925 | 0 | 240 | 220/34
|  | HOWW2C | HOWW3C | 0.0875 | 5.9208 | 0 | 240 | 220/34
|  | HOWW2C | HOWW3C | 0.0875 | 5.9042 | 0 | 240 | 220/34
Breesea Limited | Hornsea Two Offshore Wind Farm | HOWB41 | HOWB21 | 0.029474 | 2.4968 | 0 | 475 | 400/220
|  | HOWB41 | HOWB21 | 0.0295 | 2.4968 | 0 | 475 | 400/220
|  | HOWB41 | HOWB21 | 0.029474 | 2.4968 | 0 | 475 | 400/220
|  | HOWW2D | HOWW6D | 0.081481 | 4.9296 | 0 | 270 | 220/66
|  | HOWW2D | HOWW6D | 0.081481 | 4.9296 | 0 | 270 | 220/66
|  | HOWW2D | HOWW6D | 0.081481 | 4.9296 | 0 | 270 | 220/66
|  | HOWW2D | HOWW6D | 0.081481 | 4.9296 | 0 | 270 | 220/66
|  | HOWW2D | HOWW6D | 0.081481 | 4.9296 | 0 | 270 | 220/66
|  | HOWW2D | HOWW6D | 0.081481 | 4.9296 | 0 | 270 | 220/66
Humber Gateway OFTO Limited | Humber Gateway Offshore Wind Farm | HUMO21 | HUMO11 | 0.1875 | 11.4375 | 0 | 160 | 275/132
|  | HUMO22 | HUMO12 | 0.1875 | 11.4375 | 0 | 160 | 275/132
|  | HUMW11 | HUMW31 | 0.23192 | 8.5714 | 0 | 140 | 132/33
|  | HUMW12 | HUMW32 | 0.23192 | 8.5714 | 0 | 140 | 132/33
TC Lincs OFTO Limited | Lincs Offshore Wind Farm | LINO41 | LINO11 | 0.0417 | 4.6665 | 0 | 300 | 400/132
|  | LINO41 | LINO12 | 0.0417 | 4.6665 | 0 | 300 | 400/132
|  | LINS11 | LINS31 | 0.05 | 5.83 | 0 | 240 | 132/33
|  | LINS12 | LINS32 | 0.05 | 5.83 | 0 | 240 | 132/33
Blue Transmission London Array Limited | London Array Offshore Wind Farm | LONO4A | LONO11 | 0.33 | 6.4556 | 0 | 180 | 400/150
|  | LONO4B | LONO12 | 0.33 | 6.4111 | 0 | 180 | 400/150
|  | LONO4A | LONO13 | 0.33 | 6.4611 | 0 | 180 | 400/150
|  | LONO4B | LONO14 | 0.33 | 6.4389 | 0 | 180 | 400/150
|  | LOAW11 | LOAW31 | 0.402 | 6.56 | 0 | 180 | 150/33
|  | LOAW12 | LOAW32 | 0.4045 | 6.57 | 0 | 180 | 150/33
|  | LOYW11 | LOYW31 | 0.407 | 6.58 | 0 | 180 | 150/33
|  | LOYW12 | LOAW34 | 0.4045 | 6.57 | 0 | 180 | 150/33
Moray East Offshore Wind Limited | Moray East Offshore Wind Farm | MOWE21 | MOWE61 | 0.08 | 4.53 | 0 | 315 | 220/66
|  | MOWE22 | MOWE62 | 0.08 | 4.53 | 0 | 315 | 220/66
|  | MOWE23 | MOWE63 | 0.08 | 4.53 | 0 | 315 | 220/66
|  | MORF41 | MORO21 | 0.079 | 5.21 | 0 | 340 | 400/220
|  | MORF42 | MORO22 | 0.079 | 5.21 | 0 | 340 | 400/220
|  | MORF43 | MORO23 | 0.079 | 5.21 | 0 | 340 | 400/220
Ocean Winds Limited | Moray West Offshore Wind Farm | MOWO41 | MOWO21 | 0.16 | 11.63 | 0 | 470 | 400/220
|  | MOWO42 | MOWO22 | 0.16 | 11.63 | 0 | 470 | 400/220
|  | MOWW21 | MOWW61 | 0.25 | 11.99 | 0 | 440 | 220/66
|  | MOWW22 | MOWW62 | 0.25 | 11.99 | 0 | 440 | 220/66
NEART NA GAOITHE OFFSHORE WIND LIMITED | Neart na Gaoithe Offshore Wind Farm | NNGO41 | NNGO21 | 0.11154 | 4.4462 | 0 | 260 | 400/220
|  | NNGO42 | NNGO22 | 0.11154 | 4.4462 | 0 | 260 | 400/220
|  | NNGW21 | NNGW61 | 0.13478 | 5.4217 | 0 | 230 | 220/66
|  | NNGW22 | NNGW62 | 0.13478 | 5.4217 | 0 | 230 | 220/66
TC Ormonde OFTO Limited | Ormonde Offshore Wind Farm | ORMW11 | ORMW31 | 0.464 | 14.421 | 0 | 85 | 132/33
|  | ORMW11 | ORMW32 | 0.465 | 14.479 | 0 | 85 | 132/33
|  | ORMO11 | ORMO31 | 0.348 | 13.465 | 0 | 110 | 132/33
Diamond Transmission Partners RB Limited | Race Bank Offshore Wind Farm | RACO41 | RACO21 | 0.03165 | 3.1526 | 0 | 360 | 400/220
|  | RACO42 | RACO22 | 0.031779 | 3.1582 | 0 | 360 | 400/220
|  | RACW21 | RACW31 | 0.11449 | 6.0389 | 0 | 200 | 220/34
|  | RACW21 | RACW32 | 0.11465 | 6.0789 | 0 | 200 | 220/34
|  | RACW22 | RACW33 | 0.11476 | 6.0989 | 0 | 200 | 220/34
|  | RACW22 | RACW34 | 0.11435 | 6.0689 | 0 | 200 | 220/34
TC Rampion OFTO Limited | Rampion Offshore Wind Farm | RAMW11 | RAMW3A | 0.14 | 5.31 | 0 | 240 | 150/33
|  | RAMW12 | RAMW3B | 0.14 | 5.32 | 0 | 240 | 150/33
|  | TWNE41 | TWNE11 | 0.073 | 5.1 | 0 | 240 | 400/150
|  | TWNE42 | TWNE12 | 0.073 | 5.1 | 0 | 240 | 400/150
TC Robin Rigg OFTO Limited | Robin Rigg East Offshore Wind Farm | RORE11 | RORE31 | 0.87 | 41.4 | 0 | 20 | 132/33
| Robin Rigg West Offshore Wind Farm | RORW11 | RORW31 | 0.87 | 41.4 | 0 | 20 | 132/33
Sofia Offshore Wind Farm Limited | Sofia Offshore Wind Farm | LAZE41 | SOFW4A | 0.0256 | 1.272 | 0 | 1350 | 400/360
Seagreen Wind Energy Limited | Seagreen One Wind Farm | SGRX21 | SGRO21 | 0.03 | 2.97 | 0 | 410 | 275/220
|  | SGRX22 | SGRO22 | 0.03 | 2.94 | 0 | 410 | 275/220
|  | SGRX23 | SGRO23 | 0.03 | 2.94 | 0 | 410 | 275/220
|  | SGRW21 | SGRW61 | 0.052 | 3.71 | 0 | 390 | 220/66
|  | SGRW22 | SGRW62 | 0.052 | 3.71 | 0 | 390 | 220/66
|  | SGRW22 | SGRW62 | 0.052 | 3.71 | 0 | 390 | 220/66
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SSAW11 | SSAW31 | 0.23 | 12.07 | 0 | 90 | 132/33
|  | SSAW11 | SSAW32 | 0.23 | 12.07 | 0 | 90 | 132/33
|  | SSBW11 | SSBW31 | 0.23 | 12.07 | 0 | 90 | 132/33
|  | SSBW11 | SSBW32 | 0.23 | 12.07 | 0 | 90 | 132/33
Thanet OFTO Limited | Thanet Offshore Wind Farm | THOW11 | THOW31 | 0.0093 | 1.1111 | -0.0063 | 90 | 132/33
|  | THOW11 | THOW33 | 0.0093 | 1.1111 | -0.0063 | 90 | 132/33
|  | THOW12 | THOW32 | 0.0093 | 1.1111 | -0.0063 | 90 | 132/33
|  | THOW12 | THOW34 | 0.0093 | 1.1111 | -0.0063 | 90 | 132/33
Triton Knoll Wind Farm Limited | Triton Knoll Offshore Wind Farm | TKNW21 | TKNW61 | 0.07 | 3.33 | 0 | 420 | 220/66
|  | TKNE21 | TKNE61 | 0.07 | 3.33 | 0 | 420 | 220/66
|  | TKNO41 | TKNO21 | 0.036 | 3.78 | 0 | 450 | 400/220
|  | TKNO42 | TKNO22 | 0.036 | 3.78 | 0 | 450 | 400/220
Diamond Transmission Partners Walney Extension Limited | Walney Extension Offshore Wind Farm | WACW21 | WACW31 | 0.115 | 6.02 | -0.9268 | 200 | 220/34
|  | WACW21 | WACW32 | 0.115 | 6.02 | -0.9268 | 200 | 220/34
|  | WADW21 | WADW31 | 0.115 | 6.02 | 0 | 200 | 220/34
|  | WADW21 | WADW32 | 0.115 | 6.02 | 0 | 200 | 220/34
|  | WOWE41 | WOWE21 | 0.0255 | 2.617 | 0 | 470 | 400/220
|  | WOWE42 | WOWE22 | 0.0255 | 2.617 | 0 | 470 | 400/220
Blue Transmission Walney 1 OFTO Limited | Walney 1 Offshore Wind Farm | WAAW11 | WAAW31 | 0.42 | 8.75 | 0 | 120 | 132/33
|  | WAAW11 | WAAW32 | 0.42 | 8.75 | 0 | 120 | 132/33
Blue Transmission Walney 2 OFTO Limited | Walney 2 Offshore Wind Farm | WABW11 | WABW31 | 0.2395 | 8.2882 | 0 | 120 | 132/33
|  | WABW11 | WABW32 | 0.2432 | 8.3214 | 0 | 120 | 132/33
WoDS Transmission plc | West of Duddon Sands Offshore Wind Farm | WDSO41 | WDSO11 | 0.20833 | 5 | 0 | 240 | 400/155
|  | WDSO42 | WDSO12 | 0.20833 | 5 | 0 | 240 | 400/155
|  | WDSW11 | WDSW31 | 0.20833 | 5 | 0 | 240 | 155/34
|  | WDSW12 | WDSW32 | 0.20833 | 5 | 0 | 240 | 155/34
TC Westermost Rough OFTO Limited | Westermost Rough Offshore Wind Farm | WERO21 | WERO11 | 0.09 | 6.62 | 0 | 180 | 275/150
|  | WERO22 | WERO11 | 0.09 | 6.58 | 0 | 180 | 275/150
|  | WERW11 | WERW31 | 0.12 | 7.14 | 0 | 140 | 150/34
|  | WERW11 | WERW32 | 0.12 | 7.14 | 0 | 140 | 150/34

## B-3-2a
B-3-2a - SHE TransmissionTransformer Changes 2025/26 to 2035/36
Node1 | Node2 | Year | Status | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA)
CONN1J | CONN2K | 2025 | Addition | 0.143 | 5.3036 | -0.0006 | 360
CONN1J | CONN2J | 2025 | Removed | 0.143 | 5.3036 | -0.0006 | 360
CONN1K | CONN2J | 2025 | Addition | 0.143 | 5.3036 | -0.0006 | 360
ERRO1J | ERRO3- | 2025 | Addition | 0.5 | 25 | 0 | 90
ERRO1K | ERRO3- | 2025 | Addition | 0.5 | 25 | 0 | 90
GREM1J | GREM3- | 2025 | Addition | 0.5828 | 24.9932 | 0 | 90
GREM1K | GREM3- | 2025 | Addition | 0.5828 | 24.9932 | 0 | 90
TUMB1Q | TUMB5- | 2025 | Removed | 1.63 | 77.76 | 0 | 21
TUMB1R | TUMB5- | 2025 | Removed | 1.63 | 77.76 | 0 | 21
ACHE1- | ACHE3- | 2027 | Addition | 0.36 | 18 | 0 | 120
AIGA1Q | AIGA5- | 2027 | Removed | 1.76 | 44.89 | 0 | 22
AIGN1- | AIGN5- | 2027 | Addition | 1.76 | 44.89 | 0 | 36
ALYT2A | ALYT4J | 2027 | Addition | 0.0252 | 1.1997 | -0.0005 | 1200
ALYT2B | ALYT4K | 2027 | Addition | 0.0253 | 1.2081 | -0.0005 | 1200
BEAU1J | BEAU2J | 2027 | Change | 0.1486 | 5.3035 | -0.0006 | 360
BLBS3- | BLBS4- | 2027 | Addition | 0.09 | 4.475 | 0 | 400
BLEX1- | BLEX3- | 2027 | Addition | 0.36 | 18 | 0 | 120
BLHI1J | BLHI2J | 2027 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
CAID2- | CAID3- | 2027 | Addition | 0.36 | 18 | 0 | 120
CLGO1- | CLGO2- | 2027 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
CLGO1- | CLGO2A | 2027 | Addition | 0.1486 | 5.3035 | -0.0006 | 360
CULL1A | CULL5- | 2027 | Addition | 1.733 | 37.56 | 0 | 36
CULL1Q | CULL5- | 2027 | Removed | 1.46 | 37.6 | 0 | 25
DEAN1Q | DEAN5- | 2027 | Removed | 1.01 | 25.1 | 0 | 40
DEAW1- | DEAW5- | 2027 | Addition | 1.14 | 25.05 | 0 | 45
DOUN1- | DOUN3- | 2027 | Change | 0.5 | 25 | 0 | 120
DOUN1- | DOUN3- | 2027 | Change | 0.5 | 25 | 0 | 120
DUDH1Q | DUDH3- | 2027 | Removed | 0.78 | 24.93 | 0 | 60
DUDH1R | DUDH3- | 2027 | Removed | 0.78 | 23.93 | 0 | 60
ELCH1- | ELCH3- | 2027 | Addition | 0.75 | 15 | 0 | 120
FARI1J | FARI2J | 2027 | Change | 0.2184 | 8.2304 | -0.0007 | 240
FARI1K | FARI2K | 2027 | Change | 0.2184 | 8.2304 | -0.0007 | 240
FETT1- | FETT2R | 2027 | Removed | 0.217 | 4.2737 | -0.0006 | 240
FETT1- | FETT4J | 2027 | Addition | 0.108 | 3.9569 | -0.0007 | 480
KINT1- | KINT2K | 2027 | Change | 0.3751 | 10.2314 | -0.015 | 240
KINT1- | KINT3- | 2027 | Removed | 1.04 | 27.65 | 0 | 60
KINT1- | KINT3- | 2027 | Change | 0.5 | 25 | 0 | 120
KION1- | KION5- | 2027 | Addition | 1.78 | 45.42 | 0 | 36
KIOR1Q | KIOR5- | 2027 | Removed | 1.78 | 45.42 | 0 | 22
LAIS1B | LAIS3- | 2027 | Addition | 0.36 | 18 | 0 | 60
LUNA1Q | LUNA3- | 2027 | Change | 0.5 | 25 | 0 | 120
LUNA1R | LUNA3- | 2027 | Change | 0.5 | 25 | -0.0222 | 120
SFIL1Q | SFIL5- | 2027 | Change | 1.99 | 39.48 | 0 | 45
STNG1E | STNG3- | 2027 | Addition | 0.2151 | 25.124 | -0.009 | 120
STNG1E | STNG3- | 2027 | Addition | 0.2151 | 25.124 | -0.009 | 120
STSO1B | STSO3A | 2027 | Addition | 0.36 | 18 | 0 | 120
STSO1B | STSO3B | 2027 | Addition | 0.36 | 18 | 0 | 120
STWO1- | STWO3- | 2027 | Addition | 0.36 | 18 | 0 | 90
ANSN2- | ANSN3- | 2029 | Addition | 0.258 | 20.06 | 0 | 120
ANSU1- | ANSU3- | 2029 | Removed | 0.817 | 27.121 | 0 | 45
ARBR1Q | ARBR3- | 2029 | Change | 0.5 | 25 | 0 | 120
ARBR1R | ARBR3- | 2029 | Change | 0.5 | 25 | 0 | 120
ASBS1- | ASBS4B | 2029 | Addition | 0.08 | 4 | 0 | 480
ASBS1- | ASBS4B | 2029 | Addition | 0.08 | 4 | 0 | 480
BANN4J | SPIT2J | 2029 | Addition | 0.026 | 1.533 | -0.0005 | 1200
BANN4K | SPIT2K | 2029 | Addition | 0.026 | 1.533 | -0.0005 | 1200
BEWF1- | BEWF3- | 2029 | Addition | 0.36 | 17.9968 | 0 | 90
BING4- | FASN1A | 2029 | Addition | 0.106 | 3.957 | -0.0007 | 480
BING4- | FASN1B | 2029 | Addition | 0.106 | 3.957 | -0.0007 | 480
BLHI2A | BLHI2J | 2029 | Addition | 0.005 | 0.4 | 0 | 865
BLHI2B | BLHI2K | 2029 | Addition | 0.005 | 0.4 | 0 | 865
BRCW1A | BRCW3- | 2029 | Addition | 0.4181 | 24.9965 | 0 | 120
BRCW1A | CMBS4A | 2029 | Addition | 0.106 | 3.957 | -0.0007 | 480
BRCW1B | BRCW3- | 2029 | Addition | 0.4181 | 24.9965 | 0 | 120
BRCW1B | CMBS4B | 2029 | Addition | 0.106 | 3.957 | -0.0007 | 480
BRCW2J | BRCW3- | 2029 | Removed | 0.42 | 20 | 0 | 120
BRCW2K | BRCW3- | 2029 | Removed | 0.42 | 20 | 0 | 120
BROA1- | BROA3- | 2029 | Addition | 1.19 | 39 | 0 | 30
BROA1- | BROA3- | 2029 | Addition | 0.5 | 25 | 0 | 45
BROA1Q | BROA3- | 2029 | Removed | 1.19 | 39 | 0 | 30
CLOI1- | CLOI3- | 2029 | Addition | 0.36 | 18 | 0 | 120
COST1- | COST3- | 2029 | Addition | 0.54 | 18 | 0 | 45
CRAR1R | CRAR3- | 2029 | Removed | 0.36 | 18 | 0 | 90
CRAS2- | CRAS3- | 2029 | Addition | 0.258 | 20.06 | 0 | 120
CRDH1J | CRDH2J | 2029 | Addition | 0.098 | 3.936 | -0.0006 | 480
CRDH1K | CRDH2K | 2029 | Addition | 0.098 | 3.936 | -0.0006 | 480
CRMU2J | CRMU3- | 2029 | Addition | 0.42 | 20 | 0 | 120
CRMU2K | CRMU3- | 2029 | Addition | 0.42 | 20 | 0 | 120
CRSN1Q | CRSN2Q | 2029 | Addition | 0.098 | 3.936 | -0.0006 | 480
CRSN1R | CRSN2R | 2029 | Addition | 0.098 | 3.936 | -0.0006 | 480
CRSS1J | CRSS1Q | 2029 | Removed | 0.0582 | 2.145 | 0 | 240
CRSS1J | CRSS1X | 2029 | Addition | 0.0582 | 2.145 | 0 | 240
CRSS1J | CRSS2A | 2029 | Removed | 0.2466 | 9.0008 | -0.0005 | 240
CRSS1K | CRSS1R | 2029 | Removed | 0.0582 | 2.1492 | 0 | 240
CRSS1K | CRSS1Y | 2029 | Addition | 0.0582 | 2.1492 | 0 | 240
CRSS1K | CRSS2B | 2029 | Removed | 0.2459 | 9.0175 | -0.0005 | 240
CRSS1X | CRSS2A | 2029 | Addition | 0.2466 | 9.0008 | -0.0005 | 240
CRSS1Y | CRSS2B | 2029 | Addition | 0.2459 | 9.0175 | -0.0005 | 240
DOUN2- | DOUN2A | 2029 | Addition | 0.066 | 5.333 | 0 | 360
DUNO1Q | DUNO3- | 2029 | Change | 0.5 | 25 | 0 | 120
DUNO1R | DUNO3- | 2029 | Change | 0.5 | 25 | 0 | 120
EARR2B | EARR3- | 2029 | Addition | 0.258 | 20.06 | 0 | 120
EDIN1- | EDIN3- | 2029 | Removed | 0.558 | 16.991 | 0 | 60
EDIN1J | EDIN3- | 2029 | Addition | 0.558 | 16.991 | 0 | 60
EDIN1J | EDIN3- | 2032 | Change | 0.36 | 18 | 0 | 120
EDIN1J | EDIN8B | 2029 | Addition | 0.16 | 8 | 0 | 125
EDIN1K | EDIN3A | 2029 | Addition | 0.2578 | 24.757 | 0 | 120
EDIN1K | EDIN8A | 2029 | Addition | 0.16 | 8 | 0 | 125
ERED2- | ERED3- | 2029 | Addition | 0.258 | 20.06 | 0 | 120
FASN1A | FASN3- | 2029 | Addition | 0.4181 | 24.9965 | 0 | 120
FASN1B | FASN3- | 2029 | Addition | 0.4181 | 24.9965 | 0 | 120
FASN2- | FASN3- | 2029 | Removed | 0.42 | 20 | 0 | 120
FASN2- | FASN3- | 2029 | Removed | 0.42 | 20 | 0 | 120
FASQ1J | FASQ3- | 2029 | Addition | 0.75 | 15 | 0 | 120
FAUG1- | FAUG2J | 2029 | Removed | 0.2606 | 7.7039 | -0.0005 | 240
FAUG1- | FAUG2K | 2029 | Removed | 0.2629 | 7.7038 | -0.0005 | 240
FAUG1- | FAUG4J | 2029 | Addition | 0.2149 | 8.0138 | -0.013 | 240
FAUG1- | FAUG4J | 2029 | Addition | 0.3185 | 8.4523 | -0.013 | 240
FETT1- | FETT4K | 2029 | Addition | 0.108 | 3.9569 | -0.0007 | 480
FINS1- | FINS2A | 2029 | Addition | 0.044 | 5.833 | 0 | 360
FINS1- | FINS3- | 2029 | Addition | 0.451 | 25 | 0 | 120
FINS1- | FINS3- | 2029 | Addition | 0.451 | 25 | 0 | 120
FINS1- | HEST3- | 2029 | Addition | 0.54 | 18 | 0 | 45
GLNU1- | GLNU3- | 2029 | Addition | 0.36 | 18 | 0 | 60
GREM1N | MSHL3- | 2029 | Addition | 0.5828 | 24.9932 | 0 | 90
KINA4A | TUMM1J | 2029 | Addition | 0.2149 | 8.0138 | -0.013 | 240
KINA4B | TUMM1K | 2029 | Addition | 0.2149 | 8.0138 | -0.013 | 240
KRKN1- | KRKN3- | 2029 | Addition | 0.36 | 18 | 0 | 90
LOCL1J | LOCL4K | 2029 | Addition | 0.108 | 3.957 | -0.0007 | 480
LOCL1K | LOCL4J | 2029 | Addition | 0.106 | 3.957 | -0.0007 | 480
PORA1T | PORA3- | 2029 | Removed | 1.803 | 29.812 | 0 | 30
PORA1U | PORA3- | 2029 | Removed | 1.803 | 29.812 | 0 | 30
SLOY1L | SLOY5L | 2029 | Change | 0.8557 | 25 | 0 | 60
SLOY1M | SLOY5M | 2029 | Change | 0.862 | 25 | 0 | 60
SLOY1N | SLOY5N | 2029 | Change | 0.859 | 25 | 0 | 60
SLOY1P | SLOY5P | 2029 | Change | 0.862 | 25 | 0 | 60
TNGF1A | TNGF3- | 2029 | Addition | 0.36 | 18 | 0 | 120
TUMM1J | TUMM2J | 2029 | Removed | 0.259 | 7.7457 | -0.0005 | 240
TUMM1K | TUMM2K | 2029 | Removed | 0.2595 | 7.829 | -0.0005 | 240
ALYT2A | ALYT4J | 2032 | Removed | 0.0252 | 1.1997 | -0.0005 | 1200
ALYT2B | ALYT4K | 2032 | Removed | 0.0253 | 1.2081 | -0.0005 | 1200
CAAI4J | LOCB1J | 2032 | Addition | 0.108 | 3.9569 | -0.0007 | 480
CAAI4J | LOCB1J | 2032 | Addition | 0.108 | 3.9569 | -0.0007 | 480
CAAI4K | LOCB1K | 2032 | Addition | 0.108 | 3.9569 | -0.0007 | 480
EMMO4J | TEAL2K | 2032 | Addition | 0.026 | 1.533 | 0 | 1200
EMMO4K | TEAL2J | 2032 | Addition | 0.026 | 1.533 | 0 | 1200
FAUG2T | FAUG4J | 2032 | Addition | 0.026 | 1.533 | -0.0005 | 1200
HOME1- | HOME3- | 2032 | Addition | 0.36 | 18 | 0 | 60
INVB2A | INVR1- | 2032 | Removed | 0.2217 | 4.3026 | -0.0071 | 240
INVB2A | INVR1M | 2032 | Addition | 0.2217 | 4.3026 | -0.0071 | 240
INVB2B | INVR1- | 2032 | Removed | 0.2164 | 4.257 | -0.0066 | 240
INVB2B | INVR1L | 2032 | Addition | 0.2164 | 4.257 | -0.0066 | 240
INVR1- | INVR1L | 2032 | Addition | 0.0582 | 2.1492 | 0 | 240
INVR1- | INVR1M | 2032 | Addition | 0.0582 | 2.1492 | 0 | 240
LEWI1J | LEWI4J | 2032 | Addition | 0.1119 | 9.3882 | -0.19 | 360
LEWI1J | LEWI4K | 2032 | Addition | 0.1119 | 9.3882 | -0.19 | 360
LEWI1K | LEWI4K | 2032 | Addition | 0.1119 | 9.3882 | -0.19 | 360
LOSD1A | LOSD4A | 2032 | Addition | 0.108 | 3.9569 | -0.0007 | 480
LOSD1B | LOSD4B | 2032 | Addition | 0.108 | 3.9569 | -0.0007 | 480
MUAI1A | MUAI3A | 2032 | Addition | 0.36 | 18 | 0 | 120
MUAI1A | MUAI3B | 2032 | Addition | 0.36 | 18 | 0 | 120
STOR1- | STOR3- | 2032 | Addition | 0.2578 | 24.757 | 0 | 120
STOR1- | STOR3- | 2032 | Addition | 0.2578 | 24.757 | 0 | 120
CAIN2- | CAIN3J | 2035 | Removed | 0.36 | 18 | 0 | 120
CAIN3J | CAIN4- | 2035 | Addition | 0.556 | 25 | 0 | 120
DOUN2- | DOUN4A | 2035 | Addition | 0.026 | 1.533 | -0.0005 | 1200
DOUN2- | DOUN4B | 2035 | Addition | 0.026 | 1.533 | -0.0005 | 1200
NASS2Q | NASS4Q | 2035 | Addition | 0.026 | 1.533 | -0.0005 | 1200
NASS2R | NASS4R | 2035 | Addition | 0.026 | 1.533 | -0.0005 | 1200
NASS4M | NASS4R | 2035 | Addition | 0.001 | 0.21 | 0 | 3336
NASS4N | NASS4Q | 2035 | Addition | 0.001 | 0.21 | 0 | 3336
PEHE2Z | PEHE4K | 2035 | Addition | 0.026 | 1.533 | -0.0005 | 1200
THUS2J | THUS4A | 2035 | Addition | 0.026 | 1.533 | -0.0005 | 1200
THUS2K | THUS4B | 2035 | Addition | 0.026 | 1.533 | -0.0005 | 1200

## B-3-2b
B-3-2b - SPT Transformer Changes 2025/26 to 2035/36
Node1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
AREX1- | AREX3- | 2025 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
BENB1- | BENB3- | 2025 | Addition | 0.1922 | 14.207 | -0.0113 | 120
CLAU1- | CLAU3- | 2025 | Addition | 0.1922 | 14.207 | -0.0113 | 120
CUMW1- | CUMW3- | 2025 | Addition | 0.1922 | 14.207 | -0.0113 | 120
DENN4- | DENN2- | 2025 | Addition | 0.0164 | 1.6449 | -0.1161 | 1000
GIFF2Q | GIFF3A | 2025 | Change | 0.4557 | 30.1188 | -0.0331 | 90
HUER4- | HUER1- | 2025 | Removed | 0.1122 | 9.3465 | -0.2007 | 360
HUER4- | HUER1- | 2025 | Removed | 0.1134 | 9.4715 | -0.1992 | 360
HUNE4- | HUNE1- | 2025 | Addition | 0.1122 | 9.3465 | -0.2007 | 360
HUNE4- | HUNE1- | 2025 | Addition | 0.1134 | 9.4715 | -0.1992 | 360
MAHI2- | MAHI1C | 2025 | Addition | 0.1284 | 8.6824 | -0.2535 | 240
MOFF1- | MOFF3- | 2025 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
MOFF4- | MOFF1A | 2025 | Addition | 0.0914 | 6.4382 | -0.0751 | 360
NECU2- | NECU1B | 2025 | Addition | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1B | 2025 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
NECU2- | NECU1B | 2025 | Addition | 0.1164 | 8.5534 | -0.0287 | 240
NECU2- | NECU1C | 2025 | Addition | 0.1111 | 6.6657 | -0.0006 | 360
NECU2- | NECU1C | 2025 | Addition | 0.1111 | 6.6657 | -0.0006 | 360
NECU2- | NECU1Q | 2025 | Removed | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1R | 2025 | Removed | 0.1164 | 8.5534 | -0.0287 | 240
NETS1- | NETS3- | 2025 | Addition | 0.8311 | 28.2878 | -0.0097 | 60
OHLL1- | OHLL3- | 2025 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
PORD2R | PORD3- | 2025 | Change | 0.4557 | 30.1188 | -0.0331 | 90
STOC1- | STOC3- | 2025 | Addition | 0.1922 | 14.207 | -0.0113 | 120
WGEO2R | WGEO3- | 2025 | Change | 0.4557 | 30.1188 | -0.0331 | 90
ARCR2- | ARCR3A | 2027 | Addition | 0.1883 | 12.5319 | -0.0338 | 120
ARCR2- | ARCR3B | 2027 | Addition | 0.1883 | 12.5319 | -0.0338 | 120
COBA4- | COBA3- | 2027 | Addition | 0.2383 | 11.6642 | -0.0232 | 120
DEBS2- | DEBS3A | 2027 | Addition | 0.1883 | 12.5319 | -0.0338 | 120
DEBS2- | DEBS3B | 2027 | Addition | 0.1883 | 12.5319 | -0.0338 | 120
DEBS2- | DEBS3C | 2027 | Addition | 0.1883 | 12.5319 | -0.0338 | 120
DEBS2- | DEBS3D | 2027 | Addition | 0.1883 | 12.5319 | -0.0338 | 120
DEBS2- | DEBS3E | 2027 | Addition | 0.1883 | 12.5319 | -0.0338 | 120
FELL1- | FELL3- | 2027 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
GALA1- | GALA0J | 2027 | Addition | 0.917 | 55.0024 | 0 | 10
GALA1- | GALA0K | 2027 | Addition | 0.917 | 55.0024 | 0 | 10
GHPS1- | GHPS3A | 2027 | Addition | 0.1922 | 14.207 | -0.0113 | 120
GHPS1- | GHPS3B | 2027 | Addition | 0.1922 | 14.207 | -0.0113 | 120
GIFF2R | GIFF3B | 2027 | Change | 0.4557 | 30.1188 | -0.0331 | 120
GNSH1- | GNSH3- | 2027 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
HORI1- | HORI3A | 2027 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
HORI1- | HORI3B | 2027 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
KINN4- | KINN2A | 2027 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
KINN4- | KINN2B | 2027 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
LETH1- | LETH3- | 2027 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
LETH1- | LETH3- | 2027 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
LORG1- | LORG3- | 2027 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
OFOA1- | OFOA3- | 2027 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
REDS1A | REDS3A | 2027 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
REDS4- | REDS1A | 2027 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
REDS4- | REDS1A | 2027 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
TONG1- | TONG1R | 2027 | Removed | 0.0267 | 1.3331 | 0 | 90
TONG1Q | TONG1R | 2027 | Removed | 0.0125 | 2.5 | 0 | 90
TRSN1- | TRSN3- | 2027 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
CLFO1- | CLFO3- | 2029 | Addition | 0.1922 | 14.207 | -0.0113 | 120
CLYM4- | CLYM2- | 2029 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
CLYM4- | CLYM2- | 2029 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
CRCK2- | CRCK3- | 2029 | Addition | 0.2857 | 19.998 | 0 | 90
DAER1- | DAER3- | 2029 | Addition | 0.1922 | 14.207 | -0.0113 | 120
DUNE1- | DUNE3A | 2029 | Addition | 0.1922 | 14.207 | -0.0113 | 120
EUCH1- | EUCH3- | 2029 | Addition | 0.1922 | 14.207 | -0.0113 | 120
FALL4- | FALL3C | 2029 | Addition | 0.2564 | 16.6647 | 0 | 120
GALN4- | GALN1Q | 2029 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
GALN4- | GALN1R | 2029 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
GHPS4- | GHPS1- | 2029 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
GHPS4- | GHPS1- | 2029 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
GHPS4- | GHPS1- | 2029 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
HLND1- | HLND3- | 2029 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
KNOK1- | KNOK3- | 2029 | Addition | 0.1922 | 14.207 | -0.0113 | 120
LEGO1Q | LEGO3- | 2029 | Addition | 0.3119 | 21.8311 | 0 | 60
LEGO1R | LEGO3- | 2029 | Addition | 0.3119 | 21.8311 | 0 | 60
NLEI1- | NLEI3A | 2029 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
NLEI1- | NLEI3B | 2029 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
NOKY1- | NOKY3A | 2029 | Change | 0.2226 | 14.49 | -0.0076 | 120
NOKY1- | NOKY3B | 2029 | Change | 0.2344 | 14.3231 | -0.0107 | 120
QUAN1- | QUAN3- | 2029 | Addition | 0.1922 | 14.207 | -0.0113 | 120
SPRB1- | SPRB3- | 2029 | Addition | 0.1857 | 12.9987 | 0 | 160
WIYH4Q | WIYH2- | 2029 | Addition | 0.0133 | 1.6699 | -0.3581 | 1000
WLER2- | WLER3A | 2029 | Addition | 0.4321 | 27.7744 | -0.0372 | 180
WLER2- | WLER3C | 2029 | Addition | 0.4321 | 27.7744 | -0.0372 | 180
WLER2- | WLER3E | 2029 | Addition | 0.4321 | 27.7744 | -0.0372 | 180
ARFO1- | ARFO3- | 2033 | Addition | 0.2651 | 15.8311 | -0.0173 | 90
ARRS1- | ARRS3A | 2033 | Addition | 0.1922 | 14.207 | -0.0113 | 120
ARRS1- | ARRS3B | 2033 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
AUBU1- | AUBU3- | 2033 | Addition | 0.8334 | 10.0003 | 0 | 120
BONN1- | BONN2A | 2033 | Removed | 0.1559 | 8.9445 | -0.1694 | 240
BONN1- | BONN2B | 2033 | Removed | 0.1559 | 8.9445 | -0.1694 | 240
BONN4- | BONN1- | 2033 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
BONN4- | BONN1- | 2033 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
CONL4- | CONL2Q | 2033 | Addition | 0.125 | 6.8739 | -0.0373 | 240
CONL4- | CONL2R | 2033 | Addition | 0.125 | 6.8739 | -0.0373 | 240
CUMB1Q | CUMB3- | 2033 | Removed | 0.7407 | 29.324 | -0.129 | 90
CUMB1R | CUMB3- | 2033 | Removed | 0.741 | 27.111 | 0 | 90
CUMB2- | CUMB3- | 2033 | Addition | 0.2857 | 19.998 | 0 | 90
CUMB2- | CUMB3- | 2033 | Addition | 0.2857 | 19.998 | 0 | 90
HAZE1- | HAZE3A | 2033 | Addition | 0.1667 | 13.3334 | 0 | 90
HAZE1- | HAZE3B | 2033 | Addition | 0.1667 | 13.3334 | 0 | 90
KILT2Q | KILT3A | 2033 | Change | 0.493 | 28.5457 | -0.0524 | 120
KILT2R | KILT3A | 2033 | Change | 0.508 | 28.7455 | -0.0524 | 120
MOSM1A | MOSM2- | 2033 | Removed | 0.151 | 8.332 | -0.1299 | 240
MOSM1B | MOSM2- | 2033 | Removed | 0.157 | 8.7486 | -0.1299 | 240
MOSM4- | MOSM1A | 2033 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
MOSM4- | MOSM1B | 2033 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
NECU1B | NECU2- | 2033 | Change | 0.1042 | 8.7827 | -0.0556 | 240
ORLA1- | ORLA3A | 2033 | Addition | 0.11 | 4.2501 | 0 | 200
ORLA1- | ORLA3B | 2033 | Addition | 0.1375 | 5.3126 | 0 | 160
SMEA4R | SMEA2- | 2033 | Change | 0.0115 | 1.2692 | -0.312 | 1000
WFIE1A | WFIE2- | 2033 | Removed | 0.1408 | 8.6113 | -0.1827 | 240
WFIE1B | WFIE2- | 2033 | Removed | 0.1264 | 8.7366 | -0.1602 | 240
WFIE4- | WFIE1A | 2033 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
WFIE4- | WFIE1B | 2033 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
COYL4- | COYL2- | 2035 | Addition | 0.0136 | 1.4999 | -0.2547 | 1100
COYL4- | COYL2- | 2035 | Addition | 0.0136 | 1.4999 | -0.2547 | 1100
CURR4T | CURR2- | 2035 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
NECU4- | NECU2- | 2035 | Addition | 0.0136 | 1.4999 | -0.2547 | 1100
NECU4- | NECU2- | 2035 | Addition | 0.0136 | 1.4999 | -0.2547 | 1100
TEVI4- | TEVI1- | 2035 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
TEVI4- | TEVI1- | 2035 | Addition | 0.1119 | 9.3882 | -0.1905 | 360

## B-3-2c
B-3-2c - NGET Transformer Changes 2025/26 to 2035/36
Node1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
BENR41 | BENR11 | 2025 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
BENR41 | BENR11 | 2025 | Addition | 0.1303 | 7.8698 | -0.4285 | 240
HARG41 | HARG11 | 2025 | Addition | 0.148 | 7.4973 | -0.3849 | 240
HARG41 | HARG11 | 2025 | Addition | 0.148 | 7.4973 | -0.3849 | 240
HARG41 | HARG11 | 2025 | Addition | 0.148 | 7.4973 | -0.3849 | 240
HARG41 | HARG11 | 2025 | Addition | 0.148 | 7.4973 | -0.3849 | 240
LHOR4A | LHOR11 | 2025 | Addition | 0.1373 | 8.1976 | -0.1719 | 240
LHOR4B | LHOR11 | 2025 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
NEWX41 | NEWX21 | 2025 | Addition | 0.0132 | 1.4627 | -2.0624 | 1100
NEWX41 | NEWX21 | 2025 | Addition | 0.0132 | 1.4627 | -2.0624 | 1100
WIMB21 | WIMB12 | 2025 | Removed | 0.167 | 7.9774 | -0.2092 | 255
ALVE41 | ALVE11 | 2027 | Addition | 0.1118 | 8.3874 | -0.0906 | 278
ALVE41 | ALVE11 | 2027 | Addition | 0.1621 | 8.0984 | -0.0747 | 275
ALVE4A | ALVE11 | 2027 | Removed | 0.1118 | 8.3874 | -0.0906 | 278
ALVE4B | ALVE11 | 2027 | Removed | 0.1621 | 8.0984 | -0.0747 | 275
BRIM2C | BRIM11 | 2027 | Removed | 0.1688 | 8.3316 | -1.1711 | 262
BRIM2D | BRIM11 | 2027 | Removed | 0.1688 | 8.3316 | -1.1711 | 262
BRIM4C | BRIM11 | 2027 | Addition | 0.1264 | 7.974 | -0.1303 | 262
BRIM4D | BRIM11 | 2027 | Addition | 0.1264 | 7.974 | -0.1303 | 262
HACK2A | HACK61 | 2027 | Removed | 0.2793 | 13.3304 | -0.6737 | 191
HACK2B | HACK61 | 2027 | Removed | 0.2793 | 13.3304 | -0.6737 | 191
HACK41 | HACK2A | 2027 | Removed | 0.0182 | 1.5763 | -0.0904 | 1210
HACK41 | HACK2B | 2027 | Removed | 0.0182 | 1.5763 | -0.0904 | 1210
HACK41 | HACK61 | 2027 | Addition | 0.1529 | 12.1324 | -0.0623 | 278
HACK41 | HACK61 | 2027 | Addition | 0.1529 | 12.1324 | -0.0623 | 278
HARG41 | HARG11 | 2027 | Addition | 0.148 | 7.4973 | -0.3849 | 240
HARG41 | HARG11 | 2027 | Addition | 0.148 | 7.4973 | -0.3849 | 240
HARG41 | HARG21 | 2027 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
HARG41 | HARG2A | 2027 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
HARG41 | HARG2A | 2027 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
HARK21 | HARK11 | 2027 | Removed | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK11 | 2027 | Removed | 0.2264 | 12.2479 | -0.6062 | 137
HARK21 | HARK12 | 2027 | Removed | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK12 | 2027 | Removed | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK13 | 2027 | Removed | 0.1147 | 8.673 | -0.0358 | 222
HARK41 | HARK21 | 2027 | Removed | 0.0292 | 2.402 | -0.2732 | 573
HARK41 | HARK21 | 2027 | Removed | 0.0376 | 2.3797 | -3.9009 | 519
HARK41 | HARK21 | 2027 | Removed | 0.0376 | 2.3797 | -3.9009 | 547
HARK41 | HARK21 | 2027 | Removed | 0.0192 | 2.6599 | -0.1528 | 950
MONF42 | MFSN21 | 2027 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
MONF42 | MFSN21 | 2027 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
MONF42 | MFSN21 | 2027 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
MONF42 | MFSN21 | 2027 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
MONF42 | MONF21 | 2027 | Addition | 0.0176 | 1.5828 | -0.1018 | 1000
MONF4A | MONF21 | 2027 | Removed | 0.0176 | 1.5828 | -0.1018 | 1138
OSBA42 | OSBA11 | 2027 | Addition | 0.1373 | 8.1976 | -0.1238 | 278
PELH41 | PELH41 | 2027 | Addition | 0.0071 | 0.2875 | 0 | 2750
PELH41 | PELH41 | 2027 | Addition | 0.0071 | 0.2875 | 0 | 2750
POAB41 | POAB11 | 2027 | Addition | 0.0282 | 4.3546 | -0.2109 | 460
POAB41 | POAB11 | 2027 | Addition | 0.0282 | 4.3546 | -0.2109 | 460
POAB41 | POAB11 | 2027 | Addition | 0.0282 | 4.3546 | -0.2109 | 460
WALX41 | WALX2A | 2027 | Addition | 0.0176 | 1.5828 | -0.1018 | 1136
WALX41 | WALX2A | 2027 | Addition | 0.0176 | 1.5828 | -0.1018 | 1136
WALX4A | WALX21 | 2027 | Removed | 0.0176 | 1.5828 | -0.1018 | 1136
WALX4A | WALX22 | 2027 | Removed | 0.0176 | 1.5828 | -0.1018 | 1136
WALX4B | WALX21 | 2027 | Removed | 0.0176 | 1.5828 | -0.1018 | 1137
WALX4B | WALX22 | 2027 | Removed | 0.0176 | 1.5828 | -0.1018 | 1137
YORK4A | OVER21 | 2027 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
YORK4A | OVER21 | 2027 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
YORK4B | OVER21 | 2027 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
YORK4B | OVER21 | 2027 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
CHTE21 | CHTE11 | 2029 | Removed | 0.1594 | 8.6081 | -0.2215 | 261
CHTE21 | CHTE11 | 2029 | Removed | 0.1545 | 7.6337 | -0.562 | 240
CHTE21 | CHTE12 | 2029 | Removed | 0.0918 | 8.7537 | -0.0575 | 278
CHTE21 | CHTE12 | 2029 | Removed | 0.1545 | 7.6337 | -0.562 | 251
CHTE41 | CHTE11 | 2029 | Addition | 0.1307 | 7.9515 | -0.1098 | 261
CHTE41 | CHTE11 | 2029 | Addition | 0.1307 | 7.9515 | -0.1098 | 251
CHTE41 | CHTE12 | 2029 | Addition | 0.0997 | 8.0088 | -0.093 | 278
CHTE41 | CHTE12 | 2029 | Addition | 0.1307 | 7.9515 | -0.1098 | 251
CHTE41 | CHTE21 | 2029 | Addition | 0.0132 | 1.6756 | -0.4337 | 1096
CHTE41 | CHTE21 | 2029 | Addition | 0.0132 | 1.6756 | -0.4337 | 1096
HAWP41 | HAWP21 | 2029 | Addition | 0.0132 | 1.6756 | -0.4337 | 1000
HIGM41 | HIGM21 | 2029 | Removed | 0.0186 | 1.5729 | -7.729 | 1044
HIGM41 | HIGM41 | 2029 | Addition | 0.0002 | 0.2873 | 0 | 2750
HIGM41 | HIGM4A | 2029 | Removed | 0.0002 | 0.2873 | 0 | 2750
HIMB41 | HIMB21 | 2029 | Addition | 0.0186 | 1.5729 | -7.729 | 1044
POAB41 | POAB11 | 2029 | Addition | 0.0282 | 4.3546 | -0.2109 | 460
SJOW21 | LODR61 | 2029 | Removed | 0.3062 | 11.0235 | -0.4552 | 198
SJOW21 | SJOW13 | 2029 | Removed | 0.167 | 7.9774 | -0.2092 | 249
SJOW41 | LODR61 | 2029 | Addition | 0.3062 | 11.0235 | -0.4552 | 198
SJOW41 | SJOW11 | 2029 | Addition | 0.1373 | 8.1976 | -0.9295 | 249
SJOW41 | SJOW21 | 2029 | Removed | 0.0224 | 2.5703 | -0.5831 | 804
TWIN4A | TWIN11 | 2029 | Addition | 0.1373 | 8.1976 | -0.1719 | 278
TWIN4B | TWIN11 | 2029 | Addition | 0.1373 | 8.1976 | -0.1719 | 278
FOUX41 | FOUX11 | 2033 | Addition | 0.148 | 7.4973 | -0.3849 | 240
KIBY41 | KIBY21 | 2033 | Addition | 0.0124 | 1.619 | -5.4994 | 1100
KIBY41 | KIBY21 | 2033 | Addition | 0.0124 | 1.619 | -5.4994 | 1100
PEWO41 | PEWO2A | 2033 | Removed | 0.0189 | 1.6132 | -0.7226 | 1129
PEWO41 | PEWO2B | 2033 | Removed | 0.0175 | 1.5879 | -4.0069 | 1139
THOM21 | THOM61 | 2033 | Removed | 0.3985 | 16.203 | -0.4431 | 122
THOM41 | THOM21 | 2033 | Addition | 0.0124 | 1.619 | -1.098 | 1100
THOM41 | THOM21 | 2033 | Removed | 0.0189 | 1.6132 | -0.7226 | 879
THOM41 | THOM21 | 2033 | Removed | 0.0185 | 1.614 | -0.5638 | 879
THOM41 | THOM61 | 2033 | Addition | 0.1844 | 13.1765 | -0.0474 | 180
WASF41 | WASF21 | 2033 | Addition | 0.0124 | 1.619 | -5.4994 | 1100
WASF41 | WASF22 | 2033 | Addition | 0.0124 | 1.619 | -5.4994 | 1100
CARL41 | CARL41 | 2035 | Addition | 0.0032 | 0.2909 | -16.2245 | 2750
CARL41 | CARL41 | 2035 | Addition | 0.0032 | 0.2909 | -16.2245 | 2750
FIDF21 | FIDF11 | 2035 | Removed | 0.1392 | 8.4361 | -0.781 | 271
FIDF21 | FIDF12 | 2035 | Removed | 0.1594 | 8.6081 | -0.2215 | 261
FIDF41 | FIDF11 | 2035 | Addition | 0.1539 | 7.9777 | -1.1994 | 240
FIDF41 | FIDF12 | 2035 | Addition | 0.1539 | 7.9777 | -1.1994 | 240
FOUR41 | FOUR21 | 2035 | Addition | 0.0132 | 1.6756 | -0.4337 | 1000
FOUR41 | FOUR21 | 2035 | Addition | 0.0132 | 1.6756 | -0.4337 | 1000
FROD21 | FROD11 | 2035 | Removed | 0.1927 | 8.5256 | -0.5357 | 211
FROD22 | FROD11 | 2035 | Removed | 0.1392 | 8.4361 | -0.781 | 269
FROD41 | FROD11 | 2035 | Addition | 0.1539 | 7.9777 | -1.1994 | 240
FROD41 | FROD11 | 2035 | Addition | 0.1539 | 7.9777 | -1.1994 | 240
FROD41 | FROD21 | 2035 | Removed | 0.0176 | 1.5828 | -0.1018 | 1000
FROD41 | FROD22 | 2035 | Removed | 0.0132 | 1.6756 | -0.4337 | 1063
HARG41 | HARG21 | 2035 | Removed | 0.0152 | 1.6463 | -0.1118 | 1100
HARG41 | HARG2A | 2035 | Removed | 0.0152 | 1.6463 | -0.1118 | 1100
HARG41 | HARG2A | 2035 | Removed | 0.0152 | 1.6463 | -0.1118 | 1100
RAIN41 | RAIN21 | 2035 | Addition | 0.0124 | 1.619 | -5.4994 | 1100
RAIN41 | RAIN21 | 2035 | Addition | 0.0124 | 1.619 | -5.4994 | 1100

## B-3-2d
B.3.2d - OFTO Transformer Changes 2025/26 to 2035/36
Wind Farm | Node 1 | Node 2 | Year | Status | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating(MVA) | Voltage(kV)
Dogger Bank C East Offshore Wind Farm | DBCO41 | DBCODC | 2025 | Addition | TBC | TBC | TBC | 426 | 400/379
| DBCWDC | DCBW61 | 2025 | Addition | TBC | TBC | TBC | 664 | 392/66
| DBDW21 | DBDW63 | 2026 | Addition | TBC | TBC | TBC | TBC | 220/66
| DBDW21 | DBDW64 | 2026 | Addition | TBC | TBC | TBC | TBC | 220/66
Inch Cape Offshore Wind Farm | INCO2A | INCO21 | 2025 | Addition | 0.064 | 8.35 | 0 | 610 | 275/220
| INCO2A | INCO22 | 2025 | Addition | 0.064 | 8.35 | 0 | 610 | 275/220
| INCW21 | INCW61 | 2025 | Addition | 0.093 | 5.45 | 0 | 545 | 220/66
| INCW22 | INCW62 | 2025 | Addition | 0.093 | 5.45 | 0 | 545 | 220/66
Sofia Offshore Wind Farm | SOFWD | SOFW61 | 2025 | Addition | 0.0117 | 2.91 | 0 | 940 | 360/66
| SOFWD | SOFW61 | 2025 | Addition | 0.0117 | 2.91 | 0 | 940 | 360/66
Vanguard West Offshore Wind Farm | VGWWX1 | VGWWX2 | 2025 | Addition | TBC | TBC | TBC | TBC | TBC
| VGWWX1 | VGWWX3 | 2025 | Addition | TBC | TBC | TBC | TBC | TBC
East Anglia 3A Offshore Wind Farm | EACO41 | Onshore Converter station 400kV | 2027 | Addition | TBC | TBC | TBC | 458 | 400/360
| EACO41 | Onshore Converter station 400kV | 2027 | Addition | TBC | TBC | TBC | 458 | 400/360
| EACO41 | Onshore Converter station 400kV | 2027 | Addition | TBC | TBC | TBC | 458 | 400/360
Hornsea 4A-1 Offshore Wind Farm | HOWW2F | HOWW6F | 2027 | Addition | TBC | TBC | TBC | 338 | 275/66
| HOWW2F | HOWW6F | 2027 | Addition | TBC | TBC | TBC | 338 | 275/66
| HOWW2F | HOWW6F | 2027 | Addition | TBC | TBC | TBC | 338 | 275/66
| HOWW2F | HOWW6F | 2027 | Addition | TBC | TBC | TBC | 338 | 275/66
| HOWW2F | HOWW6F | 2027 | Addition | TBC | TBC | TBC | 338 | 275/66
| HOWW2F | HOWW6F | 2027 | Addition | TBC | TBC | TBC | 338 | 275/66
| HOWD41 | HOWD21 | 2027 | Addition | TBC | TBC | TBC | 594 | 400/275
| HOWD41 | HOWD21 | 2027 | Addition | TBC | TBC | TBC | 594 | 400/275
| HOWD41 | HOWD21 | 2027 | Addition | TBC | TBC | TBC | 594 | 400/275
Hornsea 3A-1 Offshore Wind Farm | HOWC41 | HOWC4X | 2027 | Addition | TBC | TBC | TBC | 469 | 400/390
| HOWW4X | HOWW6E | 2027 | Addition | TBC | TBC | TBC | 686 | 391/66
| HOWW4X | HOWW6E | 2027 | Addition | TBC | TBC | TBC | 686 | 391/66
Pentland Floating Offshore Windfarm | Onshore 132 kV HV | Onshore 66 kV HV | 2027 | Addition | TBC | TBC | TBC | 120 | 132/66
| Onshore 132 kV HV | Onshore 66 kV HV | 2027 | Addition | TBC | TBC | TBC | 120 | 132/66
Seagreen 1A offshore windfarm | Onshore 275kV-1 | Onshore 220kV-1 | 2027 | Addition | TBC | TBC | TBC | TBC | 275/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2027 | Addition | TBC | TBC | TBC | TBC | 220/66
Berwick 1 Offshore Wind Farm | Onshore 400kV-1 | Onshore 275kV-1 | 2029 | Addition | TBC | TBC | TBC | 660 | 400/275
| Onshore 400kV-1 | Onshore 275kV-1 | 2029 | Addition | TBC | TBC | TBC | 660 | 400/275
| Onshore 400kV-1 | Onshore 275kV-1 | 2029 | Addition | TBC | TBC | TBC | 660 | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2029 | Addition | TBC | TBC | TBC | 430 | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2029 | Addition | TBC | TBC | TBC | 430 | 275/66
| Offshore 275kV-3 | Offshore 66kV-3 | 2029 | Addition | TBC | TBC | TBC | 430 | 275/66
Berwick 2 Offshore Wind Farm | Onshore 400kV-1 | Onshore 275kV-1 | 2029 | Addition | TBC | TBC | TBC | 660 | 400/275
| Onshore 400kV-1 | Onshore 275kV-1 | 2029 | Addition | TBC | TBC | TBC | 660 | 400/275
| Onshore 400kV-1 | Onshore 275kV-1 | 2029 | Addition | TBC | TBC | TBC | 660 | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2029 | Addition | TBC | TBC | TBC | 430 | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2029 | Addition | TBC | TBC | TBC | 430 | 275/66
| Offshore 275kV-3 | Offshore 66kV-3 | 2029 | Addition | TBC | TBC | TBC | 430 | 275/66
Berwick Bank Offshore Wind Farm C | Onshore 400kV-1 | Onshore Converter station 400kV | 2029 | Addition | TBC | TBC | TBC | TBC | 400/525
| Offshore Converter station 400kV | Offshore 275kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 525/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2029 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-3 | 2029 | Addition | TBC | TBC | TBC | TBC | 275/66
Cenos Central Offshore Wind Farm | Onshore Converter HV | Onshore Converter LV | 2029 | Addition | TBC | TBC | TBC | 800 | 400/300
| Onshore Converter HV | Onshore Converter LV | 2029 | Addition | TBC | TBC | TBC | 800 | 400/300
| Onshore DC Platform |  | 2029 | Addition | TBC | TBC | TBC | 400 | 300/66
| Offshore AC Platform HV | Ofshore AC platform LV | 2029 | Addition | TBC | TBC | TBC | 400 | 300/66
| Offshore AC Platform HV | Ofshore AC platform LV | 2029 | Addition | TBC | TBC | TBC | 400 | 300/66
| Offshore AC Platform HV | Ofshore AC platform LV | 2029 | Addition | TBC | TBC | TBC | 400 | 300/66
East Anglia 2A Offshore Wind Farm | EABO41 | Onshore 220kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2029 | Addition | TBC | TBC | TBC | 525 | 220/66
East Anglia 3B Offshore Wind Farm | Offshore DC Platform | EACW61 | 2029 | Addition | TBC | TBC | TBC | 674 | 330/66
| Offshore DC Platform | EACW62 | 2029 | Addition | TBC | TBC | TBC | 674 | 330/66
East Anglia 1 North Offshore Wind Farm | EANO41 | EANO21 | 2029 | Addition | TBC | TBC | TBC | TBC | 400/275
| EANO41 | EANO21 | 2029 | Addition | TBC | TBC | TBC | TBC | 400/275
| EANW21 | EANW61 | 2029 | Addition | TBC | TBC | TBC | 525 | 275/66
| EANW21 | EANW61 | 2029 | Addition | TBC | TBC | TBC | 525 | 275/66
Elizabeth Yellow One | Onshore 400kV-1 | Onshore 275kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-1 | Onshore 275kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-3 | Offshore 66kV-3 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
EQUINOR Offshore Windfarm | Onshore 400kV-1 | Onshore 275kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-2 | Onshore 275kV-2 | 2029 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2029 | Addition | TBC | TBC | TBC | TBC | 275/66
Erebus Offshore windfarm | EOWL11 | EOWF61 | 2029 | Addition | TBC | TBC | TBC | 120 | 132/66
| EOWL11 | EOWF61 | 2029 | Addition | TBC | TBC | TBC | 120 | 132/66
Green Volt Offshore Wind Farm | Onshore 400kV-1 | Onshore 220kV-1 | 2029 | Addition | TBC | TBC | TBC | 450 | 400/220
| Onshore 400kV-2 | Onshore 220kV-2 | 2029 | Addition | TBC | TBC | TBC | 450 | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2029 | Addition | TBC | TBC | TBC | 400 | 220/66
| Offshore 220kV-2 | Offshore 66kV-2 | 2029 | Addition | TBC | TBC | TBC | 400 | 220/66
Hornsea 4A-2 Offshore Wind Farm | HOWD41 | HOWD21 | 2029 | Addition | TBC | TBC | TBC | 594 | 400/275
| HOWD41 | HOWD21 | 2029 | Addition | TBC | TBC | TBC | 594 | 400/275
| HOWW2F | HOWW6F | 2029 | Addition | TBC | TBC | TBC | 338 | 275/66
| HOWW2F | HOWW6F | 2029 | Addition | TBC | TBC | TBC | 338 | 275/66
| HOWW2F | HOWW6F | 2029 | Addition | TBC | TBC | TBC | 338 | 275/66
| HOWW2F | HOWW6F | 2029 | Addition | TBC | TBC | TBC | 338 | 275/66
Hornsea 3A-2 Offshore Wind Farm | HOWC42 | HOWC4X | 2029 | Addition | TBC | TBC | TBC | 469 | 400/390
| HOWW4X | HOWW6E | 2029 | Addition | TBC | TBC | TBC | 686 | 391/66
| HOWW4X | HOWW6E | 2029 | Addition | TBC | TBC | TBC | 686 | 391/66
Morecambe Offshore Wind Farm | Onshore 400kV-1 | Onshore 275kV-1 | 2029 | Addition | TBC | TBC | TBC | 450 | 400/275
| Onshore 400kV-2 | Onshore 275kV-2 | 2029 | Addition | TBC | TBC | TBC | 450 | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 275kV-2 | Offshore 66kV-4 | 2029 | Addition | TBC | TBC | TBC | TBC | 220/66
North Sea B(Irish Sea) Offshore Substation | Onshore 400kV-1 | Onshore 220kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 400/220
| Onshore 400kV-2 | Onshore 220kV-2 | 2029 | Addition | TBC | TBC | TBC | TBC | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-1 | Offshore 66kV-2 | 2029 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-2 | Offshore 66kV-3 | 2029 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-2 | Offshore 66kV-4 | 2029 | Addition | TBC | TBC | TBC | TBC | 220/66
OWPL Offshore Windfarm | Onshore 400kV-1 | Onshore 275kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-2 | Onshore 275kV-2 | 2029 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2029 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-3 | 2029 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-4 | 2029 | Addition | TBC | TBC | TBC | TBC | 275/66
Project Elizabeth Offshore Windfarm | Onshore 400kV-1 | Onshore 275kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-2 | Onshore 275kV-2 | 2029 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2029 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-3 | 2029 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-4 | 2029 | Addition | TBC | TBC | TBC | TBC | 275/66
Rampion Extension Windfarm | Onshore 400kV-1 | Onshore 220kV-1 | 2029 | Addition | TBC | TBC | TBC | 450 | 400/220
| Onshore 400kV-2 | Onshore 220kV-2 | 2029 | Addition | TBC | TBC | TBC | 450 | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2029 | Addition | TBC | TBC | TBC | 400 | 220/66
| Offshore 220kV-2 | Offshore 66kV-2 | 2029 | Addition | TBC | TBC | TBC | 400 | 220/66
Salamander Offshore Wind Farm | Onshore 132 kV HV | Onshore 66 kV HV | 2029 | Addition | TBC | TBC | TBC | 240 | 132/66
| Onshore 132 kV HV | Onshore 66 kV HV | 2029 | Addition | TBC | TBC | TBC | 240 | 132/66
Vanguard East Offshore Wind Farm | VGEO41 | Onshore Converter LV | 2029 | Addition | TBC | TBC | TBC | TBC | 400/365
| VGEWX1 | Onshore AC platform | 2029 | Addition | TBC | TBC | TBC | TBC | 365/220
| Offshore AC Platform HV | VGEWX2 | 2029 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore AC Platform HV | VGEWX3 | 2029 | Addition | TBC | TBC | TBC | TBC | 220/66
Awel Y Mor Extension Wind Farm | Onshore 400kV-1 | Onshore 220kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/220
| Onshore 400kV-2 | Onshore 220kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-2 | Offshore 66kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 220/66
Caledonia Wind Farm | Onshore 400kV-1 | Onshore 275kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-1 | Onshore 275kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-2 | Onshore 275kV-3 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-2 | Onshore 275kV-4 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-3 | Offshore 66kV-3 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-4 | Offshore 66kV-4 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
East Anglia 2B Offshore Wind Farm | EABO41 | Onshore 220kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/220
| Offshore 220kV-2 | Offshore 66kV-2 | 2032 | Addition | TBC | TBC | TBC | 525 | 220/66
Five Estuaries Wind Farm | Onshore 400kV-1 | Onshore 220kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-2 | Offshore 66kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 220/66
GT R4 Wind Farm (Outer Dowsing) | Onshore 400kV-1 | Onshore 275kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-1 | Onshore 275kV-2 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-3 | Offshore 66kV-3 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
Llyr 1 Offshore Wind Farm | Onshore 400kV-1 | Offshore 66kV-1 | 2032 | Addition | TBC | TBC | TBC | 110 | 400/66
Llyr 2 Offshore Wind Farm | Onshore 400kV-2 | Offshore 66kV-2 | 2032 | Addition | TBC | TBC | TBC | 110 | 400/66
Machair | Offshore Converter station 400kV | Offshore 275kV-1 | 2029 | Addition | TBC | TBC | TBC | TBC | 525/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-3 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-4 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
Marram | Onshore 400kV-1 | Onshore Converter station 400kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | TBC
| Offshore Converter station 400kV-1 | Offshore 275kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | TBC
| Offshore 275kV-1 | Offshore 66kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-3 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
North Falls Offshore Wind Farm | Onshore 400kV-1 | Onshore 275V-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
North Sea Offshore Substation | Onshore 220 kV | Onshore 66 kV | 2032 | Addition | TBC | TBC | TBC | TBC | TBC
| Onshore 220 kV | Onshore 66 kV | 2032 | Addition | TBC | TBC | TBC | TBC | TBC
Race Bank Extension Windfarm | Onshore 400kV-1 | Onshore 275kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-2 | Onshore 275kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-3 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-4 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
Spiorad na Mara | Onshore 400kV-1 | Onshore 275kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-1 | Onshore 275kV-2 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
Talisk | Onshore 400kV-1 | Onshore 275kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-1 | Onshore 275kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
Alverdiscott 2 XL Offshore Windfarm | Onshore 400kV-1 | Onshore 275kV-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-2 | Onshore 275kV-2 | 2035 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2035 | Addition | TBC | TBC | TBC | TBC | 275/66
Ayre Offshore Wind Farm | Onshore 400kV-1 | Onshore 220kV-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 400/220
| Onshore 400kV-2 | Onshore 220kV-2 | 2035 | Addition | TBC | TBC | TBC | TBC | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-2 | Offshore 66kV-2 | 2035 | Addition | TBC | TBC | TBC | TBC | 220/66
BELLROCK OFFSHORE WINDFARM | Onshore 275kV-1 | Onshore 220kV-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 275/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-1 | Offshore 66kV-2 | 2035 | Addition | TBC | TBC | TBC | TBC | 220/66
Buchan 01 Offshore Wind Farm | Onshore 400kV-1 | Onshore 275kV-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-2 | Onshore 275kV-2 | 2035 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2035 | Addition | TBC | TBC | TBC | TBC | 275/66
Gatroben Offshore Wind Farm | Onshore Converter HV | Onshore Converter LV | 2035 | Addition | TBC | TBC | TBC | TBC | 400/320
| Onshore DC Platform | Onshore AC platform | 2035 | Addition | TBC | TBC | TBC | TBC | 320/220
| Offshore AC Platform HV | Offshore AC Platform LV | 2035 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore AC Platform HV | Offshore AC Platform LV | 2035 | Addition | TBC | TBC | TBC | TBC | 220/66
Llywelyn Extension Offshore Wind Farm | Onshore 400kV-1 | Onshore 275kV-1 | 2035 | Addition | TBC | TBC | TBC | 550 | 400/275
| Onshore 400kV-2 | Onshore 275kV-2 | 2035 | Addition | TBC | TBC | TBC | 550 | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2035 | Addition | TBC | TBC | TBC | TBC | 275/66
Llywelyn Floating Offshore Wind Farm | Onshore 400kV-1 | Onshore 275kV-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 275/66
Morven Offshore Wind Farm | Onshore Converter HV | Onshore Converter LV | 2035 | Addition | TBC | TBC | TBC | TBC | 400/320
| Onshore DC Platform | Onshore AC platform | 2035 | Addition | TBC | TBC | TBC | TBC | 320/220
| Offshore AC Platform HV | Offshore AC Platform LV | 2035 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore AC Platform HV | Offshore AC Platform LV | 2035 | Addition | TBC | TBC | TBC | TBC | 220/66
Morven Extension Offshore Wind Farm | Onshore Converter HV | Onshore Converter LV | 2035 | Addition | TBC | TBC | TBC | TBC | 400/320
| Onshore DC Platform | Onshore AC platform | 2035 | Addition | TBC | TBC | TBC | TBC | 320/220
| Offshore AC Platform HV | Offshore AC Platform LV | 2035 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore AC Platform HV | Offshore AC Platform LV | 2035 | Addition | TBC | TBC | TBC | TBC | 220/66
Muir Mhor Offshore Wind Farm | Onshore 400kV-1 | Onshore 220kV-1 | 2035 | Addition | TBC | TBC | TBC | 450 | 400/220
| Onshore 400kV-2 | Onshore 220kV-2 | 2035 | Addition | TBC | TBC | TBC | 450 | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2035 | Addition | TBC | TBC | TBC | 400 | 220/66
| Offshore 220kV-2 | Offshore 66kV-2 | 2035 | Addition | TBC | TBC | TBC | 400 | 220/66
NPI A offshore wind farm | Onshore 400kV-1 | Onshore 275V-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2035 | Addition | TBC | TBC | TBC | TBC | 275/66
Ossian Offshore Wind farm | Onshore 400kV-1 | Onshore Converter station 400kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/525
| Onshore 400kV-2 | Onshore Converter station 400kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 400/525
| Offshore Converter station 400kV-1 | Offshore 275kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 525/275
| Offshore Converter station 400kV-2 | Offshore 275kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 525/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-3 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-4 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-5 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-6 | 2032 | Addition | TBC | TBC | TBC | TBC | 275/66
Stromar Offshore Wind Farm | Onshore 400kV-1 | Onshore 220kV-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 400/220
| Onshore 400kV-2 | Onshore 220kV-2 | 2035 | Addition | TBC | TBC | TBC | TBC | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2035 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-2 | Offshore 66kV-2 | 2035 | Addition | TBC | TBC | TBC | TBC | 220/66

## B-4-1a
B-4-1a - SHE Transmission Reactive Compensation Equipment 2024/25
Site Name | Node | Unit Number | MVar Generation | MVar Absorption | Compensation Type | Connection Voltage (kV)
ALYTH | ALYT2A | 1 | 100 | 0 | Mechanically Switched Capacitor | 275
ALYTH | ALYT2A | 1 | 225 | 225 | SVC | 275
BEAULY | BEAU3U | 1 | 0 | 90 | Shunt Reactor - SGT tertiary | 33
BEAULY | BEAU1J | 1 | 45 | 0 | Mechanically Switched Capacitor | 132
BEAULY | BEAU1K | 1 | 45 | 0 | Mechanically Switched Capacitor | 132
BEAULY | BEAU2J | 1 | 150 | 150 | SVC | 275
BEAULY | BEAU3V | 2 | 0 | 90 | Shunt Reactor - SGT tertiary | 33
CROSSAIG | CRSS3W | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33
CROSSAIG | CRSS3X | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33
DOUNREAY | DOUN3W | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33
DOUNREAY | DOUN3X | 2 | 0 | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3W | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3X | 2 | 0 | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3Y | 3 | 0 | 60 | Shunt Reactor - SGT tertiary | 33
FORT AUGUSTUS | FAUG3Z | 4 | 0 | 60 | Shunt Reactor - SGT tertiary | 33
KINARDOCHY | KINA2J | 1 | 225 | 225 | SVC | 275
KINARDOCHY | KINA2K | 1 | 100 | 0 | Mechanically Switched Capacitor | 275
KINTORE | KINT1- | 1 | 0 | 100 | Shunt Reactor | 132
KINTORE | KINT1B | 2 | 0 | 100 | Shunt Reactor | 132
KINTORE | KINT3W | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33
KINTORE | KINT3Y | 2 | 0 | 60 | Shunt Reactor - SGT tertiary | 33
MACDUFF | MACD3- | 1 | 10 | 0 | Mechanically Switched Capacitor | 33
MELGARVE | MELG4J | 1 | 100 | 100 | STATCOM | 400
MELGARVE | MELG4K | 1 | 100 | 100 | STATCOM | 400
TEALING | TEAL1- | 1 | 90 | 0 | Mechanically Switched Capacitor | 132
TEALING | TEAL1- | 1 | 0 | 100 | Shunt Reactor | 132
TEALING | TEAL2J | 1 | 225 | 75 | SVC | 275
TEALING | TEAL3W | 1 | 0 | 28.96 | Shunt Reactor - SGT tertiary | 33
TEALING | TEAL3Y | 1 | 0 | 28.89 | Shunt Reactor - SGT tertiary | 33

## B-4-1b
B-4-1b - SPT Reactive Compensation Equipment 2024/25
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Bonnybridge | BONN3U | 1 | 0 | 60 | Shunt Reactor | 33
Bonnybridge | BONN3V | 2 | 0 | 60 | Shunt Reactor | 33
Coalburn | COAL3U | 1 | 0 | 60 | Shunt Reactor | 33
Coalburn | COAL3V | 2 | 0 | 60 | Shunt Reactor | 33
Cockenzie | COCK2- | 1 | 231 | 0 | Mechanically Switched Capacitor | 275
Crystal Rig | CRYR3V | 2 | 0 | 60 | Shunt Reactor | 33
Currie | CURR3W | 3 | 0 | 60 | Shunt Reactor | 33
Dewar Place | DEWP3- | 1 | 0 | 60 | Shunt Reactor | 33
Dewar Place | DEWP3- | 2 | 0 | 60 | Shunt Reactor | 33
Eccles | ECCL3V | 1 | 0 | 60 | Shunt Reactor | 33
Elvanfoot | ELVA3V | 2 | 0 | 60 | Shunt Reactor | 33
Elvanfoot | ELVA4- | 1 | 226 | 0 | Mechanically Switched Capacitor | 400
Hunterston Converter Station | HUCS4- | 1 | 248 | 382 | STATCOM | 400
Hunterston North | HUNN3W | 1 | 0 | 60 | Shunt Reactor | 33
Hunterston North | HUNN3X | 2 | 0 | 60 | Shunt Reactor | 33
Kilgallioch | KILG2- | 1 | 0 | 60 | Shunt Reactor | 275
Kilmarnock South | KILS3U | 4 | 0 | 60 | Shunt Reactor | 33
Kilmarnock South | KILS3X | 6 | 0 | 60 | Shunt Reactor | 33
Longannet | LOAN2- | 1 | 225 | 0 | Mechanically Switched Capacitor | 275
Longannet | LOAN2- | 2 | 225 | 0 | Mechanically Switched Capacitor | 275
Mark Hill | MAHI3U | 2 | 0 | 60 | Shunt Reactor | 33
Moffat | MOFF3U | 1 | 0 | 60 | Shunt Reactor | 33
Moffat | MOFF4- | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
PHOENIX HYBRID REACTIVE COMPENSATION | NEIL2- | 1 | 70 | 70 | STATCOM | 275
PHOENIX HYBRID REACTIVE COMPENSATION | NEIL2- | 1 | 70 | 33 | Sync Comp | 275
Neilston | NEIL3U | 1 | 0 | 60 | Shunt Reactor | 33
Neilston | NEIL3V | 2 | 0 | 60 | Shunt Reactor | 33
Smeaton | SMEA3U | 1 | 0 | 60 | Shunt Reactor | 33
Smeaton | SMEA3V | 2 | 0 | 60 | Shunt Reactor | 33
Strathaven | STHA3V | 4 | 0 | 60 | Shunt Reactor | 33
Torness | TORN4- | 1 | 0 | 150 | Shunt Reactor | 400
Torness | TORN4- | 2 | 0 | 150 | Shunt Reactor | 400
Wishaw (Gowkthrapple) | WISH3W | 1 | 0 | 60 | Shunt Reactor | 33
Windyhill | WIYH2- | 1 | 150 | 0 | Mechanically Switched Capacitor | 275
Windyhill | WIYH3W | 3 | 0 | 60 | Shunt Reactor | 33

## B-4-1c
B-4-1c - NGET Reactive Compensation Equipment for 2024/25
Site Name | Node | Unit Number | Mvar Generation | Mvar Absorption | Compensation Type | Connection Voltage (kV)
Aberthaw | ABTH11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132
Aberthaw | ABTH11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Abham | ABHA11 | 3 | 45 | 0 | Mechanically Switched Capacitor | 132
Abham | ABHA12 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132
Alverdiscott | ALVE11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Barking | BARK22 | 2B WDG 1 | 0 | 30 | Shunt Reactor | 13
Barking | BARK22 | 2B WDG 2 | 0 | 30 | Shunt Reactor | 13
Barking | BARK22 | 4B WDG 2 | 0 | 30 | Shunt Reactor | 13
Barking | BARK22 | 4B WDG 1 | 0 | 30 | Shunt Reactor | 13
Beddington | BEDD21 | 3B | 0 | 60 | Shunt Reactor | 13
Beddington | BEDD21 | 1B | 0 | 60 | Shunt Reactor | 13
Beddington | BEDD21 | 4B | 154 | 0 | Mechanically Switched Capacitor | 275
Beddington | BEDD21 | 5B | 0 | 100 | Shunt Reactor | 275
Beddington | BEDD22 | 4B | 0 | 60 | Shunt Reactor | 13
Beddington | BEDD22 | 3B | 154 | 0 | Mechanically Switched Capacitor | 275
Beddington | BEDD23 | 2B | 0 | 60 | Shunt Reactor | 13
Beddington | BEDD23 | 6A | 0 | 100 | Shunt Reactor | 275
Berkswell | BESW11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Berkswell | BESW12 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Berkswell | BESW12 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Birkenhead | BIRK21 | 4 WDG B | 0 | 30 | Shunt Reactor | 13
Birkenhead | BIRK21 | 4 WDG A | 0 | 30 | Shunt Reactor | 13
Bishops Wood | BISW11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132
Bishops Wood | BISW11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132
Blyth | BLYT21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275
Blyth | BLYT21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275
Bolney | BOLN11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Bolney | BOLN11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Bolney | BOLN12 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Bolney | BOLN12 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132
Bolney | BOLN41 | 2 | 0 | 60 | Shunt Reactor | 13
Bolney | BOLN41 | 6 | 225 | 100 | SVC | 32
Bolney | BOLN41 | 1 | 0 | 60 | Shunt Reactor | 13
Bolney | BOLN41 | 7 | 225 | 0 | Mechanically Switched Capacitor | 400
Bolney | BOLN41 | 5 | 228 | 0 | Mechanically Switched Capacitor | 400
Bradford West | BRAW11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Bradford West | BRAW21 | 4 WDG B | 0 | 30 | Shunt Reactor | 13
Bradford West | BRAW21 | 4 WDG A | 0 | 30 | Shunt Reactor | 13
Bradford West | BRAW21 | 3 | 0 | 60 | Shunt Reactor | 13
Bradford West | BRAW21 | 5 | 0 | 100 | Shunt Reactor | 275
Bramford | BRFO11 | 1B | 59 | 0 | Mechanically Switched Capacitor | 132
Bramford | BRFO11 | 1A | 59 | 0 | Mechanically Switched Capacitor | 132
Bramford | BRFO11 | 1C | 59 | 0 | Mechanically Switched Capacitor | 132
Bramford | BRFO41 | 1 | 0 | 200 | Shunt Reactor | 400
Bredbury | BRED21 | 102 | 0 | 30 | Shunt Reactor | 13
Bredbury | BRED21 | 101 | 0 | 30 | Shunt Reactor | 13
Bredbury | BRED21 | 301 | 0 | 30 | Shunt Reactor | 13
Bredbury | BRED21 | 302 | 0 | 30 | Shunt Reactor | 13
Bridgewater | BRWA11 | 1A | 45 | 0 | Mechanically Switched Capacitor | 132
Bridgewater | BRWA11 | 1B | 45 | 0 | Mechanically Switched Capacitor | 132
Burwell Main | BURW41 | -2 | 225 | 0 | Mechanically Switched Capacitor | 400
Burwell Main | BURW41 | -1 | 225 | 0 | Mechanically Switched Capacitor | 400
Bushbury | BUSH11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132
Bushbury | BUSH11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132
Bushbury | BUSH11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132
Bushbury | BUSH21 | 3 | 0 | 60 | Shunt Reactor | 13
Bushbury | BUSH21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275
Bustleholme | BUST21 | 1 WDG A | 0 | 30 | Shunt Reactor | 13
Bustleholme | BUST21 | 1 WDG B | 0 | 30 | Shunt Reactor | 13
Bustleholme | BUST21 | 4 | 0 | 60 | Shunt Reactor | 13
Canterbury North | CANT41 | 4 | 0 | 200 | Shunt Reactor | 400
Capenhurst | CAPE21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275
Cellarhead | CELL11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132
Cellarhead | CELL11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132
Cellarhead | CELL12 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Cellarhead | CELL12 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132
Cellarhead | CELL41 | 2 WDG 2 | 0 | 30 | Shunt Reactor | 13
Cellarhead | CELL41 | 3 WDG B | 0 | 30 | Shunt Reactor | 13
Cellarhead | CELL41 | 2 WDG 1 | 0 | 30 | Shunt Reactor | 13
Cellarhead | CELL41 | 6 | 150 | 95 | SVC | 7.9
Cellarhead | CELL41 | 3 WDG A | 0 | 30 | Shunt Reactor | 13
Cellarhead | CELL41 | 5 | 150 | 95 | SVC | 7.9
Cellarhead | CELL41 | 7 | 230 | 0 | Mechanically Switched Capacitor | 400
Cellarhead | CELL41 | 8 | 230 | 0 | Mechanically Switched Capacitor | 400
Chesterfield | CHTE21 | 4 | 0 | 60 | Shunt Reactor | 13
Chickerell | CHIC41 | 2 | 0 | 60 | Shunt Reactor | 13
Chickerell | CHIC41 | 1 | 0 | 200 | Shunt Reactor | 400
Chickerell | CHIC4A | 2 | 230 | 0 | Mechanically Switched Capacitor | 400
Chickerell | CHIC4A | 3 | 0 | 200 | Shunt Reactor | 400
Cilfynydd | CILF41 | 1 | 0 | 60 | Shunt Reactor | 13
Cilfynydd | CILF41 | 2 | 0 | 60 | Shunt Reactor | 13
Cilfynydd | CILF41 | 6 | 0 | 200 | Shunt Reactor | 400
Cilfynydd | CILF41 | 4 | 0 | 200 | Shunt Reactor | 400
City Road | CITR41 | 2 | 56 | 0 | Mechanically Switched Capacitor | 13
City Road | CITR41 | 4 | 56 | 0 | Mechanically Switched Capacitor | 13
City Road | CITR41 | 1 | 0 | 200 | Shunt Reactor | 400
Coventry | COVE11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Coventry | COVE11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Coventry | COVE12 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Coventry | COVE21 | 3 | 0 | 60 | Shunt Reactor | 13
Cowley | COWL11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132
Cowley | COWL11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132
Cowley | COWL11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132
Cowley | COWL41 | 2 | 0 | 200 | Shunt Reactor | 400
Cowley | COWL41 | 3 | 0 | 200 | Shunt Reactor | 400
Drakelow | DRAK41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400
Drakelow | DRAK41 | 3 | 230 | 0 | Mechanically Switched Capacitor | 400
Drakelow | DRAK41 | 6 | 0 | 200 | Shunt Reactor | 400
Drakelow | DRAK41 | 4 | 0 | 200 | Shunt Reactor | 400
Drax | DRAX41 | 1 | 0 | 60 | Shunt Reactor | 13
Drax | DRAX41 | 2 | 0 | 60 | Shunt Reactor | 13
East Claydon | ECLA12 | 3 | 61 | 0 | Mechanically Switched Capacitor | 132
East Claydon | ECLA41 | 1 WDG B | 0 | 30 | Shunt Reactor | 13
East Claydon | ECLA41 | 2 WDG B | 0 | 30 | Shunt Reactor | 13
East Claydon | ECLA41 | 2 WDG A | 0 | 30 | Shunt Reactor | 13
East Claydon | ECLA41 | 1 WDG A | 0 | 30 | Shunt Reactor | 13
East Claydon | ECLA41 | 5 | 225 | 0 | Mechanically Switched Capacitor | 400
Elland | ELLA21 | 2 | 0 | 60 | Shunt Reactor | 13
Elstree | ELST41 | 1 | 0 | 200 | Shunt Reactor | 400
Enderby | ENDE41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
Enderby | ENDE41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400
Exeter | ELLA21 | 5 | 150 | 95 | SVC | 7.9
Exeter | ELLA21 | 3 | 150 | 95 | SVC | 7.9
Exeter | EXET11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Exeter | EXET41 | 1 | 28 | 0 | Mechanically Switched Capacitor | 13
Exeter | EXET41 | 2 | 28 | 0 | Mechanically Switched Capacitor | 13
FECKENHAM | FECK21 | 6 | 150 | 75 | SVC | 275
Feckenham | FECK41 | 4 | 0 | 30 | Shunt Reactor | 13
Feckenham | FECK41 | 4 | 0 | 30 | Shunt Reactor | 13
Fleet | FLEE11 | 2B | 53 | 0 | Mechanically Switched Capacitor | 132
Fleet | FLEE11 | 2C | 53 | 0 | Mechanically Switched Capacitor | 132
Fleet | FLEE11 | 2A | 53 | 0 | Mechanically Switched Capacitor | 132
Fleet | FLEE41 | 3 WDG 1 | 0 | 30 | Shunt Reactor | 13
Fleet | FLEE41 | 4A WDG 2 | 0 | 30 | Shunt Reactor | 13
Fleet | FLEE41 | 4A WDG 1 | 0 | 30 | Shunt Reactor | 13
Fleet | FLEE41 | 3 WDG 2 | 0 | 30 | Shunt Reactor | 13
Fleet | FLEE41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
Frodsham | FROD41 | 1 | 0 | 200 | Shunt Reactor | 400
Grain | GRAI41 | 1 | 0 | 200 | Shunt Reactor | 400
Grendon | GREN11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132
Grendon | GREN11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132
Grendon | GREN11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132
Grendon | GREN41 | 1 | 0 | 60 | Shunt Reactor | 13
Grendon | GREN41 | 6 | 225 | 0 | Mechanically Switched Capacitor | 400
Grendon | GREN41 | 5 | 230 | 0 | Mechanically Switched Capacitor | 400
Grendon | GREN41 | 3 | 230 | 0 | Mechanically Switched Capacitor | 400
Grendon | GREN41 | 4 | 225 | 0 | Mechanically Switched Capacitor | 400
Greystones A | GRST2A | 1 | 0 | 100 | Shunt Reactor | 275
Greystones B | GRST2B | 3 | 0 | 100 | Shunt Reactor | 275
Hams Hall | HAMH41 | 3 | 230 | 0 | Mechanically Switched Capacitor | 400
Hams Hall | HAMH41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400
Hams Hall | HAMH41 | 4 | 0 | 200 | Shunt Reactor | 400
Harker | HARK21 | 7 | 146 | 124 | SVC | 14
Harker | HARK21 | 8 | 146 | 124 | SVC | 14
Harker | HARK21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275
Harker | HARK41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400
Harker | HARK41 | 3A | 225 | 0 | Mechanically Switched Capacitor | 400
Harker | HARK41 | 3B | 225 | 0 | Mechanically Switched Capacitor | 400
Hurst | HURS21 | 2 | 0 | 60 | Shunt Reactor | 13
Hurst | HURS21 | 3 | 0 | 60 | Shunt Reactor | 13
Hurst | HURS21 | 4 | 0 | 100 | Shunt Reactor | 275
Hurst | HURS21 | 7 | 0 | 100 | Shunt Reactor | 275
Hurst | HURS21 | 2A | 0 | 100 | Shunt Reactor | 275
Hurst | HURS21 | 1 | 0 | 100 | Shunt Reactor | 275
Hurst | HURS21 | 2B | 154 | 0 | Mechanically Switched Capacitor | 275
Hutton | HUTT41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400
Indian Queens | INDQ11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Indian Queens | INDQ11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132
Indian Queens | INDQ11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Indian Queens | INDQ41 | 1 | 0 | 60 | Shunt Reactor | 13
Indian Queens | INDQ41 | 5 | 230 | 0 | Mechanically Switched Capacitor | 400
Indian Queens | INDQ41 | 2 | 0 | 200 | Shunt Reactor | 400
Iron Acton | IROA11 | 6 | 45 | 0 | Mechanically Switched Capacitor | 132
Ironbridge | IRON11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Ironbridge | IRON12 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Ironbridge | IRON12 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Ironbridge | IRON41 | 5 | 231 | 0 | Mechanically Switched Capacitor | 400
Iver | IVER21 | 1A | 0 | 60 | Shunt Reactor | 13
Iver | IVER21 | 3A | 0 | 60 | Shunt Reactor | 13
IVER | IVER4A | 6B | 0 | 55 | Shunt Reactor | 400
IVER | IVER4B | 5A | 0 | 55 | Shunt Reactor | 400
Jordanthorpe 33kV | JORD31 | 2 | 0 | 60 | Shunt Reactor | 33
Kearsley | KEAR11 | 1C | 53 | 0 | Mechanically Switched Capacitor | 132
Kearsley | KEAR11 | 1B | 53 | 0 | Mechanically Switched Capacitor | 132
Kearsley | KEAR11 | 1A | 53 | 0 | Mechanically Switched Capacitor | 132
Kearsley | KEAR21 | 3A | 0 | 60 | Shunt Reactor | 13
Kingsnorth | KINO41 | 2 WDG 1 | 0 | 30 | Shunt Reactor | 13
Kingsnorth | KINO41 | 1 WDG 2 | 0 | 30 | Shunt Reactor | 13
Kingsnorth | KINO41 | 2 WDG 2 | 0 | 30 | Shunt Reactor | 13
Kingsnorth | KINO41 | 1 WDG 1 | 0 | 30 | Shunt Reactor | 13
Kingsnorth | KINO41 | 4 | 0 | 200 | Shunt Reactor | 400
Kingsnorth | KINO41 | 3 | 0 | 200 | Shunt Reactor | 400
Kirkby | KIBY11 | 1A | 45 | 0 | Mechanically Switched Capacitor | 132
Kirkby | KIBY11 | 4A | 45 | 0 | Mechanically Switched Capacitor | 132
Kirkby | KIBY11 | 2A | 45 | 0 | Mechanically Switched Capacitor | 132
Kirkby | KIBY11 | 3B | 45 | 0 | Mechanically Switched Capacitor | 132
Kirkstall | KIRK21 | 4 | 0 | 60 | Shunt Reactor | 13
Kirkstall | KIRK21 | 2 | 0 | 60 | Shunt Reactor | 13
Kirkstall | KIRK21 | 3 | 154 | 0 | Mechanically Switched Capacitor | 275
Laleham | LALE21 | 1 | 0 | 100 | Shunt Reactor | 275
Laleham | LALE21 | 2 | 0 | 100 | Shunt Reactor | 275
Laleham | LALE21 | 3 | 0 | 100 | Shunt Reactor | 275
Landulph | LAND11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Landulph | LAND41 | 2 WDG B | 0 | 30 | Shunt Reactor | 13
Landulph | LAND41 | 2 WDG A | 0 | 30 | Shunt Reactor | 13
Landulph | LAND42 | H | 60 | 60 | SVC | 13
Landulph | LAND42 | 3 | 0 | 200 | Shunt Reactor | 400
Legacy | LEGA41 | 1 | 0 | 60 | Shunt Reactor | 13
Legacy | LEGA41 | 2 | 0 | 60 | Shunt Reactor | 13
Legacy | LEGA41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
Lister Drive | LISD21 | 1 | 0 | 100 | Shunt Reactor | 275
Lovedean | LOVE41 | 3 | 0 | 60 | Shunt Reactor | 13
Lovedean | LOVE41 | 5 | 150 | 95 | SVC | 7.9
Lovedean | LOVE41 | 4A | 0 | 60 | Shunt Reactor | 13
Lovedean | LOVE41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400
Lovedean | LOVE41 | 1 | 0 | 200 | Shunt Reactor | 400
Lovedean | LOVE41 | 7 | 0 | 200 | Shunt Reactor | 400
Mannington | MANN11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132
Mannington | MANN11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132
Mannington | MANN11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132
Mannington | MANN11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132
Mannington | MANN11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132
Mannington | MANN11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132
Melksham | MELK11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132
Melksham | MELK11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132
Melksham | MELK11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132
Melksham | MELK41 | 5 | 0 | 60 | Shunt Reactor | 13
Melksham | MELK41 | 6 | 0 | 60 | Shunt Reactor | 13
Melksham | MELK41 | 1 | 0 | 200 | Shunt Reactor | 400
Mill Hill | MILH2A | 2A WDG 2 | 0 | 30 | Shunt Reactor | 13
Mill Hill | MILH2A | 1B WDG 2 | 0 | 30 | Shunt Reactor | 13
Mill Hill | MILH2A | 1B WDG 1 | 0 | 30 | Shunt Reactor | 13
Mill Hill | MILH2B | 2A WDG 1 | 0 | 30 | Shunt Reactor | 13
Monk Fryston | MONF21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275
Nechells | NECH21 | 4 WDG B | 0 | 30 | Shunt Reactor | 13
Nechells | NECH21 | 1 | 0 | 60 | Shunt Reactor | 13
Nechells | NECH21 | 4 WDG A | 0 | 30 | Shunt Reactor | 13
New Cross | NEWX21 | 6 | 0 | 100 | Shunt Reactor | 275
New Cross | NEWX21 | 5 | 0 | 100 | Shunt Reactor | 275
Ninfield | NINF41 | 5 | 225 | 100 | SVC | 56.6
Ninfield | NINF41 | 1 | 0 | 200 | Shunt Reactor | 400
Ninfield | NINF41 | 2 | 225 | 0 | Mechanically Switched Capacitor | 400
NINFIELD | NINF41 | 6 | 150 | 150 | SVC | 400
Nursling | NURS41 | 2 | 0 | 60 | Shunt Reactor | 13
Ocker Hill | OCKH21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275
Oldbury | OLDB21 | 2 WDG B | 0 | 30 | Shunt Reactor | 13
Oldbury | OLDB21 | 2 WDG A | 0 | 30 | Shunt Reactor | 13
Pelham | PELH41 | -1 | 225 | 0 | Mechanically Switched Capacitor | 400
Pelham | PELH41 | -2 | 225 | 0 | Mechanically Switched Capacitor | 400
Pelham | PELH41 | 3 | 0 | 200 | Shunt Reactor | 400
Pembroke | PEMB41 | 1 | 0 | 60 | Shunt Reactor | 13
Pembroke | PEMB41 | 2 | 0 | 60 | Shunt Reactor | 13
Pentir | PENT41 | 2 | 0 | 200 | Shunt Reactor | 400
Pentir | PENT41 | 5 | 0 | 200 | Shunt Reactor | 400
Penwortham | PEWO41 | 6 | 0 | 60 | Shunt Reactor | 13
Pitsmoor 33kV | PITS31 | 4 | 0 | 60 | Shunt Reactor | 33
Pitsmoor 33kV | PITS31 | 3 | 0 | 60 | Shunt Reactor | 33
Port Ham | PORH11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Port Ham | PORH11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132
Rainhill | RAIN11 | 2 | 45 | 0 | Mechanically Switched Capacitor | 132
Rainhill | RAIN11 | 4 | 45 | 0 | Mechanically Switched Capacitor | 132
Rainhill | RAIN12 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132
Rainhill | RAIN12 | 3 | 45 | 0 | Mechanically Switched Capacitor | 132
Ratcliffe-On-Soar | RATS41 | 2 | 0 | 200 | Shunt Reactor | 400
Rayleigh | RAYL41 | 5 | 0 | 60 | Shunt Reactor | 13
Richborough | RICH41 | 1 | 225 | 100 | SVC | 32
Richborough | RICH41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400
Rochdale | ROCH11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132
Rochdale | ROCH11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132
Rochdale | ROCH11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132
Rye House | RYEH41 | -1 | 225 | 0 | Mechanically Switched Capacitor | 400
Rye House | RYEH41 | -2 | 225 | 0 | Mechanically Switched Capacitor | 400
Sandford | SAFO41 | 3 | 0 | 200 | Shunt Reactor | 400
Sandford | SAFO41 | 1 | 0 | 200 | Shunt Reactor | 400
Sellindge Compound A | SELL4A | 2 | 150 | 150 | SVC | 56.6
Sellindge Compound A | SELL4A | 1 | 150 | 150 | SVC | 56.6
Skelton Grange | SKLG11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG21 | 3 | 0 | 100 | Shunt Reactor | 275
Skelton Grange | SKLG21 | 6 | 154 | 0 | Mechanically Switched Capacitor | 275
Spennymoor | SPEN41 | 1 | 0 | 60 | Shunt Reactor | 13
St. Johns Wood | SJOW11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132
St. Johns Wood | SJOW11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132
St. Johns Wood | SJOW11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132
St. Johns Wood | SJOW21 | 2B | 0 | 60 | Shunt Reactor | 13
St. Johns Wood | SJOW41 | 2 | 0 | 200 | Shunt Reactor | 400
St. Johns Wood | SJOW41 | 1 | 0 | 200 | Shunt Reactor | 400
St. Johns Wood | SJOW41 | 4 | 0 | 200 | Shunt Reactor | 400
ST.JOHNS WOOD | SJOW21 | 1 | 150 | 106 | SVC | 275
ST.JOHNS WOOD | SJOW21 | 3 | 150 | 106 | SVC | 275
Stalybridge | STAL41 | 1 | 0 | 200 | Shunt Reactor | 400
Stella West | STEW21 | 2 | 0 | 100 | Shunt Reactor | 275
Stella West | STEW41 | 2 | 225 | 0 | Mechanically Switched Capacitor | 400
Stella West | STEW41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400
Stocksbridge | STSB4A | 1 | 0 | 200 | Shunt Reactor | 400
Sundon | SUND41 | 5 WDG 1 | 0 | 30 | Shunt Reactor | 13
Sundon | SUND41 | 5 WDG 2 | 0 | 30 | Shunt Reactor | 13
Sundon | SUND41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
Sundon | SUND42 | 8 WDG 1 | 0 | 30 | Shunt Reactor | 13
Sundon | SUND42 | 8 WDG 2 | 0 | 30 | Shunt Reactor | 13
Sundon | SUND42 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400
Thorpe Marsh | THOM42 | 6 | 0 | 200 | Shunt Reactor | 400
Tottenham | TOTT21 | 5 | 0 | 100 | Shunt Reactor | 275
Tottenham | TOTT21 | 1 | 0 | 100 | Shunt Reactor | 275
Tottenham | TOTT22 | 3 | 0 | 100 | Shunt Reactor | 275
Tynemouth | TYNE21 | 2 | 0 | 60 | Shunt Reactor | 13
Uskmouth | USKM12 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132
Walham | WALH41 | 3 | 0 | 60 | Shunt Reactor | 13
Walham | WALH41 | 2 | 0 | 60 | Shunt Reactor | 13
Walham | WALH41 | 1 | 57 | 0 | Mechanically Switched Capacitor | 13
Walham | WALH41 | 4 | 0 | 200 | Shunt Reactor | 400
Walpole | WALP11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132
Walpole | WALP11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132
Walpole | WALP11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132
Walpole | WALP41 | 1 | 0 | 60 | Shunt Reactor | 13
Walpole | WALP41 | 2 | 0 | 60 | Shunt Reactor | 13
Warley | WARL11 | 1C | 52 | 0 | Mechanically Switched Capacitor | 132
Warley | WARL11 | 1B | 52 | 0 | Mechanically Switched Capacitor | 132
Warley | WARL11 | 1A | 52 | 0 | Mechanically Switched Capacitor | 132
West Ham | WHAM41 | 4 | 230 | 0 | Mechanically Switched Capacitor | 400
West Ham | WHAM41 | 1 | 0 | 200 | Shunt Reactor | 400
West Melton | WMEL12 | 3C | 45 | 0 | Mechanically Switched Capacitor | 132
West Melton | WMEL12 | 3A | 45 | 0 | Mechanically Switched Capacitor | 132
West Melton | WMEL12 | 3B | 45 | 0 | Mechanically Switched Capacitor | 132
West Weybridge | WWEY21 | 1 | 0 | 100 | Shunt Reactor | 275
Whitegate | WHGA21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275
Whitegate | WHGA21 | 4B | 0 | 60 | Shunt Reactor | 13
Whitegate | WHGA21 | 4A | 0 | 60 | Shunt Reactor | 13
Willesden | WISD21 | 2B | 0 | 60 | Shunt Reactor | 13
Willesden | WISD21 | 3B WDG 1 | 0 | 30 | Shunt Reactor | 13
Willesden | WISD21 | 3B WDG 2 | 0 | 30 | Shunt Reactor | 13
Wimbledon | WIMB21 | 4 | 0 | 100 | Shunt Reactor | 275
Wimbledon | WIMB21 | 2 | 0 | 100 | Shunt Reactor | 275
Wimbledon | WIMB41 | -5 | 0 | 200 | Shunt Reactor | 400
Wimbledon | WIMB41 | 6 | 0 | 225 | Shunt Reactor | 400
Wylfa | WYLF41 | 1 | 0 | 200 | Shunt Reactor | 400
Wymondley | WYMO41 | 3 | 0 | 200 | Shunt Reactor | 400
Wymondley | WYMO41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400
Wymondley | WYMO41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400

## B-4-1d
B.4.1d - OFTO Reactive Compensation Equipment 2024/25
OFTO | Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSO11 | 1 | 0 | 24 | Shunt Reactor | 132
TC Beatrice OFTO Limited | Beatrice Offshore Windfarm | BEAT21 | SHR1 | 0 | 115 | Shunt Reactor | 220
|  | BEAT22 | SHR2 | 0 | 115 | Shunt Reactor | 220
|  | BEAT21 | SHR3 | 0 | 115 | Shunt Reactor | 220
|  | BEAT22 | SHR4 | 0 | 115 | Shunt Reactor | 220
|  | BEAT41 | SVC1 | 144 | 155 | SVC | 400
|  | BEAT41 | SVC2 | 144 | 155 | SVC | 400
Diamond Transmission Partners BBE Limited | Burbo Bank Extension Wind Farm | BBWO41 | 1 | 0 | 60 | Shunt Reactor | 400
|  | BBWO21 | 1 | 0 | 125 | Shunt Reactor | 220
|  | BBWO41 | SVC1 | 82.17 | 82.17 | SVC | 400
TC Dudgeon OFTO plc | Dudgeon Offshore Wind Farm | DUDO11 | SHR1 | 0 | 85 | Shunt Reactor | 132
|  | DUDO12 | SHR2 | 0 | 85 | Shunt Reactor | 132
|  | NECT41 | SVC1 | 125 | 125 | SVC | 400
|  | NECT41 | SVC2 | 125 | 125 | SVC | 400
East Anglia One Limited | East Anglia Offshore Wind Farm | EAAW21 | SH1 | 0 | 174 | Shunt Reactor | 220
|  | EAAW22 | SH2 | 0 | 174 | Shunt Reactor | 220
|  | BRST21 | VSR-1 | 0 | 228 | Shunt Reactor | 220
|  | BRST22 | VSR-2 | 0 | 228 | Shunt Reactor | 220
|  | BRST41 | SVC1 | 215 | 215 | SVC | 400
|  | BRST42 | SVC2 | 215 | 215 | SVC | 400
Diamond Transmission Partners Galloper Limited | Galloper Offshore Wind Farm | GALO11 | SVC3 | 70 | 70 | SVC | 132
|  | GALO12 | SVC4 | 70 | 70 | SVC | 132
|  | GALO11 | MSR 05 | 0 | 85 | Shunt Reactor | 132
|  | GALO12 | MSR 06 | 0 | 85 | Shunt Reactor | 132
Greater Gabbard OFTO plc | Greater Gabbard Offshore Wind Farm | GGON11 | 1 | 55 | 0 | Mechanically Switched Capacitor | 132
|  | GGON12 | 2 | 55 | 0 | Mechanically Switched Capacitor | 132
|  | GGON13 | 3 | 55 | 0 | Mechanically Switched Capacitor | 132
|  | GGON11 | 1 | 0 | 43 | Shunt Reactor | 132
|  | GGON12 | 2 | 0 | 43 | Shunt Reactor | 132
|  | GGON13 | 3 | 0 | 43 | Shunt Reactor | 132
|  | GANW3A | 1 | 0 | 30 | Shunt Reactor | 33
|  | GANW3B | 1 | 0 | 30 | Shunt Reactor | 33
|  | GGON11 | 1 | 50 | 50 | SVC | 132
|  | GGON12 | 2 | 50 | 50 | SVC | 132
|  | GGON13 | 3 | 50 | 50 | SVC | 132
TC Gunfleet Sands OFTO Limited | Gunfleet Sands Offshore Wind Farm | CLTO11 | 1 | 0 | 64 | Shunt Reactor | 132
Gwynt y Môr OFTO plc | Gwynt Y Mor Offshore Wind Farm | BODE41 | 1 | 50 | 50 | SVC | 400
|  | BODE41 | 2 | 50 | 50 | SVC | 400
|  | BODE41 | 1A | 0 | 55 | Shunt Reactor | 400
|  | BODE41 | 1B | 0 | 55 | Shunt Reactor | 400
|  | BODE41 | 2A | 0 | 55 | Shunt Reactor | 400
|  | BODE41 | 2B | 0 | 55 | Shunt Reactor | 400
|  | BODE41 | 1A | 30 | 0 | Mechanically Switched Capacitor | 400
|  | BODE41 | 1B | 30 | 0 | Mechanically Switched Capacitor | 400
|  | BODE41 | 2A | 30 | 0 | Mechanically Switched Capacitor | 400
|  | BODE41 | 2B | 30 | 0 | Mechanically Switched Capacitor | 400
Diamond Transmission Partners Hornsea One Limited | Hornsea One Offshore Wind Farm | HOWA41 | 3 | 0 | 75 | Shunt Reactor | 400
|  | HOWA41 | 4 | 0 | 75 | Shunt Reactor | 400
|  | HOWA21 | 1 | 0 | 300 | Shunt Reactor | 220
|  | HOWA21 | 2 | 0 | 300 | Shunt Reactor | 220
|  | HOWA21 | 3 | 0 | 300 | Shunt Reactor | 220
|  | HOWR2A | 1 | 0 | 220 | Shunt Reactor | 220
|  | HOWR2A | 2 | 0 | 220 | Shunt Reactor | 220
|  | HOWR2A | 3 | 0 | 220 | Shunt Reactor | 220
|  | HOWW2A | 1 | 0 | 85 | Shunt Reactor | 220
|  | HOWW2B | 1 | 0 | 105 | Shunt Reactor | 220
|  | HOWW2C | 1 | 0 | 135 | Shunt Reactor | 220
|  | HOWA21 | 1 | 160 | 200 | SVC | 220
|  | HOWA21 | 2 | 160 | 200 | SVC | 220
|  | HOWA21 | 3 | 160 | 200 | SVC | 220
Breesea Limited | Hornsea Two Offshore Wind Farm | HOWB41 | 3 | 0 | 85 | Shunt Reactor | 400
|  | HOWB41 | 4 | 0 | 85 | Shunt Reactor | 400
|  | HOWB21 | VSR1 | 0 | 300 | Shunt Reactor | 220
|  | HOWB21 | VSR2 | 0 | 300 | Shunt Reactor | 220
|  | HOWB21 | VSR3 | 0 | 300 | Shunt Reactor | 220
|  | HOWB21 | SVC1 | 240 | 240 | SVC | 220
|  | HOWB21 | SVC2 | 240 | 240 | SVC | 220
|  | HOWB21 | SVC3 | 240 | 240 | SVC | 220
|  | HOWW2D | 1 | 0 | 90 | Shunt Reactor | 220
|  | HOWW2D | 2 | 0 | 90 | Shunt Reactor | 220
|  | HOWW2D | 3 | 0 | 90 | Shunt Reactor | 220
|  | HOWR2B | 1 | 0 | 170 | Shunt Reactor | 220
|  | HOWR2B | 2 | 0 | 170 | Shunt Reactor | 220
|  | HOWR2B | 3 | 0 | 170 | Shunt Reactor | 220
Humber Gateway OFTO Limited | Humber Gateway Offshore Wind Farm | HUMO11 | 1 | 0 | 28.2 | Shunt Reactor | 132
|  | HUMO12 | 2 | 0 | 28.2 | Shunt Reactor | 132
|  | HUMO31 | 1A | 0 | 28 | Shunt Reactor | 33
|  | HUMO31 | 1B | 0 | 28 | Shunt Reactor | 33
|  | HUMO32 | 2A | 0 | 28 | Shunt Reactor | 33
|  | HUMO32 | 2B | 0 | 28 | Shunt Reactor | 33
|  | HUMO31 | 1 | 24 | 24 | SVC | 33
|  | HUMO32 | 2 | 24 | 24 | SVC | 33
TC Lincs OFTO Limited | Lincs Offshore Wind Farm | LINO41 | SVC1 | 94 | 139 | SVC | 400
|  | LINO13 | SR1 | 0 | 46 | Shunt Reactor | 132
|  | LINO14 | SR2 | 0 | 46 | Shunt Reactor | 132
|  | LINS31 | SR1 | 0 | 40 | Shunt Reactor | 33
|  | LINS32 | SR2 | 0 | 40 | Shunt Reactor | 33
Blue Transmission London Array Limited | London Array Offshore Wind Farm | LONO41 | 1A | 52 | 52 | SVC | 400
|  | LONO42 | 2A | 52 | 52 | SVC | 400
|  | LONO43 | 1B | 52 | 52 | SVC | 400
|  | LONO44 | 2B | 52 | 52 | SVC | 400
Moray East Offshore Wind Limited | Moray East Offshore Wind Farm | MOWE21 | SHR1 | 0 | 75 | Shunt Reactor | 220
|  | MOWE22 | SHR1 | 0 | 75 | Shunt Reactor | 220
|  | MOWE23 | SHR1 | 0 | 75 | Shunt Reactor | 220
|  | MORO21 | SHR1A | 0 | 110 | Shunt Reactor | 220
|  | MORO21 | SHR1B | 0 | 110 | Shunt Reactor | 220
|  | MORO22 | SHR2A | 0 | 110 | Shunt Reactor | 220
|  | MORO22 | SHR2B | 0 | 110 | Shunt Reactor | 220
|  | MORO23 | SHR3A | 0 | 110 | Shunt Reactor | 220
|  | MORO23 | SHR3B | 0 | 110 | Shunt Reactor | 220
|  | MORF21 | MSR1 | 0 | 133 | Shunt Reactor | 275
|  | MORF21 | SVC1 | 174 | 197 | SVC | 275
|  | MORF22 | MSR2 | 0 | 133 | Shunt Reactor | 275
|  | MORF22 | SVC2 | 174 | 197 | SVC | 275
|  | MORF23 | MSR3 | 0 | 133 | Shunt Reactor | 275
|  | MORF23 | SVC3 | 174 | 197 | SVC | 275
NEART NA GAOITHE OFFSHORE WIND LIMITED | Neart na Gaoithe Offshore Wind Farm | NNGW21 | 1 | 0 | 125 | Shunt Reactor | 220
|  | NNGW22 | 1 | 0 | 125 | Shunt Reactor | 220
|  | NNGO21 | SVC1 | 79 | 74 | SVC | 220
|  | NNGO22 | SVC2 | 79 | 74 | SVC | 220
TC Ormonde OFTO Limited | Ormonde Offshore Wind Farm | ORMO31 | SR1 | 0 | 35 | Shunt Reactor | 33
|  | ORMO31 | SR2 | 0 | 35 | Shunt Reactor | 33
|  | ORMO31 | MSC1 | 15 | 0 | Mechanically Switched Capacitor | 33
|  | ORMO31 | SVC 1 | 28 | 28 | SVC | 33
Diamond Transmission Partners RB Limited | Race Bank Offshore windfarm | RACO21 | VSR1 | 0 | 200 | Shunt Reactor | 220
|  | RACO22 | VSR2 | 0 | 200 | Shunt Reactor | 220
|  | RACW21 | SR1 | 0 | 90 | Shunt Reactor | 220
|  | RACW22 | SR2 | 0 | 90 | Shunt Reactor | 220
|  | RACO21 | 1 | 120 | 120 | SVC | 220
|  | RACO22 | 2 | 120 | 120 | SVC | 220
TC Rampion OFTO Limited | Rampion Offshore Wind Farm | TWNE41 | SVC1 | 75 | 121 | SVC | 400
|  | TWNE42 | SVC2 | 75 | 121 | SVC | 400
|  | TWNE11 | SHR1 | 0 | 64 | Shunt Reactor | 150
|  | TWNE12 | SHR2 | 0 | 64 | Shunt Reactor | 150
Seagreen Wind Energy Limited | Seagreen One Wind Farm | SGRO21 | 1 | 0 | 177 | Shunt Reactor | 220
|  | SGRO22 | 2 | 0 | 177 | Shunt Reactor | 220
|  | SGRO23 | 3 | 0 | 177 | Shunt Reactor | 220
|  | SGRX21 | SVC1 | 118 | 118 | SVC | 275
|  | SGRX22 | SVC2 | 118 | 118 | SVC | 275
|  | SGRX23 | SVC3 | 118 | 118 | SVC | 275
TC Robin Rigg OFTO Limited | Robin Rigg East Offshore Wind Farm | RORE11 | 1 | 0 | 18 | Shunt Reactor | 33
|  | RORE11 | 1 | 12 | 0 | Mechanically Switched Capacitor | 33
| Robin Rigg West Offshore Wind Farm | RORW11 | 1 | 0 | 18 | Shunt Reactor | 33
|  | RORW11 | 1 | 12 | 0 | Mechanically Switched Capacitor | 33
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SALL11 | 1 | 0 | 60 | Shunt Reactor | 132
|  | SALL12 | 2 | 0 | 60 | Shunt Reactor | 132
Thanet OFTO Limited | Thanet Offshore Wind Farm | THAW11 | SVC 1 | 49.3 | 49.3 | SVC | 132
|  | THAW12 | SVC 2 | 49.3 | 49.3 | SVC | 132
Triton Knoll Wind Farm Limited | Triton Knoll Offshore Wind Farm | TKNO21 | SHR1 | 0 | 172 | Shunt Reactor | 220
|  | TKNO22 | SHR2 | 0 | 172 | Shunt Reactor | 220
|  | TKNW21 | SHR4 | 0 | 43 | Shunt Reactor | 220
|  | TKNE21 | SHR3 | 0 | 43 | Shunt Reactor | 220
|  | TKNO42 | MSR2B | 0 | 163 | Shunt Reactor | 400
|  | TKNO42 | MSR2C | 0 | 163 | Shunt Reactor | 400
|  | TKNO42 | SVC2A | 143 | 143 | SVC | 400
|  | TKNO41 | MSR1B | 0 | 163 | Shunt Reactor | 400
|  | TKNO41 | MSR1C | 0 | 163 | Shunt Reactor | 400
|  | TKNO41 | SVC1A | 143 | 143 | SVC | 400
Diamond Transmission Partners Walney Extension Limited | Walney Extension Offshore Wind Farm | WOWE41 | SHR1 | 0 | 62 | Shunt Reactor | 400
|  | WOWE21 | VSR-1 | 0 | 250 | Shunt Reactor | 220
|  | WACW21 | SHR1 | 0 | 90 | Shunt Reactor | 220
|  | WOWE21 | SVC1 | 140 | 140 | SVC | 220
|  | WOWE42 | SHR2 | 0 | 62 | Shunt Reactor | 400
|  | WOWE22 | VSR-2 | 0 | 250 | Shunt Reactor | 220
|  | WADW21 | SHR2 | 0 | 90 | Shunt Reactor | 220
|  | WOWE22 | SVC2 | 140 | 140 | SVC | 220
Blue Transmission Walney 1 OFTO Limited | Walney 1 Offshore Wind Farm | WAAO1A | RCT1 | 0 | 64 | Shunt Reactor | 132
Blue Transmission Walney 2 OFTO Limited | Walney 2 Offshore Wind Farm | WABO1A | RCT1 | 0 | 80 | Shunt Reactor | 132
WoDS Transmission plc | West of Duddon Sands Offshore Wind Farm | WDSO41 | 1A | 0 | 30 | Shunt Reactor | 400
|  | WDSO42 | 2A | 0 | 30 | Shunt Reactor | 400
|  | WDSO11 | SR3 | 0 | 60 | Shunt Reactor | 155
|  | WDSO12 | SR4 | 0 | 60 | Shunt Reactor | 155
|  | WDSO41 | SVC1 | 50 | 50 | SVC | 400
|  | WDSO42 | SVC2 | 50 | 50 | SVC | 400
TC Westermost Rough OFTO Limited | Westermost Rough Offshore Wind Farm | WERO21 | 1 | 25 | 25 | SVC | 275
|  | WERO21 | 2 | 25 | 25 | SVC | 275
|  | WERO21 | 1 | 0 | 50 | Shunt Reactor | 275

## B-4-2a
B-4-2a - SHE Transmission Reactive Compensation Equipment Changes 2025/26 to 2035/36
Site Name | Node | Unit Number | Year | Status | MVar Generation | MVar Absorption | Compensation Type | Connection Voltage (kV)
ALYTH | ALYT2A | 1 | 2027 | Removed | 100 | 0 | Mechanically Switched Capacitor | 275
ALYTH | ALYT2A | 1 | 2027 | Removed | 225 | 225 | SVC | 275
ALYTH | ALYT4J | 1 | 2027 | Addition | 100 | 0 | Mechanically Switched Capacitor | 400
ALYTH | ALYT4J | 1 | 2027 | Addition | 225 | 225 | SVC | 400
DOUNREAY | DOUN3Y | 1 | 2029 | Addition | 0 | 90 | Shunt Reactor - SGT tertiary | 33
ORKNEY FINSTOWN | FINS1- | 1 | 2029 | Addition | 70 | 35 | Sync Comp | 132
ORKNEY FINSTOWN | FINS1- | 2 | 2029 | Addition | 70 | 35 | Sync Comp | 132
BROADFORD | BROA1A | 1 | 2029 | Addition | 0 | 60 | Shunt Reactor | 132
BROADFORD | BROA1B | 1 | 2029 | Addition | 0 | 60 | Shunt Reactor | 132
EDINBANE | EDIN8A | 1 | 2029 | Addition | 125 | 50 | Sync Comp | 132
EDINBANE | EDIN8B | 1 | 2029 | Addition | 125 | 50 | Sync Comp | 132
EDINBANE | EDIN1A | 1 | 2029 | Addition | 0 | 60 | Shunt Reactor | 132
EDINBANE | EDIN1B | 1 | 2029 | Addition | 0 | 60 | Shunt Reactor | 132
KINARDOCHY | KINA2J | 1 | 2029 | Removed | 225 | 225 | SVC | 275
KINARDOCHY | KINA2K | 1 | 2029 | Removed | 100 | 0 | Mechanically Switched Capacitor | 275
KINARDOCHY | KINA4A | 1 | 2029 | Addition | 225 | 225 | SVC | 400
KINARDOCHY | KINA4B | 1 | 2029 | Addition | 100 | 0 | Mechanically Switched Capacitor | 400
ORKNEY FINSTOWN | FINS3Y | 1 | 2029 | Addition | 0 | 90 | Shunt Reactor - SGT tertiary | 33
ALYTH | ALYT4K | 1 | 2033 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
ALYTH | ALYT4K | 1 | 2033 | Addition | 225 | 225 | SVC | 400
BEAULY | BEAU2J | 1 | 2033 | Removed | 150 | 150 | SVC | 275
EMMOCK | EMMO4J | 1 | 2033 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
EMMOCK | EMMO4J | 1 | 2033 | Addition | 225 | 225 | SVC | 400
HURLIE | HURL4B | 1 | 2033 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
TEALING | TEAL2J | 1 | 2033 | Removed | 225 | 75 | SVC | 275

## B-4-2b
B-4-2b - SPT Reactive Compensation Equipment Changes 2025/26 to 2035/36
Site Name | Node | Unit Number | Year | Status | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Arecleoch Repowering Windfarm | ARCR2- | 1 | 2027 | Addition | 0 | 60 | Shunt Reactor | 275
ECCLES | ECCL4A | 1 | 2025 | Addition | 150 | 150 | STATCOM | 400
ECCLES | ECCL4A | 1 | 2025 | Addition | 150 | 70 | Sync Comp | 400
ECCLES | ECCL4B | 1 | 2025 | Addition | 150 | 150 | STATCOM | 400
ECCLES | ECCL4B | 1 | 2025 | Addition | 150 | 70 | Sync Comp | 400
Gretna | GRNA3U | 1 | 2027 | Addition | 0 | 60 | Shunt Reactor | 33
HUNE4- | HUNE4- | 1 | 2025 | Addition | 0 | 200 | Shunt Reactor | 400
Kincardine | KINC2- | 2 | 2029 | Addition | 232 | 0 | Mechanically Switched Capacitor | 275
Kincardine | KINC2- | 1 | 2029 | Addition | 232 | 0 | Mechanically Switched Capacitor | 275
Longannet | LOAN2- | 2 | 2029 | Removed | 232 | 0 | Mechanically Switched Capacitor | 275
Longannet | LOAN2- | 1 | 2029 | Removed | 232 | 0 | Mechanically Switched Capacitor | 275

## B-4-2c
B-4-2c - NGET Reactive Compensation Equipment Changes 2025/26 to 2035/36
Site Name | Node | Unit Number | Year | Status | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Cottam | COTT41 | 1 | 2025 | Addition | 0 | 200 | Shunt Reactor | 400
East Claydon | ECLA41 | 3 | 2025 | Addition | 0 | 200 | Shunt Reactor | 400
Ironbridge | IRON41 | 1 | 2025 | Addition | 0 | 200 | Shunt Reactor | 400
Mannington | MANN41 | 2 | 2025 | Addition | 150 | 95 | SVC | 400
Melksham | MELK41 | 1 | 2025 | Addition | 0 | 200 | Shunt Reactor | 400
Rowdown | ROWD41 | 1 | 2025 | Addition | 0 | 200 | Shunt Reactor | 400
Taunton | TAUN42 | 1 | 2025 | Addition | 0 | 200 | Shunt Reactor | 400
Willington East | WILE41 | 1 | 2025 | Addition | 0 | 200 | Shunt Reactor | 400
Wimbledon | WIMB21 | 2 | 2025 | Removed | 0 | 100 | Shunt Reactor | 275
Wimbledon | WIMB21 | 4 | 2025 | Removed | 0 | 100 | Shunt Reactor | 275
Harker | HARK41 | 1 | 2027 | Removed | 225 | 0 | Mechanically Switched Capacitor | 400
Harker | HARK21 | 2 | 2027 | Removed | 154 | 0 | Mechanically Switched Capacitor | 275
Harker | HARK21 | 7 | 2027 | Removed | 146 | 124 | SVC | 14
Harker | HARK21 | 8 | 2027 | Removed | 146 | 124 | SVC | 14
Harker | HARK41 | 3A | 2027 | Removed | 225 | 0 | Mechanically Switched Capacitor | 400
Harker | HARK41 | 3B | 2027 | Removed | 225 | 0 | Mechanically Switched Capacitor | 400
Harker GIS | HARG41 | 4 | 2027 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Harker GIS | HARG41 | 5A | 2027 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Harker GIS | HARG41 | 5B | 2027 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Lackenby | LACK41 | 1 | 2027 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
Norton | NORT41 | 1 | 2027 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
Spennymoor | SPEN41 | 1 | 2027 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
Penwortham | PEWO41 | 1 | 2028 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
Penwortham | PEWO41 | 2 | 2028 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
Bramford | BRFO41 | 1 | 2029 | Addition | 0 | 200 | Shunt Reactor | 400
Bramford | BRFO41 | 1 | 2029 | Addition | 0 | 200 | Shunt Reactor | 400
Chesterfield | CHTE41 | 4 | 2029 | Addition | 0 | 60 | Shunt Reactor | 400
Elstree | ELST41 | 1 | 2029 | Addition | 0 | 200 | Shunt Reactor | 400
Feckenham | FECK41 | 1 | 2029 | Addition | 0 | 230 | Shunt Reactor | 400
Harker GIS | HARG41 | 4 | 2029 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Melksham | MELK41 | 1 | 2029 | Addition | 0 | 230 | Shunt Reactor | 400
St. Johns Wood | SJOW21 | 3 | 2029 | Removed | 150 | 144 | SVC | 16
St. Johns Wood | SJOW21 | 1 | 2029 | Removed | 150 | 144 | SVC | 16
Bramford | BRFO41 | 1 | 2033 | Addition | 0 | 200 | Shunt Reactor | 400
Bramford | BRFO41 | 1 | 2033 | Addition | 0 | 200 | Shunt Reactor | 400
Cottam | COTT41 | 1 | 2033 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
Cottam | COTT41 | 1 | 2033 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
East Anglia Coastal | EACS41 | 1 | 2033 | Addition | 0 | 200 | Shunt Reactor | 400
East Anglia Coastal | EACS41 | 1 | 2033 | Addition | 0 | 200 | Shunt Reactor | 400
East Anglia Coastal | EACS41 | 1 | 2033 | Addition | 0 | 200 | Shunt Reactor | 400
East Anglia Coastal | EACS41 | 1 | 2033 | Addition | 0 | 200 | Shunt Reactor | 400
Harker GIS | HARG41 | 4 | 2033 | Addition | 459 | 0 | Mechanically Switched Capacitor | 400
Hawthorn Pit | HAWP41 | 1 | 2033 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
High Marnham-B | HIMB41 | 1 | 2033 | Addition | 450 | 0 | Mechanically Switched Capacitor | 400
High Marnham-B | HIMB41 | 1 | 2033 | Addition | 450 | 0 | Mechanically Switched Capacitor | 400
Keadby | KEAD42 | 1 | 2033 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
Ratcliffe-On-Soar | RATS41 | 1 | 2033 | Addition | 465 | 0 | Mechanically Switched Capacitor | 400
Ratcliffe-On-Soar | RATS41 | 1 | 2033 | Addition | 465 | 0 | Mechanically Switched Capacitor | 400
Ryhall | RYHA41 | 1 | 2033 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
Staythorpe | STAY41 | 1 | 2033 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
Staythorpe | STAY41 | 1 | 2033 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
Tilbury North | TILN41 | 1 | 2033 | Addition | 0 | 200 | Shunt Reactor | 400
Tilbury North | TILN41 | 1 | 2033 | Addition | 0 | 200 | Shunt Reactor | 400
Trawsfynydd | TRAW41 | 1 | 2033 | Addition | 0 | 30 | Shunt Reactor | 400
Carlisle | CARL41 | 1 | 2035 | Addition | 0 | 400 | Shunt Reactor | 400
Harker GIS | HARG41 | 1 | 2035 | Addition | 0 | 400 | Shunt Reactor | 400
Harker GIS | HARG41 | 1 | 2035 | Addition | 0 | 60 | Shunt Reactor | 400

## B-4-2d
B.4.2d - OFTO Reactive Compensation Equipment Changes 2025/26 to 2035/36
Wind Farm | Node 1 | Unit Number | Year | Status | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage(kV)
Inch Cape Offshore Wind Farm | INCO2A | SHR1 | 2025 | Addition | 0 | 215 | Shunt Reactor | 220
| INCO2A | SHR3 | 2025 | Addition | 0 | 87 | Shunt Reactor | 220
| INCW21 | SHR1 | 2025 | Addition | 0 | 215 | Shunt Reactor | 220
| INCW22 | SHR3 | 2025 | Addition | 0 | 87 | Shunt Reactor | 220
| INCO31 | SVC 1 | 2025 | Addition | 177 | 177 | SVC | 275
| INCO31 | SVC 2 | 2025 | Addition | 177 | 177 | SVC | 275
Hornsea 4A-1 Offshore Wind Farm | HOWD21 | 1 | 2027 | Addition | 0 | 100 | Shunt Reactor | 275
| HOWD21 | 2 | 2027 | Addition | 0 | 100 | Shunt Reactor | 275
| HOWD21 | 3 | 2027 | Addition | 0 | 100 | Shunt Reactor | 275
| HOWR2C | 1 | 2027 | Addition | 0 | 150 | Shunt Reactor | 275
| HOWR2C | 2 | 2027 | Addition | 0 | 150 | Shunt Reactor | 275
| HOWR2C | 3 | 2027 | Addition | 0 | 150 | Shunt Reactor | 275
| HOWD21 | 1 | 2027 | Addition | 0 | 150 | Shunt Reactor | 275
| HOWD21 | 2 | 2027 | Addition | 0 | 150 | Shunt Reactor | 275
| HOWD21 | 3 | 2027 | Addition | 0 | 150 | Shunt Reactor | 275
| HOWR2C | 1 | 2027 | Addition | 0 | 300 | Shunt Reactor | 275
| HOWR2C | 2 | 2027 | Addition | 0 | 300 | Shunt Reactor | 275
| HOWR2C | 3 | 2027 | Addition | 0 | 300 | Shunt Reactor | 275
| HOWD41 | 1 | 2027 | Addition | 0 | 75 | Shunt Reactor | 400
| HOWD41 | 1 | 2027 | Addition | TBC | TBC | SVC | 400
| HOWD41 | 2 | 2027 | Addition | TBC | TBC | SVC | 400
| HOWD41 | 3 | 2027 | Addition | TBC | TBC | SVC | 400
Pentland Floating Offshore Windfarm | Onshore 132 kV HV | SVC1 | 2027 | Addition | 40 | 40 | SVC | 132
| Onshore 132 kV HV | SHR1 | 2027 | Addition | 0 | TBC | Shunt Reactor | 132
Seagreen 1A offshore windfarm | Offshore 275kV-1 | 1 | 2027 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-1 | 1 | 2027 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 220kV-1 | 1 | 2027 | Addition | 0 | TBC | Shunt Reactor | 220
| Offshore 220kV-2 | 1 | 2027 | Addition | 0 | TBC | Shunt Reactor | 220
Berwick 1 Offshore Wind Farm | Onshore 400kV-1 | SHR1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | SHR2 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | SHR3 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 275kV-1 | SHR4 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 275kV-1 | SHR5 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 275kV-1 | SHR6 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 275kV-1 | SVC1 | 2029 | Addition | 100 | 100 | SVC | 275
| Onshore 275kV-1 | SVC2 | 2029 | Addition | 100 | 100 | SVC | 275
| Onshore 275kV-1 | SVC3 | 2029 | Addition | 100 | 100 | SVC | 275
| Offshore 275kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-3 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
Berwick 2 Offshore Wind Farm | Onshore 400kV-1 | SHR1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | SHR2 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | SHR3 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 275kV-1 | SHR4 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 275kV-1 | SHR5 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 275kV-1 | SHR6 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 275kV-1 | SVC1 | 2029 | Addition | 100 | 100 | SVC | 275
| Onshore 275kV-1 | SVC2 | 2029 | Addition | 100 | 100 | SVC | 275
| Onshore 275kV-1 | SVC3 | 2029 | Addition | 100 | 100 | SVC | 275
| Offshore 275kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-3 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
Berwick Bank Offshore Wind Farm C | Offshore 275kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2029 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2029 | Addition | TBC | TBC | SVC | 400
Cenos Central Offshore Wind Farm | Onshore 400kV-1 | 1 | 2029 | Addition | TBC | TBC | SVC | 300
| Onshore 400kV-1 | 2 | 2029 | Addition | TBC | TBC | SVC | 300
| Onshore 400kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 300
| Onshore 400kV-1 | 2 | 2029 | Addition | 0 | TBC | Shunt Reactor | 300
| Onshore 400kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 300
| Onshore 400kV-1 | 2 | 2029 | Addition | 0 | TBC | Shunt Reactor | 300
Elizabeth Yellow One Offshore Windfarm | Offshore 275kV-1 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-2 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2032 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-1 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2032 | Addition | TBC | TBC | SVC | 400
EQUINOR Offshore Windfarm | Onshore 275kV-1 | 1 | 2029 | Addition | TBC | TBC | SVC | 275
| Onshore 275kV-1 | 2 | 2029 | Addition | TBC | TBC | SVC | 275
| Onshore 275kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 275kV-1 | 2 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-1 | 2 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
Erebus Offshore Windfarm | EOWL11 | SVC1 | 2029 | Addition | 40 | 40 | SVC | 132
| EOWL11 | SHR1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 132
Green Volt Offshore Wind Farm | Offshore 220kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 220
| Offshore 220kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 220
| Onshore 400kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2029 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2029 | Addition | TBC | TBC | SVC | 400
Hornsea 4A-2 Offshore Wind Farm | HOWD21 | 4 | 2029 | Addition | 0 | 100 | Shunt Reactor | 275
| HOWD21 | 5 | 2029 | Addition | 0 | 100 | Shunt Reactor | 275
| HOWR2C | 4 | 2029 | Addition | 0 | 150 | Shunt Reactor | 275
| HOWR2C | 5 | 2029 | Addition | 0 | 150 | Shunt Reactor | 275
| HOWD21 | 4 | 2029 | Addition | 0 | 150 | Shunt Reactor | 275
| HOWD21 | 5 | 2029 | Addition | 0 | 150 | Shunt Reactor | 275
| HOWR2C | 4 | 2029 | Addition | 0 | 300 | Shunt Reactor | 275
| HOWR2C | 5 | 2029 | Addition | 0 | 300 | Shunt Reactor | 275
| HOWD41 | 2 | 2029 | Addition | 0 | 75 | Shunt Reactor | 400
| HOWD41 | 4 | 2029 | Addition | TBC | TBC | SVC | 400
| HOWD41 | 5 | 2029 | Addition | TBC | TBC | SVC | 400
Morecambe Offshore Wind Farm | Offshore 220kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 220kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2029 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2029 | Addition | TBC | TBC | SVC | 400
North Sea B(Irish Sea) Offshore Substation | Offshore 220kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 220
| Offshore 220kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 220
| Onshore 400kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2029 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2029 | Addition | TBC | TBC | SVC | 400
OWPL Offshore Windfarm | Offshore 275kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2029 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2029 | Addition | TBC | TBC | SVC | 400
Project Elizabeth Offshore Windfarm | Offshore 275kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2029 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2029 | Addition | TBC | TBC | SVC | 400
Rampion Extension Windfarm | Offshore 220kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 220
| Offshore 220kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 220
| Onshore 400kV-1 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2029 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2029 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2029 | Addition | TBC | TBC | SVC | 400
Awel Y Mor Extension Wind Farm | Offshore 220kV-1 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 220
| Offshore 220kV-2 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 220
| Onshore 400kV-1 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2032 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2032 | Addition | TBC | TBC | SVC | 400
Caledonia Offshore Wind Farm | Offshore 275kV-1 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-2 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2032 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2032 | Addition | TBC | TBC | SVC | 400
GT R4 Wind Farm | Offshore 275kV-1 | 1 | 2030 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-2 | 1 | 2030 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2030 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2030 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-1 | 1 | 2030 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2030 | Addition | TBC | TBC | SVC | 400
Llyr 1 Offshore Wind Farm | Onshore 400kV-1 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 400
Llyr 2 Offshore Wind Farm | Onshore 400kV-2 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 400
Marram Offshore Wind Farm | Onshore 275kV-1 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 275kV-2 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 275
North Falls Offshore Wind Farm | Offshore 275kV-1 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-2 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 275
Race Bank Extension Windfarm | Offshore 275kV-1 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-2 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2032 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2032 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2032 | Addition | TBC | TBC | SVC | 400
Spiorad na Mara | Offshore 275kV-1 | 1 | 2030 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-2 | 1 | 2030 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2030 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2030 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-1 | 1 | 2030 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2030 | Addition | TBC | TBC | SVC | 400
Talisk | Offshore 275kV-1 | 1 | 2030 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-1 | 1 | 2030 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2030 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2030 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-1 | 1 | 2030 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2030 | Addition | TBC | TBC | SVC | 400
Alverdiscott 2 XL Offshore Windfarm | Offshore 275kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
Ayre Offshore Wind Farm | Offshore 220kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 220
| Offshore 220kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 220
| Onshore 400kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
BELLROCK OFFSHORE WINDFARM | Offshore 220kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 220
| Offshore 220kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 220
Buchan 01 Offshore Wind Farm | Offshore 275kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
Llywelyn Extension Offshore Wind Farm | Offshore 220kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 220kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
Llywelyn Floating Offshore Wind Farm | Offshore 220kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 220kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 275
Muir Mhor Offshore Wind Farm | Offshore 220kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 220
| Offshore 220kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 220
| Onshore 400kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
NPI A offshore wind farm | Offshore 220kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 220kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
Ossian 1 Offshore Wind farm | Offshore 275kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 275
| Offshore 275kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 275
| Onshore 400kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
Ossian 2 Offshore Wind farm | Offshore 220kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 220
| Offshore 220kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 220
| Onshore 400kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
Stromar Offshore Wind Farm | Offshore 220kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 220
| Offshore 220kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 220
| Onshore 400kV-1 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-1 | 1 | 2035 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | 0 | TBC | Shunt Reactor | 400
| Onshore 400kV-2 | 1 | 2035 | Addition | TBC | TBC | SVC | 400

## B-5-1
B.5.1 - Intra GB HVDC 2024/25 to 2035/36
Interconnector Name | Existing | Planned from year | Node 1 | Node 2 | Type | Rated Voltage (kV) | Length(km) | Metallic Return | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Node 1 MVAr Gen | Node 1 MVAr Abs | Node 2 MVAr Gen | Node 2 MVAr Abs
Caithness Moray Shetland Multi-Terminal Link - Terminal 1 | Yes | Existing | SPIT2K | Central DC Substation | VSC | ±320 | 31 | No | 800 | 800 | 800 | 800 | 263 | 263 | N/A | N/A
Caithness Moray Shetland Multi-Terminal Link - Terminal 2 | Yes | Existing | BLHI4R | Central DC Substation | VSC | ±320 | 136 | No | 1200 | 1200 | 1200 | 1200 | 394 | 394 | N/A | N/A
Offshore HVDC - SCD1 (Sealink) | No | 2032 | RICH41 | SIZE41 | VSC | ±525 | 138 | No | 2000 | 2000 | 2000 | 2000 | 657 | 657 | 657 | 657
PSDC HVDC Link | No | 2030 | BANN4R | LOSD4R | VSC | ±525 | 145 | Yes | 2000 | 2000 | 2000 | 2000 | 657 | 657 | 657 | 657
Western Isles HVDC Link | No | 2030 | LEWI4R | FNLN4R | VSC | ±525 | 170 | No | 1800 | 1800 | 1800 | 1800 | 592 | 592 | 592 | 592
Shetland Hub HVDC | No | 2035 | Shetland Hub | COFD4A | VSC | ±525 | TBC | No | 1800 | 1800 | 1800 | 1800 | 592 | 592 | 592 | 592
Caithness Moray Shetland Multi-Terminal Link - Terminal 3 | Yes | Existing | KERG1J | Central DC Substation | VSC | ±320 | 269 | No | 600 | 600 | 600 | 600 | 197 | 197 | N/A | N/A
Western HVDC Link | Yes | Existing | FLIB41 | HUCS4- | LCC | ±600 | 422 | No | 2250 | 2250 | 2250 | 2250 | 1712 | 705 | 688 | 1946
Eastern Green Link 2 | No | 2029 | DRAX41 | PEHE4- | VSC | ±525 | 505 | No | 2000 | 2000 | 2000 | 2000 | 657 | 657 | 657 | 657
Eastern HVDC Link 1 | No | 2029 | BRNX4A | HAWP41 | VSC | ±525 | 193 | No | 2000 | 2000 | 2000 | 2000 | 660 | 660 | 657 | 657
Eastern HVDC Link 4 | No | 2035 | WALP41 | WFIE4A | VSC | ±525 | 525 | No | 2000 | 2000 | 2000 | 2000 | 657 | 657 | 657 | 657
HND | No | 2033 | Ballantrae | Kilmarnock South | VSC | ±525 | 69 | DC+Return | 2000 | 2000 | 2000 | 2000 | 624 | 624 | 624 | 624
Eastern HVDC Link 3 | No | 2035 | LOSD4M | WALP41 | VSC | ±525 | 575 | No | 2000 | 2000 | 2000 | 2000 | 657 | 657 | 657 | 657
Eastern Green Link 3 | No | 2033 | WALP4- | LOSD4M | VSC | ±525 | 650 | Yes | 2000 | 2000 | 2000 | 2000 | 657 | 657 | 657 | 657