## Nodes
Node Name | Relevant TO | Sheets | Voltage (Derived) | Site Name | latitude | longitude | Full Name
ABBA1- | SHET | B-2-1a | 132 | ABERDEEN BAY WINDFARM |  |  | ABERDEEN BAY WINDFARM 132kV
ABED1- | SHET | B-2-2a | 132 | ABERARDER ONSHORE WIND FARM |  |  | ABERARDER ONSHORE WIND FARM 132kV
ABHA11 | NGET | B-3-1c, B-4-1c | 132 | ABHAM | 50.4717 | -3.7309 | ABHAM 132kV
ABHA12 | NGET | B-3-1c, B-4-1c | 132 | ABHAM | 50.4717 | -3.7309 | ABHAM 132kV
ABHA4A | NGET | B-2-1c, B-3-1c | 400 | ABERTHAW | 50.4717 | -3.7309 | ABERTHAW 400kV
ABHA4B | NGET | B-2-1c, B-3-1c | 400 | ABERTHAW | 50.4717 | -3.7309 | ABERTHAW 400kV
ABNE1Q | SHET | B-2-1a, B-3-1a | 132 | ABERNETHY | 56.34 | -3.297 | ABERNETHY 132kV
ABNE1R | SHET | B-2-1a, B-3-1a | 132 | ABERNETHY | 56.34 | -3.297 | ABERNETHY 132kV
ABNE3- | SHET | B-3-1a | 33 | ABERNETHY | 56.34 | -3.297 | ABERNETHY 33kV
ABTH11 | NGET | B-3-1c, B-4-1c | 132 | ABERTHAW | 51.3883 | -3.4032 | ABERTHAW 132kV
ABTH12 | NGET | B-3-1c | 132 | ABERTHAW | 51.3883 | -3.4032 | ABERTHAW 132kV
ABTH13 | NGET | B-3-1c | 132 | ABERTHAW | 51.3883 | -3.4032 | ABERTHAW 132kV
ABTH21 | NGET | B-2-1c, B-3-1c | 275 | ABERTHAW | 51.3883 | -3.4032 | ABERTHAW 275kV
ACHE1- | SHET | B-2-2a, B-3-2a | 132 | ACHANY EXTENSION |  |  | ACHANY EXTENSION 132kV
ACHE3- | SHET | B-3-2a | 33 | ACHANY EXTENSION |  |  | ACHANY EXTENSION 33kV
AIGA1Q | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | AIGAS HYDRO | 57.4287 | -4.5772 | AIGAS HYDRO 132kV
AIGA5- | SHET | B-3-1a, B-3-2a | 11 | AIGAS HYDRO | 57.4287 | -4.5772 | AIGAS HYDRO 11kV
AIGN1- | SHET | B-2-2a, B-3-2a | 132 | AIGAS NORTH | 57.4287 | -4.5772 | AIGAS NORTH 132kV
AIGN1A | SHET | B-2-2a | 132 | AIGAS NORTH | 57.4287 | -4.5772 | AIGAS NORTH 132kV
AIGN5- | SHET | B-3-2a | 11 | AIGAS NORTH | 57.4287 | -4.5772 | AIGAS NORTH 11kV
AIKE3A | SPT | B-3-1b | 33 | AIKENGALL | 55.9085 | -2.4867 | AIKENGALL 33kV
AIKE3B | SPT | B-3-1b | 33 | AIKENGALL | 55.9085 | -2.4867 | AIKENGALL 33kV
ALDW21 | NGET | B-2-1c, B-3-1c | 275 | ALDWARKE | 53.4455 | -1.3206 | ALDWARKE 275kV
ALDW31 | NGET | B-3-1c | 33 | ALDWARKE | 53.4455 | -1.3206 | ALDWARKE 33kV
ALDW32 | NGET | B-3-1c | 33 | ALDWARKE | 53.4455 | -1.3206 | ALDWARKE 33kV
ALNE1Q | SHET | B-2-1a, B-3-1a | 132 | ALNESS GSP | 57.7082 | -4.2754 | ALNESS GSP 132kV
ALNE1R | SHET | B-2-1a, B-3-1a | 132 | ALNESS GSP | 57.7082 | -4.2754 | ALNESS GSP 132kV
ALNE3J | SHET | B-3-1a | 33 | ALNESS GSP | 57.7082 | -4.2754 | ALNESS GSP 33kV
ALST31 | NGET | B-3-1c | 33 | ALPHA STEEL | 51.547 | -2.9786 | ALPHA STEEL 33kV
ALST32 | NGET | B-3-1c | 33 | ALPHA STEEL | 51.547 | -2.9786 | ALPHA STEEL 33kV
ALVE11 | NGET | B-3-1c, B-3-2c, B-4-1c | 132 | ALVERDISCOTT | 51.0059 | -4.1365 | ALVERDISCOTT 132kV
ALVE41 | NGET | B-3-2c | 400 | ALVERDISCOTT | 51.0059 | -4.1365 | ALVERDISCOTT 400kV
ALVE4A | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 400 | ALVERDISCOTT | 51.0059 | -4.1365 | ALVERDISCOTT 400kV
ALVE4B | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 400 | ALVERDISCOTT | 51.0059 | -4.1365 | ALVERDISCOTT 400kV
ALYT2A | SHET | B-2-1a, B-2-2a, B-3-2a, B-4-1a, B-4-2a | 275 | ALYTH | 56.609 | -3.1651 | ALYTH 275kV
ALYT2B | SHET | B-2-1a, B-2-2a, B-3-2a | 275 | ALYTH | 56.609 | -3.1651 | ALYTH 275kV
ALYT4J | SHET | B-2-2a, B-3-2a, B-4-2a | 400 | ALYTH | 56.609 | -3.1651 | ALYTH 400kV
ALYT4K | SHET | B-2-2a, B-3-2a | 400 | ALYTH | 56.609 | -3.1651 | ALYTH 400kV
AMEM11 | NGET | B-3-1c | 132 | AMERSHAM MAIN | 51.6652 | -0.65634 | AMERSHAM MAIN 132kV
AMEM4A | NGET | B-2-1c, B-3-1c | 400 | AMERSHAM MAIN | 51.6652 | -0.65634 | AMERSHAM MAIN 400kV
AMEM4B | NGET | B-2-1c, B-3-1c | 400 | AMERSHAM MAIN | 51.6652 | -0.65634 | AMERSHAM MAIN 400kV
AMUL1E | SHET | B-2-1a | 132 | AMULREE |  |  | AMULREE 132kV
AMUL1F | SHET | B-2-1a | 132 | AMULREE |  |  | AMULREE 132kV
AMUL1G | SHET | B-2-1a | 132 | AMULREE |  |  | AMULREE 132kV
AMUL1H | SHET | B-2-1a | 132 | AMULREE |  |  | AMULREE 132kV
ANSN2- | SHET | B-2-2a, B-3-2a | 275 | AN SUIDHE NORTH | 56.198 | -5.1456 | AN SUIDHE NORTH 275kV
ANSN3- | SHET | B-3-2a | 33 | AN SUIDHE NORTH | 56.198 | -5.1456 | AN SUIDHE NORTH 33kV
ANSU1- | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | AN SUIDHE | 56.198 | -5.1456 | AN SUIDHE 132kV
ANSU3- | SHET | B-3-1a, B-3-2a | 33 | AN SUIDHE | 56.198 | -5.1456 | AN SUIDHE 33kV
ARBR1Q | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | ARBROATH | 56.5642 | -2.6202 | ARBROATH 132kV
ARBR1R | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | ARBROATH | 56.5642 | -2.6202 | ARBROATH 132kV
ARBR3- | SHET | B-3-1a, B-3-2a | 33 | ARBROATH | 56.5642 | -2.6202 | ARBROATH 33kV
ARCR2- | SPT | B-2-2b, B-3-2b, B-4-2b | 275 | ARECLEOCH REPOWERING | 56.5144 | -3.0428 | ARECLEOCH REPOWERING 275kV
ARCR3A | SPT | B-3-2b | 33 | ARECLEOCH REPOWERING | 56.5144 | -3.0428 | ARECLEOCH REPOWERING 33kV
ARCR3B | SPT | B-3-2b | 33 | ARECLEOCH REPOWERING | 56.5144 | -3.0428 | ARECLEOCH REPOWERING 33kV
ARDK1- | SHET | B-2-1a, B-3-1a | 132 | ARDKINGLAS WIND | 56.2772 | -4.9218 | ARDKINGLAS WIND 132kV
ARDK3K | SHET | B-3-1a | 33 | ARDKINGLAS WIND | 56.2772 | -4.9218 | ARDKINGLAS WIND 33kV
AREC1- | SPT | B-2-1b, B-3-1b | 132 | ARECLEOCH | 55.0843 | -4.851 | ARECLEOCH 132kV
AREC3- | SPT | B-2-1b, B-3-1b | 33 | ARECLEOCH | 55.0843 | -4.851 | ARECLEOCH 33kV
AREC3A | SPT | B-3-1b | 33 | ARECLEOCH | 55.0843 | -4.851 | ARECLEOCH 33kV
AREC3B | SPT | B-3-1b | 33 | ARECLEOCH | 55.0843 | -4.851 | ARECLEOCH 33kV
AREX1- | SPT | B-2-2b, B-3-2b | 132 | ARECLEOCH EXTENSION | 56.5144 | -3.0428 | ARECLEOCH EXTENSION 132kV
AREX1A | SPT | B-2-2b | 132 | ARECLEOCH EXTENSION | 56.5144 | -3.0428 | ARECLEOCH EXTENSION 132kV
AREX3- | SPT | B-3-2b | 33 | ARECLEOCH EXTENSION | 56.5144 | -3.0428 | ARECLEOCH EXTENSION 33kV
ARFO1- | SPT | B-2-2b | 132 | ARTFIELD FOREST WF |  |  | ARTFIELD FOREST WF 132kV
ARMA1- | SHET | B-2-2a | 132 | ARMADALE | 55.8941 | -3.6966 | ARMADALE 132kV
ARMO1J | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | ARDMORE | 57.5544 | -6.6447 | ARDMORE 132kV
ARMO3- | SHET | B-3-1a | 33 | ARDMORE | 57.5544 | -6.6447 | ARDMORE 33kV
ARRS1- | SPT | B-2-2b | 132 | ARRESGILL |  |  | ARRESGILL 132kV
ASBS1- | SHET | B-3-2a | 132 | ALYTH SOLAR AND BATTERY STORAGE | 56.609 | -3.1651 | ALYTH SOLAR AND BATTERY STORAGE 132kV
ASBS4B | SHET | B-2-2a, B-3-2a | 400 | ALYTH SOLAR AND BATTERY STORAGE | 56.609 | -3.1651 | ALYTH SOLAR AND BATTERY STORAGE 400kV
AUBU1- | SPT | B-2-2b | 132 | AUCHENMADY BURN |  |  | AUCHENMADY BURN 132kV
AUCH2- | SPT | B-2-1b | 275 | AUCHENCROSH | 55.0707 | -4.9801 | AUCHENCROSH 275kV
AUCW1- | SPT | B-2-1b | 132 | AUCHENWYND | 55.3422 | -4.6844 | AUCHENWYND 132kV
AXMI11 | NGET | B-3-1c | 132 | AXMINSTER | 50.7865 | -2.9246 | AXMINSTER 132kV
AXMI41 | NGET | B-2-1c, B-3-1c | 400 | AXMINSTER | 50.7865 | -2.9246 | AXMINSTER 400kV
AYR-2Q | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | AYR | 55.4575 | -4.5881 | AYR 275kV
AYR-2R | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | AYR | 55.4575 | -4.5881 | AYR 275kV
AYR-3- | SPT | B-3-1b | 33 | AYR | 55.4575 | -4.5881 | AYR 33kV
AYRS4- | SPT | B-2-2b | 400 | AYRSHIRE GRID COLLECTOR | 55.4575 | -4.5881 | AYRSHIRE GRID COLLECTOR 400kV
BAGA1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | BATHGATE | 55.9002 | -3.6734 | BATHGATE 132kV
BAGA1R | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | BATHGATE | 55.9002 | -3.6734 | BATHGATE 132kV
BAGA3- | SPT | B-3-1b | 33 | BATHGATE | 55.9002 | -3.6734 | BATHGATE 33kV
BAGB21 | NGET | B-2-1c | 275 | BAGLAN BAY | 51.617 | -3.8325 | BAGLAN BAY 275kV
BAGP2- | SHET | B-2-2a | 275 | BAILLIE GREENER GRID PARK | 57.0854 | -2.3465 | BAILLIE GREENER GRID PARK 275kV
BAGP2J | SHET | B-2-2a | 275 | BAILLIE GREENER GRID PARK | 57.0854 | -2.3465 | BAILLIE GREENER GRID PARK 275kV
BAGP2K | SHET | B-2-2a | 275 | BAILLIE GREENER GRID PARK | 57.0854 | -2.3465 | BAILLIE GREENER GRID PARK 275kV
BAIN1Q | SPT | B-2-1b, B-3-1b | 132 | BAINSFORD | 56.0143 | -3.7688 | BAINSFORD 132kV
BAIN1R | SPT | B-2-1b, B-3-1b | 132 | BAINSFORD | 56.0143 | -3.7688 | BAINSFORD 132kV
BAIN3- | SPT | B-3-1b | 33 | BAINSFORD | 56.0143 | -3.7688 | BAINSFORD 33kV
BALA1A | SHET | B-2-2a | 132 | BALALLAN | 52.9201 | -3.5861 | BALALLAN 132kV
BALA1B | SHET | B-2-2a | 132 | BALALLAN | 52.9201 | -3.5861 | BALALLAN 132kV
BANN4J | SHET | B-2-2a, B-3-2a | 400 | BANNISKIRK |  |  | BANNISKIRK 400kV
BANN4K | SHET | B-2-2a, B-3-2a | 400 | BANNISKIRK |  |  | BANNISKIRK 400kV
BANN4R | SHET | B-2-2a | 400 | BANNISKIRK |  |  | BANNISKIRK 400kV
BARK11 | NGET | B-3-1c | 132 | BARKING | 51.5226 | 0.11536 | BARKING 132kV
BARK21 | NGET | B-2-1c, B-3-1c | 275 | BARKING | 51.5226 | 0.11536 | BARKING 275kV
BARK22 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | BARKING | 51.5226 | 0.11536 | BARKING 275kV
BARK41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | BARKING | 51.5226 | 0.11536 | BARKING 400kV
BARW31 | NGET | B-3-1c | 33 | BARKING WEST | 51.5202 | 0.11548 | BARKING WEST 33kV
BARW32 | NGET | B-3-1c | 33 | BARKING WEST | 51.5202 | 0.11548 | BARKING WEST 33kV
BEAT4- | SHET | B-2-1a | 400 | BEATRICE ONSHORE |  |  | BEATRICE ONSHORE 400kV
BEAT4- | SHET | B-2-1a | 400 | BEATRICE ONSHORE |  |  | BEATRICE ONSHORE 400kV
BEAU1J | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a, B-4-1a | 132 | BEAULY | 57.4699 | -4.49 | BEAULY 132kV
BEAU1K | SHET | B-2-1a, B-2-2a, B-3-1a, B-4-1a | 132 | BEAULY | 57.4699 | -4.49 | BEAULY 132kV
BEAU1L | SHET | B-2-1a | 132 | BEAULY | 57.4699 | -4.49 | BEAULY 132kV
BEAU1M | SHET | B-2-1a | 132 | BEAULY | 57.4699 | -4.49 | BEAULY 132kV
BEAU1N | SHET | B-2-1a, B-2-2a | 132 | BEAULY | 57.4699 | -4.49 | BEAULY 132kV
BEAU1P | SHET | B-2-1a, B-3-1a | 132 | BEAULY | 57.4699 | -4.49 | BEAULY 132kV
BEAU1Q | SHET | B-2-1a, B-3-1a | 132 | BEAULY | 57.4699 | -4.49 | BEAULY 132kV
BEAU1R | SHET | B-2-1a | 132 | BEAULY | 57.4699 | -4.49 | BEAULY 132kV
BEAU1S | SHET | B-2-1a | 132 | BEAULY | 57.4699 | -4.49 | BEAULY 132kV
BEAU1T | SHET | B-2-1a, B-2-2a | 132 | BEAULY | 57.4699 | -4.49 | BEAULY 132kV
BEAU2J | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a, B-4-1a | 275 | BEAULY | 57.4699 | -4.49 | BEAULY 275kV
BEAU2K | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | BEAULY | 57.4699 | -4.49 | BEAULY 275kV
BEAU3- | SHET | B-3-1a | 33 | BEAULY | 57.4699 | -4.49 | BEAULY 33kV
BEAU3U | SHET | B-4-1a | 33 | BEAULY | 57.4699 | -4.49 | BEAULY 33kV
BEAU3V | SHET | B-4-1a | 33 | BEAULY | 57.4699 | -4.49 | BEAULY 33kV
BEAU4- | SHET | B-2-1a, B-2-2a, B-3-1a | 400 | BEAULY | 57.4699 | -4.49 | BEAULY 400kV
BEDD11 | NGET | B-3-1c | 132 | BEDDINGTON | 51.3726 | -0.12647 | BEDDINGTON 132kV
BEDD12 | NGET | B-3-1c | 132 | BEDDINGTON | 51.3726 | -0.12647 | BEDDINGTON 132kV
BEDD21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | BEDDINGTON | 51.3726 | -0.12647 | BEDDINGTON 275kV
BEDD22 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | BEDDINGTON | 51.3726 | -0.12647 | BEDDINGTON 275kV
BEDD23 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | BEDDINGTON | 51.3726 | -0.12647 | BEDDINGTON 275kV
BEDD4A | NGET | B-2-1c, B-3-1c | 400 | BEDDINGTON | 51.3726 | -0.12647 | BEDDINGTON 400kV
BEDD4B | NGET | B-2-1c, B-3-1c | 400 | BEDDINGTON | 51.3726 | -0.12647 | BEDDINGTON 400kV
BEDT1A | NGET | B-3-1c | 132 | BEDDINGTON TEE | 51.373 | -0.12795 | BEDDINGTON TEE 132kV
BEDT1B | NGET | B-3-1c | 132 | BEDDINGTON TEE | 51.373 | -0.12795 | BEDDINGTON TEE 132kV
BEIN11 | SHET | B-2-1a, B-3-1a | 132 | BEINNEUN WIND FARM | 57.1539 | -4.8701 | BEINNEUN WIND FARM 132kV
BEIN31 | SHET | B-3-1a | 33 | BEINNEUN WIND FARM | 57.1539 | -4.8701 | BEINNEUN WIND FARM 33kV
BENB1- | SPT | B-2-2b, B-3-2b | 132 | BENBRACK WIND FARM |  |  | BENBRACK WIND FARM 132kV
BENB1T | SPT | B-2-2b | 132 | BENBRACK WIND FARM |  |  | BENBRACK WIND FARM 132kV
BENB3- | SPT | B-3-2b | 33 | BENBRACK WIND FARM |  |  | BENBRACK WIND FARM 33kV
BENR11 | NGET | B-3-2c | 132 | BENGEWORTH ROAD | 51.4658 | -0.098387 | BENGEWORTH ROAD 132kV
BENR41 | NGET | B-2-2c, B-3-2c | 400 | BENGEWORTH ROAD | 51.4658 | -0.098387 | BENGEWORTH ROAD 400kV
BERB2Q | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | BERRY BURN | 57.5041 | -3.6001 | BERRY BURN 275kV
BERB3- | SHET | B-3-1a | 33 | BERRY BURN | 57.5041 | -3.6001 | BERRY BURN 33kV
BERW1Q | SPT | B-2-1b, B-3-1b | 132 | BERWICK | 55.7777 | -2.0777 | BERWICK 132kV
BERW1R | SPT | B-2-1b, B-3-1b | 132 | BERWICK | 55.7777 | -2.0777 | BERWICK 132kV
BERW3- | SPT | B-3-1b | 33 | BERWICK | 55.7777 | -2.0777 | BERWICK 33kV
BESW11 | NGET | B-3-1c, B-4-1c | 132 | BERKSWELL | 52.3859 | -1.6155 | BERKSWELL 132kV
BESW12 | NGET | B-3-1c, B-4-1c | 132 | BERKSWELL | 52.3859 | -1.6155 | BERKSWELL 132kV
BESW21 | NGET | B-2-1c, B-3-1c | 275 | BERKSWELL | 52.3859 | -1.6155 | BERKSWELL 275kV
BEWF1- | SHET | B-2-2a, B-3-2a | 132 | BEAW FIELD |  |  | BEAW FIELD 132kV
BEWF3- | SHET | B-3-2a | 33 | BEAW FIELD |  |  | BEAW FIELD 33kV
BHLA11 | SHET | B-2-1a, B-3-1a | 132 | BHLARAIDH WIND FARM | 57.2446 | -4.704 | BHLARAIDH WIND FARM 132kV
BHLA31 | SHET | B-3-1a | 33 | BHLARAIDH WIND FARM | 57.2446 | -4.704 | BHLARAIDH WIND FARM 33kV
BICF11 | NGET | B-3-1c | 132 | BICKER FEN | 52.9308 | -0.22118 | BICKER FEN 132kV
BICF41 | NGET | B-2-1c, B-3-1c | 400 | BICKER FEN | 52.9308 | -0.22118 | BICKER FEN 400kV
BIGG11 | NGET | B-3-1c | 132 | BIGGLESWADE | 52.0814 | -0.26357 | BIGGLESWADE 132kV
BIGG41 | NGET | B-2-1c, B-3-1c | 400 | BIGGLESWADE | 52.0814 | -0.26357 | BIGGLESWADE 400kV
BIHI1Q | SHET | B-2-1a | 132 | BIRKHILL |  |  | BIRKHILL 132kV
BIHI1R | SHET | B-2-1a | 132 | BIRKHILL |  |  | BIRKHILL 132kV
BING4- | SHET | B-2-2a, B-3-2a | 400 | BINGALLY |  |  | BINGALLY 400kV
BIRK11 | NGET | B-3-1c | 132 | BIRKENHEAD | 53.3657 | -3.0627 | BIRKENHEAD 132kV
BIRK21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | BIRKENHEAD | 53.3657 | -3.0627 | BIRKENHEAD 275kV
BISW11 | NGET | B-3-1c, B-4-1c | 132 | BISHOPS WOOD | 52.3121 | -2.2417 | BISHOPS WOOD 132kV
BISW21 | NGET | B-2-1c, B-3-1c | 275 | BISHOPS WOOD | 52.3121 | -2.2417 | BISHOPS WOOD 275kV
BLAH1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | BLACKHILL | 57.5218 | -2.9515 | BLACKHILL 132kV
BLAH3A | SPT | B-3-1b | 33 | BLACKHILL | 57.5218 | -2.9515 | BLACKHILL 33kV
BLAH3B | SPT | B-2-2b, B-3-1b | 33 | BLACKHILL | 57.5218 | -2.9515 | BLACKHILL 33kV
BLBS3- | SHET | B-3-2a | 33 | BLACKHILLOCK BATTERY STORAGE | 57.5251 | -2.9484 | BLACKHILLOCK BATTERY STORAGE 33kV
BLBS4- | SHET | B-3-2a | 400 | BLACKHILLOCK BATTERY STORAGE | 57.5251 | -2.9484 | BLACKHILLOCK BATTERY STORAGE 400kV
BLCW1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | BLACKCRAIG | 55.1291 | -4.0572 | BLACKCRAIG 132kV
BLCW3- | SPT | B-2-1b, B-2-2b, B-3-1b | 33 | BLACKCRAIG | 55.1291 | -4.0572 | BLACKCRAIG 33kV
BLEX1- | SHET | B-2-2a, B-3-2a | 132 | BHLARAIDH EXTENSION | 57.2446 | -4.704 | BHLARAIDH EXTENSION 132kV
BLEX1A | SHET | B-2-2a | 132 | BHLARAIDH EXTENSION | 57.2446 | -4.704 | BHLARAIDH EXTENSION 132kV
BLEX1B | SHET | B-2-2a | 132 | BHLARAIDH EXTENSION | 57.2446 | -4.704 | BHLARAIDH EXTENSION 132kV
BLEX3- | SHET | B-3-2a | 33 | BHLARAIDH EXTENSION | 57.2446 | -4.704 | BHLARAIDH EXTENSION 33kV
BLGH1- | SHET | B-2-2a | 132 | BLARGHOUR |  |  | BLARGHOUR 132kV
BLHI1J | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | BLACKHILLOCK | 57.5251 | -2.9484 | BLACKHILLOCK 132kV
BLHI1K | SHET | B-2-1a, B-3-1a | 132 | BLACKHILLOCK | 57.5251 | -2.9484 | BLACKHILLOCK 132kV
BLHI2A | SHET | B-2-2a, B-3-2a | 275 | BLACKHILLOCK | 57.5251 | -2.9484 | BLACKHILLOCK 275kV
BLHI2B | SHET | B-2-2a, B-3-2a | 275 | BLACKHILLOCK | 57.5251 | -2.9484 | BLACKHILLOCK 275kV
BLHI2J | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 275 | BLACKHILLOCK | 57.5251 | -2.9484 | BLACKHILLOCK 275kV
BLHI2K | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 275 | BLACKHILLOCK | 57.5251 | -2.9484 | BLACKHILLOCK 275kV
BLHI4- | SHET | B-2-1a, B-2-2a, B-3-1a | 400 | BLACKHILLOCK | 57.5251 | -2.9484 | BLACKHILLOCK 400kV
BLHI4R | SHET | B-2-1a | 400 | BLACKHILLOCK | 57.5251 | -2.9484 | BLACKHILLOCK 400kV
BLKL1- | SPT | B-2-1b, B-3-1b | 132 | BLACKLAW |  |  | BLACKLAW 132kV
BLKL3A | SPT | B-3-1b | 33 | BLACKLAW |  |  | BLACKLAW 33kV
BLKL3B | SPT | B-3-1b | 33 | BLACKLAW |  |  | BLACKLAW 33kV
BLKS3- | SPT | B-2-1b, B-2-2b | 33 | BLACKCRAIG SOUTH | 55.1291 | -4.0572 | BLACKCRAIG SOUTH 33kV
BLLX1- | SPT | B-2-1b, B-3-1b | 132 | BLACKLAW EXTENSION | 55.7926 | -3.7379 | BLACKLAW EXTENSION 132kV
BLLX3- | SPT | B-3-1b | 33 | BLACKLAW EXTENSION | 55.7926 | -3.7379 | BLACKLAW EXTENSION 33kV
BLYT1A | NGET | B-3-1c | 132 | BLYTH | 55.1412 | -1.5306 | BLYTH 132kV
BLYT1B | NGET | B-3-1c | 132 | BLYTH | 55.1412 | -1.5306 | BLYTH 132kV
BLYT21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | BLYTH | 55.1412 | -1.5306 | BLYTH 275kV
BLYT22 | NGET | B-2-1c | 275 | BLYTH | 55.1412 | -1.5306 | BLYTH 275kV
BLYT23 | NGET | B-2-1c | 275 | BLYTH | 55.1412 | -1.5306 | BLYTH 275kV
BLYT41 | NGET | B-3-1c | 400 | BLYTH | 55.1412 | -1.5306 | BLYTH 400kV
BLYT61 | NGET | B-3-1c | 66 | BLYTH | 55.1412 | -1.5306 | BLYTH 66kV
BOAG1L | SHET | B-2-1a | 132 | BOAT OF GARTEN | 57.2541 | -3.7317 | BOAT OF GARTEN 132kV
BOAG1M | SHET | B-2-1a | 132 | BOAT OF GARTEN | 57.2541 | -3.7317 | BOAT OF GARTEN 132kV
BOAG1P | SHET | B-2-1a | 132 | BOAT OF GARTEN | 57.2541 | -3.7317 | BOAT OF GARTEN 132kV
BOAG1Q | SHET | B-2-1a, B-3-1a | 132 | BOAT OF GARTEN | 57.2541 | -3.7317 | BOAT OF GARTEN 132kV
BOAG1R | SHET | B-2-1a, B-3-1a | 132 | BOAT OF GARTEN | 57.2541 | -3.7317 | BOAT OF GARTEN 132kV
BOAG3- | SHET | B-3-1a | 33 | BOAT OF GARTEN | 57.2541 | -3.7317 | BOAT OF GARTEN 33kV
BODE41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | BODELWYDDAN | 53.2501 | -3.4761 | BODELWYDDAN 400kV
BOLN11 | NGET | B-3-1c, B-4-1c | 132 | BOLNEY | 50.9752 | -0.23508 | BOLNEY 132kV
BOLN12 | NGET | B-3-1c, B-4-1c | 132 | BOLNEY | 50.9752 | -0.23508 | BOLNEY 132kV
BOLN41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | BOLNEY | 50.9752 | -0.23508 | BOLNEY 400kV
BONB2J | SHET, SPT | B-2-1a, B-2-1b, B-2-2a, B-2-2b | 275 | BONNYBRIDGE BORDER NODE | 56.0078 | -3.8607 | BONNYBRIDGE BORDER NODE 275kV
BONB2J | SHET, SPT | B-2-1a, B-2-1b, B-2-2a, B-2-2b | 275 | BONNYBRIDGE BORDER NODE | 56.0078 | -3.8607 | BONNYBRIDGE BORDER NODE 275kV
BONB4- | SHET, SPT | B-2-1a, B-2-1b, B-2-2b | 400 | BONNYBRIDGE BORDER NODE | 56.0078 | -3.8607 | BONNYBRIDGE BORDER NODE 400kV
BONB4- | SHET, SPT | B-2-1a, B-2-1b, B-2-2b | 400 | BONNYBRIDGE BORDER NODE | 56.0078 | -3.8607 | BONNYBRIDGE BORDER NODE 400kV
BONB4A | SHET, SPT | B-2-2a, B-2-2b | 400 | BONNYBRIDGE BORDER NODE | 56.0078 | -3.8607 | BONNYBRIDGE BORDER NODE 400kV
BONB4A | SHET, SPT | B-2-2a, B-2-2b | 400 | BONNYBRIDGE BORDER NODE | 56.0078 | -3.8607 | BONNYBRIDGE BORDER NODE 400kV
BONN1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | BONNYBRIDGE | 56.0078 | -3.8607 | BONNYBRIDGE 132kV
BONN2A | SPT | B-2-1b, B-3-1b | 275 | BONNYBRIDGE | 56.0078 | -3.8607 | BONNYBRIDGE 275kV
BONN2B | SPT | B-2-1b, B-3-1b | 275 | BONNYBRIDGE | 56.0078 | -3.8607 | BONNYBRIDGE 275kV
BONN3- | SPT | B-3-1b | 33 | BONNYBRIDGE | 56.0078 | -3.8607 | BONNYBRIDGE 33kV
BONN3U | SPT | B-4-1b | 33 | BONNYBRIDGE | 56.0078 | -3.8607 | BONNYBRIDGE 33kV
BONN3V | SPT | B-4-1b | 33 | BONNYBRIDGE | 56.0078 | -3.8607 | BONNYBRIDGE 33kV
BOTW11 | NGET | B-3-1c | 132 | BOTLEY WOOD | 50.8845 | -1.2321 | BOTLEY WOOD 132kV
BOTW41 | NGET | B-2-1c, B-3-1c | 400 | BOTLEY WOOD | 50.8845 | -1.2321 | BOTLEY WOOD 400kV
BPGR3J | SPT | B-3-1b | 33 | BP GRANGEMOUTH | 51.5604 | -3.7546 | BP GRANGEMOUTH 33kV
BPGR3K | SPT | B-3-1b | 33 | BP GRANGEMOUTH | 51.5604 | -3.7546 | BP GRANGEMOUTH 33kV
BRAI11 | NGET | B-3-1c | 132 | BRAINTREE | 51.8649 | 0.57634 | BRAINTREE 132kV
BRAI4A | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | BRAINTREE | 51.8649 | 0.57634 | BRAINTREE 400kV
BRAI4B | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | BRAINTREE | 51.8649 | 0.57634 | BRAINTREE 400kV
BRAP1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | BRAEHEAD PARK | 55.8813 | -4.3815 | BRAEHEAD PARK 132kV
BRAP3- | SPT | B-3-1b | 33 | BRAEHEAD PARK | 55.8813 | -4.3815 | BRAEHEAD PARK 33kV
BRAW11 | NGET | B-3-1c, B-4-1c | 132 | BRADFORD WEST | 53.8105 | -1.8653 | BRADFORD WEST 132kV
BRAW12 | NGET | B-3-1c | 132 | BRADFORD WEST | 53.8105 | -1.8653 | BRADFORD WEST 132kV
BRAW21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | BRADFORD WEST | 53.8105 | -1.8653 | BRADFORD WEST 275kV
BRAW4A | NGET | B-2-1c, B-3-1c | 400 | BRADFORD WEST | 53.8105 | -1.8653 | BRADFORD WEST 400kV
BRCW1A | SHET | B-3-2a | 132 | BRACO WEST | 56.2613 | -3.9471 | BRACO WEST 132kV
BRCW1B | SHET | B-3-2a | 132 | BRACO WEST | 56.2613 | -3.9471 | BRACO WEST 132kV
BRCW2J | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 275 | BRACO WEST | 56.2613 | -3.9471 | BRACO WEST 275kV
BRCW2K | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 275 | BRACO WEST | 56.2613 | -3.9471 | BRACO WEST 275kV
BRCW3- | SHET | B-3-1a, B-3-2a | 33 | BRACO WEST | 56.2613 | -3.9471 | BRACO WEST 33kV
BREC1Q | SHET | B-2-1a, B-2-2a | 132 | BRECHIN | 56.7401 | -2.6287 | BRECHIN 132kV
BREC1R | SHET | B-2-1a | 132 | BRECHIN | 56.7401 | -2.6287 | BRECHIN 132kV
BRED11 | NGET | B-3-1c | 132 | BREDBURY | 53.4145 | -2.1289 | BREDBURY 132kV
BRED21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | BREDBURY | 53.4145 | -2.1289 | BREDBURY 275kV
BREE1- | SPT | B-2-2b | 132 | BREEZY HILL |  |  | BREEZY HILL 132kV
BRFO11 | NGET | B-3-1c, B-4-1c | 132 | BRAMFORD | 52.0713 | 1.0621 | BRAMFORD 132kV
BRFO12 | NGET | B-3-1c | 132 | BRAMFORD | 52.0713 | 1.0621 | BRAMFORD 132kV
BRFO41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c, B-4-2c | 400 | BRAMFORD | 52.0713 | 1.0621 | BRAMFORD 400kV
BRID1Q | SHET | B-2-1a, B-3-1a | 132 | BRIDGE OF DUN | 56.7202 | -2.557 | BRIDGE OF DUN 132kV
BRID1R | SHET | B-2-1a, B-3-1a | 132 | BRIDGE OF DUN | 56.7202 | -2.557 | BRIDGE OF DUN 132kV
BRID3- | SHET | B-3-1a | 33 | BRIDGE OF DUN | 56.7202 | -2.557 | BRIDGE OF DUN 33kV
BRIM11 | NGET | B-3-1c, B-3-2c | 132 | BRIMSDOWN | 51.6635 | -0.02494 | BRIMSDOWN 132kV
BRIM2A | NGET | B-2-1c, B-2-2c, B-3-1c | 275 | BRIMSDOWN | 51.6635 | -0.02494 | BRIMSDOWN 275kV
BRIM2B | NGET | B-2-1c, B-2-2c, B-3-1c | 275 | BRIMSDOWN | 51.6635 | -0.02494 | BRIMSDOWN 275kV
BRIM2C | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 275 | BRIMSDOWN | 51.6635 | -0.02494 | BRIMSDOWN 275kV
BRIM2D | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 275 | BRIMSDOWN | 51.6635 | -0.02494 | BRIMSDOWN 275kV
BRIM4C | NGET | B-2-2c, B-3-2c | 400 | BRIMSDOWN | 51.6635 | -0.02494 | BRIMSDOWN 400kV
BRIM4D | NGET | B-2-2c, B-3-2c | 400 | BRIMSDOWN | 51.6635 | -0.02494 | BRIMSDOWN 400kV
BRIN21 | NGET | B-2-1c, B-2-2c, B-3-1c | 275 | BRINSWORTH | 53.4015 | -1.352 | BRINSWORTH 275kV
BRIN22 | NGET | B-2-1c, B-2-2c, B-3-1c | 275 | BRINSWORTH | 53.4015 | -1.352 | BRINSWORTH 275kV
BRIN41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | BRINSWORTH | 53.4015 | -1.352 | BRINSWORTH 400kV
BRLE11 | NGET | B-3-1c | 132 | BRAMLEY | 51.3361 | -1.0773 | BRAMLEY 132kV
BRLE12 | NGET | B-3-1c | 132 | BRAMLEY | 51.3361 | -1.0773 | BRAMLEY 132kV
BRLE13 | NGET | B-3-1c | 132 | BRAMLEY | 51.3361 | -1.0773 | BRAMLEY 132kV
BRLE14 | NGET | B-3-1c | 132 | BRAMLEY | 51.3361 | -1.0773 | BRAMLEY 132kV
BRLE1A | NGET | B-3-1c | 132 | BRAMLEY | 51.3361 | -1.0773 | BRAMLEY 132kV
BRLE1B | NGET | B-3-1c | 132 | BRAMLEY | 51.3361 | -1.0773 | BRAMLEY 132kV
BRLE41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | BRAMLEY | 51.3361 | -1.0773 | BRAMLEY 400kV
BRNX4- | SPT | B-2-2b | 400 | BRANXTON | 55.9485 | -2.4168 | BRANXTON 400kV
BRNX4A | SPT | B-2-2b | 400 | BRANXTON | 55.9485 | -2.4168 | BRANXTON 400kV
BRNX4Q | SPT | B-2-2b | 400 | BRANXTON | 55.9485 | -2.4168 | BRANXTON 400kV
BRNX4R | SPT | B-2-2b | 400 | BRANXTON | 55.9485 | -2.4168 | BRANXTON 400kV
BROA1- | SHET | B-2-2a, B-3-2a | 132 | BROADFORD | 53.8029 | -1.7526 | BROADFORD 132kV
BROA1A | SHET | B-2-2a, B-4-2a | 132 | BROADFORD | 53.8029 | -1.7526 | BROADFORD 132kV
BROA1B | SHET | B-2-2a, B-4-2a | 132 | BROADFORD | 53.8029 | -1.7526 | BROADFORD 132kV
BROA1C | SHET | B-2-2a | 132 | BROADFORD | 53.8029 | -1.7526 | BROADFORD 132kV
BROA1D | SHET | B-2-2a | 132 | BROADFORD | 53.8029 | -1.7526 | BROADFORD 132kV
BROA1J | SHET | B-2-2a | 132 | BROADFORD | 53.8029 | -1.7526 | BROADFORD 132kV
BROA1K | SHET | B-2-2a | 132 | BROADFORD | 53.8029 | -1.7526 | BROADFORD 132kV
BROA1Q | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | BROADFORD | 53.8029 | -1.7526 | BROADFORD 132kV
BROA3- | SHET | B-3-1a, B-3-2a | 33 | BROADFORD | 53.8029 | -1.7526 | BROADFORD 33kV
BROC1- | SPT | B-2-1b, B-2-2b | 132 | BROKEN CROSS | 51.9219 | -2.5903 | BROKEN CROSS 132kV
BROR1- | SHET | B-2-1a, B-3-1a | 132 | BRORA | 58.0202 | -3.8755 | BRORA 132kV
BROR1Q | SHET | B-2-1a, B-2-2a | 132 | BRORA | 58.0202 | -3.8755 | BRORA 132kV
BROR3- | SHET | B-3-1a | 33 | BRORA | 58.0202 | -3.8755 | BRORA 33kV
BROT1- | SPT | B-2-1b, B-2-2b | 132 | BROKEN CROSS TEE | 51.9219 | -2.5903 | BROKEN CROSS TEE 132kV
BROX1Q | SPT | B-2-1b, B-3-1b | 132 | BROXBURN | 55.9196 | -3.4545 | BROXBURN 132kV
BROX1R | SPT | B-2-1b, B-3-1b | 132 | BROXBURN | 55.9196 | -3.4545 | BROXBURN 132kV
BROX3- | SPT | B-3-1b | 33 | BROXBURN | 55.9196 | -3.4545 | BROXBURN 33kV
BRWA11 | NGET | B-3-1c, B-4-1c | 132 | BRIDGWATER | 51.1173 | -2.969 | BRIDGWATER 132kV
BRWA41 | NGET | B-2-1c, B-3-1c | 400 | BRIDGWATER | 51.1173 | -2.969 | BRIDGWATER 400kV
BRWA42 | NGET | B-2-1c, B-3-1c | 400 | BRIDGWATER | 51.1173 | -2.969 | BRIDGWATER 400kV
BRWA4A | NGET | B-2-1c | 400 | BRIDGWATER | 51.1173 | -2.969 | BRIDGWATER 400kV
BRWA4B | NGET | B-2-1c | 400 | BRIDGWATER | 51.1173 | -2.969 | BRIDGWATER 400kV
BULL41 | NGET | B-2-1c | 400 | BULLS LODGE | 51.7659 | 0.53743 | BULLS LODGE 400kV
BUMU1Q | SHET | B-2-1a, B-3-1a | 132 | BURGHMUIR | 56.3969 | -3.4885 | BURGHMUIR 132kV
BUMU1R | SHET | B-2-1a, B-3-1a | 132 | BURGHMUIR | 56.3969 | -3.4885 | BURGHMUIR 132kV
BUMU3- | SHET | B-3-1a | 33 | BURGHMUIR | 56.3969 | -3.4885 | BURGHMUIR 33kV
BURW11 | NGET | B-3-1c | 132 | BURWELL MAIN | 52.2801 | 0.31212 | BURWELL MAIN 132kV
BURW41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | BURWELL MAIN | 52.2801 | 0.31212 | BURWELL MAIN 400kV
BUSB2- | SPT | B-2-1b, B-2-2b | 275 | BUSBY | 55.7745 | -4.2638 | BUSBY 275kV
BUSH11 | NGET | B-3-1c, B-4-1c | 132 | BUSHBURY | 52.6362 | -2.1148 | BUSHBURY 132kV
BUSH2* | NGET | B-4-1c | 275 | BUSHBURY | 52.6362 | -2.1148 | BUSHBURY 275kV
BUSH21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | BUSHBURY | 52.6362 | -2.1148 | BUSHBURY 275kV
BUST11 | NGET | B-3-1c | 132 | BUSTLEHOLME | 52.5529 | -1.964 | BUSTLEHOLME 132kV
BUST21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | BUSTLEHOLME | 52.5529 | -1.964 | BUSTLEHOLME 275kV
BUST4A | NGET | B-2-1c, B-3-1c | 400 | BUSTLEHOLME | 52.5529 | -1.964 | BUSTLEHOLME 400kV
BUST4B | NGET | B-2-1c, B-3-1c | 400 | BUSTLEHOLME | 52.5529 | -1.964 | BUSTLEHOLME 400kV
CAAD1Q | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | CARRADALE | 55.5903 | -5.5034 | CARRADALE 132kV
CAAD1R | SHET | B-2-1a, B-3-1a | 132 | CARRADALE | 55.5903 | -5.5034 | CARRADALE 132kV
CAAD3- | SHET | B-3-1a | 33 | CARRADALE | 55.5903 | -5.5034 | CARRADALE 33kV
CAAD3J | SHET | B-3-1a | 33 | CARRADALE | 55.5903 | -5.5034 | CARRADALE 33kV
CAAI4J | SHET | B-2-2a, B-3-2a | 400 | CARNAIG |  |  | CARNAIG 400kV
CAAI4K | SHET | B-2-2a, B-3-2a | 400 | CARNAIG |  |  | CARNAIG 400kV
CAFA1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | CARSFAD | 55.1434 | -4.1896 | CARSFAD 132kV
CAFA5R | SPT | B-3-1b | 11 | CARSFAD | 55.1434 | -4.1896 | CARSFAD 11kV
CAID2- | SHET | B-2-2a, B-3-2a | 275 | CAIRN DUHIE WIND FARM |  |  | CAIRN DUHIE WIND FARM 275kV
CAID3- | SHET | B-3-2a | 33 | CAIRN DUHIE WIND FARM |  |  | CAIRN DUHIE WIND FARM 33kV
CAIN2- | SHET | B-2-1a, B-3-1a | 275 | CAIRNFORD | 57.4525 | -2.8497 | CAIRNFORD 275kV
CAIN3J | SHET | B-3-1a | 33 | CAIRNFORD | 57.4525 | -2.8497 | CAIRNFORD 33kV
CALD4- | SHET | B-2-2a | 400 | CALEDONIA OFFSHORE |  |  | CALEDONIA OFFSHORE 400kV
CAMA11 | NGET | B-2-1c | 132 | CAMBRIDGE ARMS | 51.4745 | -2.6103 | CAMBRIDGE ARMS 132kV
CAMA12 | NGET | B-2-1c | 132 | CAMBRIDGE ARMS | 51.4745 | -2.6103 | CAMBRIDGE ARMS 132kV
CAML61 | NGET | B-3-1c | 66 | CAMBLESFORTH | 53.7295 | -1.0008 | CAMBLESFORTH 66kV
CANT13 | NGET | B-3-1c | 132 | CANTERBURY NORTH | 51.2923 | 1.0941 | CANTERBURY NORTH 132kV
CANT14 | NGET | B-3-1c | 132 | CANTERBURY NORTH | 51.2923 | 1.0941 | CANTERBURY NORTH 132kV
CANT41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | CANTERBURY NORTH | 51.2923 | 1.0941 | CANTERBURY NORTH 400kV
CAPE11 | NGET | B-3-1c | 132 | CAPENHURST | 53.2688 | -2.9492 | CAPENHURST 132kV
CAPE1A | NGET | B-2-1c, B-3-1c | 132 | CAPENHURST | 53.2688 | -2.9492 | CAPENHURST 132kV
CAPE1B | NGET | B-2-1c, B-3-1c | 132 | CAPENHURST | 53.2688 | -2.9492 | CAPENHURST 132kV
CAPE21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | CAPENHURST | 53.2688 | -2.9492 | CAPENHURST 275kV
CAPE4A | NGET | B-2-1c, B-3-1c | 400 | CAPENHURST | 53.2688 | -2.9492 | CAPENHURST 400kV
CAPE4B | NGET | B-2-1c, B-3-1c | 400 | CAPENHURST | 53.2688 | -2.9492 | CAPENHURST 400kV
CARE11 | NGET | B-3-1c | 132 | CARDIFF EAST | 51.4948 | -3.1454 | CARDIFF EAST 132kV
CARE21 | NGET | B-2-1c, B-3-1c | 275 | CARDIFF EAST | 51.4948 | -3.1454 | CARDIFF EAST 275kV
CARR11 | NGET | B-3-1c | 132 | CARRINGTON | 53.4363 | -2.4072 | CARRINGTON 132kV
CARR12 | NGET | B-3-1c | 132 | CARRINGTON | 53.4363 | -2.4072 | CARRINGTON 132kV
CARR21 | NGET | B-2-1c, B-3-1c | 275 | CARRINGTON | 53.4363 | -2.4072 | CARRINGTON 275kV
CARR41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | CARRINGTON | 53.4363 | -2.4072 | CARRINGTON 400kV
CARR42 | NGET | B-2-1c, B-2-2c | 400 | CARRINGTON | 53.4363 | -2.4072 | CARRINGTON 400kV
CARR4A | NGET | B-3-1c | 400 | CARRINGTON | 53.4363 | -2.4072 | CARRINGTON 400kV
CARR4B | NGET | B-2-1c, B-3-1c | 400 | CARRINGTON | 53.4363 | -2.4072 | CARRINGTON 400kV
CASS1Q | SHET | B-2-1a, B-3-1a | 132 | CASSLEY | 58.1874 | -4.7297 | CASSLEY 132kV
CASS3- | SHET | B-3-1a | 33 | CASSLEY | 58.1874 | -4.7297 | CASSLEY 33kV
CATY1Q | SPT | B-2-1b, B-3-1b | 132 | CARNTYNE | 55.858 | -4.197 | CARNTYNE 132kV
CATY1R | SPT | B-2-1b, B-3-1b | 132 | CARNTYNE | 55.858 | -4.197 | CARNTYNE 132kV
CATY3- | SPT | B-3-1b | 33 | CARNTYNE | 55.858 | -4.197 | CARNTYNE 33kV
CCSS1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | CUMBERHEAD COLLECTOR | 55.5824 | -3.9259 | CUMBERHEAD COLLECTOR 132kV
CCSS3- | SPT | B-2-1b, B-2-2b, B-3-1b | 33 | CUMBERHEAD COLLECTOR | 55.5824 | -3.9259 | CUMBERHEAD COLLECTOR 33kV
CEAN1Q | SHET | B-2-1a, B-3-1a | 132 | CEANNACROC | 57.1541 | -4.9369 | CEANNACROC 132kV
CEAN5- | SHET | B-3-1a | 11 | CEANNACROC | 57.1541 | -4.9369 | CEANNACROC 11kV
CELL11 | NGET | B-3-1c, B-4-1c | 132 | CELLARHEAD | 53.0409 | -2.0826 | CELLARHEAD 132kV
CELL12 | NGET | B-3-1c, B-4-1c | 132 | CELLARHEAD | 53.0409 | -2.0826 | CELLARHEAD 132kV
CELL41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | CELLARHEAD | 53.0409 | -2.0826 | CELLARHEAD 400kV
CELL42 | NGET | B-2-2c | 400 | CELLARHEAD | 53.0409 | -2.0826 | CELLARHEAD 400kV
CELL43 | NGET | B-2-2c | 400 | CELLARHEAD | 53.0409 | -2.0826 | CELLARHEAD 400kV
CHAP1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | CHAPELCROSS | 55.0167 | -3.231 | CHAPELCROSS 132kV
CHAP3- | SPT | B-3-1b | 33 | CHAPELCROSS | 55.0167 | -3.231 | CHAPELCROSS 33kV
CHAR1- | SHET | B-2-1a, B-3-1a | 132 | CHARLESTON | 56.4732 | -3.0455 | CHARLESTON 132kV
CHAR1R | SHET | B-2-1a, B-3-1a | 132 | CHARLESTON | 56.4732 | -3.0455 | CHARLESTON 132kV
CHAR1S | SHET | B-2-1a, B-2-2a | 132 | CHARLESTON | 56.4732 | -3.0455 | CHARLESTON 132kV
CHAR1T | SHET | B-2-1a, B-2-2a | 132 | CHARLESTON | 56.4732 | -3.0455 | CHARLESTON 132kV
CHAR3- | SHET | B-3-1a | 33 | CHARLESTON | 56.4732 | -3.0455 | CHARLESTON 33kV
CHAS2Q | SPT | B-2-1b, B-3-1b | 275 | CHARLOTTE STREET | 51.1312 | -2.7535 | CHARLOTTE STREET 275kV
CHAS2R | SPT | B-2-1b, B-3-1b | 275 | CHARLOTTE STREET | 51.1312 | -2.7535 | CHARLOTTE STREET 275kV
CHAS3A | SPT | B-3-1b | 33 | CHARLOTTE STREET | 51.1312 | -2.7535 | CHARLOTTE STREET 33kV
CHAS3C | SPT | B-3-1b | 33 | CHARLOTTE STREET | 51.1312 | -2.7535 | CHARLOTTE STREET 33kV
CHIC11 | NGET | B-3-1c | 132 | CHICKERELL | 50.6246 | -2.4865 | CHICKERELL 132kV
CHIC41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | CHICKERELL | 50.6246 | -2.4865 | CHICKERELL 400kV
CHIC42 | NGET | B-4-1c | 400 | CHICKERELL | 50.6246 | -2.4865 | CHICKERELL 400kV
CHIC4A | NGET | B-2-1c | 400 | CHICKERELL | 50.6246 | -2.4865 | CHICKERELL 400kV
CHIL41 | NGET | B-2-1c | 400 | CHILLING | 50.8217 | -1.3286 | CHILLING 400kV
CHLS1- | SHET | B-2-2a | 132 | CHLEANSAID |  |  | CHLEANSAID 132kV
CHMO1- | SPT | B-2-2b | 132 | CHIRMORIE |  |  | CHIRMORIE 132kV
CHMO1T | SPT | B-2-2b | 132 | CHIRMORIE |  |  | CHIRMORIE 132kV
CHSI11 | NGET | B-3-1c | 132 | CHESSINGTON | 51.3441 | -0.32271 | CHESSINGTON 132kV
CHSI1A | NGET | B-3-1c | 132 | CHESSINGTON | 51.3441 | -0.32271 | CHESSINGTON 132kV
CHSI1B | NGET | B-3-1c | 132 | CHESSINGTON | 51.3441 | -0.32271 | CHESSINGTON 132kV
CHSI21 | NGET | B-2-1c, B-3-1c | 275 | CHESSINGTON | 51.3441 | -0.32271 | CHESSINGTON 275kV
CHTE11 | NGET | B-3-1c, B-3-2c | 132 | CHESTERFIELD | 53.2246 | -1.3889 | CHESTERFIELD 132kV
CHTE12 | NGET | B-3-1c, B-3-2c | 132 | CHESTERFIELD | 53.2246 | -1.3889 | CHESTERFIELD 132kV
CHTE21 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c, B-4-1c | 275 | CHESTERFIELD | 53.2246 | -1.3889 | CHESTERFIELD 275kV
CHTE41 | NGET | B-2-2c, B-3-2c, B-4-2c | 400 | CHESTERFIELD | 53.2246 | -1.3889 | CHESTERFIELD 400kV
CHUE4A | NGET | B-2-1c | 400 | CHAFFORD HUNDRED EAST | 51.4908 | 0.3119 | CHAFFORD HUNDRED EAST 400kV
CHUE4B | NGET | B-2-1c | 400 | CHAFFORD HUNDRED EAST | 51.4908 | 0.3119 | CHAFFORD HUNDRED EAST 400kV
CILF2A | NGET | B-2-1c, B-3-1c | 275 | CILFYNYDD | 51.6359 | -3.3002 | CILFYNYDD 275kV
CILF2B | NGET | B-2-1c, B-3-1c | 275 | CILFYNYDD | 51.6359 | -3.3002 | CILFYNYDD 275kV
CILF41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | CILFYNYDD | 51.6359 | -3.3002 | CILFYNYDD 400kV
CITR11 | NGET | B-3-1c | 132 | CITY ROAD | 51.5302 | -0.095741 | CITY ROAD 132kV
CITR12 | NGET | B-3-1c | 132 | CITY ROAD | 51.5302 | -0.095741 | CITY ROAD 132kV
CITR41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | CITY ROAD | 51.5302 | -0.095741 | CITY ROAD 400kV
CLAC1Q | SHET | B-2-1a, B-3-1a | 132 | CLACHAN | 56.2774 | -4.9217 | CLACHAN 132kV
CLAC5J | SHET | B-3-1a | 11 | CLACHAN | 56.2774 | -4.9217 | CLACHAN 11kV
CLAU1- | SPT | B-2-2b, B-3-2b | 132 | CLAUCHRIE |  |  | CLAUCHRIE 132kV
CLAU3- | SPT | B-3-2b | 33 | CLAUCHRIE |  |  | CLAUCHRIE 33kV
CLAW1- | SPT | B-2-2b | 132 | CLAWFIN |  |  | CLAWFIN 132kV
CLAY1Q | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | CLAYHILLS | 57.1404 | -2.0992 | CLAYHILLS 132kV
CLAY1R | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | CLAYHILLS | 57.1404 | -2.0992 | CLAYHILLS 132kV
CLAY3- | SHET | B-3-1a | 33 | CLAYHILLS | 57.1404 | -2.0992 | CLAYHILLS 33kV
CLEH41 | NGET | B-2-1c | 400 | CLEVE HILL | 51.3382 | 0.94034 | CLEVE HILL 400kV
CLFO1- | SPT | B-2-2b, B-3-2b | 132 | CLOICH FOREST |  |  | CLOICH FOREST 132kV
CLFO3- | SPT | B-3-2b | 33 | CLOICH FOREST |  |  | CLOICH FOREST 33kV
CLGO1- | SHET | B-3-2a | 132 | CLASH GOUR WIND FARM |  |  | CLASH GOUR WIND FARM 132kV
CLGO2- | SHET | B-2-2a, B-3-2a | 275 | CLASH GOUR WIND FARM |  |  | CLASH GOUR WIND FARM 275kV
CLGO2A | SHET | B-2-2a, B-3-2a | 275 | CLASH GOUR WIND FARM |  |  | CLASH GOUR WIND FARM 275kV
CLOI1- | SHET | B-3-2a | 132 | CLOICHE WIND FARM |  |  | CLOICHE WIND FARM 132kV
CLOI1A | SHET | B-2-2a | 132 | CLOICHE WIND FARM |  |  | CLOICHE WIND FARM 132kV
CLOI3- | SHET | B-3-2a | 33 | CLOICHE WIND FARM |  |  | CLOICHE WIND FARM 33kV
CLUN1Q | SHET | B-2-1a, B-3-1a | 132 | CLUNIE | 56.7174 | -3.7838 | CLUNIE 132kV
CLUN1R | SHET | B-2-1a, B-3-1a | 132 | CLUNIE | 56.7174 | -3.7838 | CLUNIE 132kV
CLUN1S | SHET | B-2-1a, B-2-2a | 132 | CLUNIE | 56.7174 | -3.7838 | CLUNIE 132kV
CLUN1T | SHET | B-2-1a, B-2-2a | 132 | CLUNIE | 56.7174 | -3.7838 | CLUNIE 132kV
CLUN5J | SHET | B-3-1a | 11 | CLUNIE | 56.7174 | -3.7838 | CLUNIE 11kV
CLUN5K | SHET | B-3-1a | 11 | CLUNIE | 56.7174 | -3.7838 | CLUNIE 11kV
CLYM2- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 275 | CLYDE'S MILL | 55.8223 | -4.1472 | CLYDE'S MILL 275kV
CLYM3A | SPT | B-3-1b | 33 | CLYDE'S MILL | 55.8223 | -4.1472 | CLYDE'S MILL 33kV
CLYM3B | SPT | B-3-1b | 33 | CLYDE'S MILL | 55.8223 | -4.1472 | CLYDE'S MILL 33kV
CLYM4- | SPT | B-2-2b, B-3-2b | 400 | CLYDE'S MILL | 55.8223 | -4.1472 | CLYDE'S MILL 400kV
CLYN2Q | SPT | B-2-1b, B-3-1b | 275 | CLYDE NORTH |  |  | CLYDE NORTH 275kV
CLYN3A | SPT | B-3-1b | 33 | CLYDE NORTH |  |  | CLYDE NORTH 33kV
CLYN3B | SPT | B-3-1b | 33 | CLYDE NORTH |  |  | CLYDE NORTH 33kV
CLYN3C | SPT | B-3-1b | 33 | CLYDE NORTH |  |  | CLYDE NORTH 33kV
CLYN3D | SPT | B-3-1b | 33 | CLYDE NORTH |  |  | CLYDE NORTH 33kV
CLYS2R | SPT | B-2-1b, B-3-1b | 275 | CLYDE SOUTH |  |  | CLYDE SOUTH 275kV
CLYS3A | SPT | B-2-2b, B-3-1b | 33 | CLYDE SOUTH |  |  | CLYDE SOUTH 33kV
CLYS3B | SPT | B-2-1b, B-2-2b | 33 | CLYDE SOUTH |  |  | CLYDE SOUTH 33kV
CLYS3X | SPT | B-2-1b, B-3-1b | 33 | CLYDE SOUTH |  |  | CLYDE SOUTH 33kV
CMBS4A | SHET | B-2-2a, B-3-2a | 400 | CAMBUSHINNIE | 57.9436 | -4.4143 | CAMBUSHINNIE 400kV
CMBS4B | SHET | B-2-2a, B-3-2a | 400 | CAMBUSHINNIE | 57.9436 | -4.4143 | CAMBUSHINNIE 400kV
COAB4- | SPT | B-2-2b | 400 | COALBURN BATTERY STORAGE FACILITY | 55.6163 | -3.8684 | COALBURN BATTERY STORAGE FACILITY 400kV
COAL1- | SPT | B-2-1b | 132 | COALBURN | 55.6163 | -3.8684 | COALBURN 132kV
COAL1A | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | COALBURN | 55.6163 | -3.8684 | COALBURN 132kV
COAL1B | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | COALBURN | 55.6163 | -3.8684 | COALBURN 132kV
COAL3U | SPT | B-4-1b | 33 | COALBURN | 55.6163 | -3.8684 | COALBURN 33kV
COAL3V | SPT | B-4-1b | 33 | COALBURN | 55.6163 | -3.8684 | COALBURN 33kV
COAL4- | SPT | B-2-1b, B-2-2b, B-3-1b | 400 | COALBURN | 55.6163 | -3.8684 | COALBURN 400kV
COAN4- | SPT | B-2-2b | 400 | COALBURN NORTH | 55.6163 | -3.8684 | COALBURN NORTH 400kV
COAT2Q | SPT | B-2-1b, B-3-1b | 275 | COATBRIDGE | 55.851 | -4.0125 | COATBRIDGE 275kV
COAT2R | SPT | B-2-1b, B-3-1b | 275 | COATBRIDGE | 55.851 | -4.0125 | COATBRIDGE 275kV
COAT3- | SPT | B-3-1b | 33 | COATBRIDGE | 55.851 | -4.0125 | COATBRIDGE 33kV
COBA3- | SPT | B-3-2b | 33 | COALBURN BATTERY STORAGE TWO | 55.6163 | -3.8684 | COALBURN BATTERY STORAGE TWO 33kV
COBA4- | SPT | B-2-2b, B-3-2b | 400 | COALBURN BATTERY STORAGE TWO | 55.6163 | -3.8684 | COALBURN BATTERY STORAGE TWO 400kV
COCK2- | SPT | B-2-1b, B-3-1b, B-4-1b | 275 | COCKENZIE | 55.9673 | -2.968 | COCKENZIE 275kV
COCK3- | SPT | B-3-1b | 33 | COCKENZIE | 55.9673 | -2.968 | COCKENZIE 33kV
COCK4Q | SPT | B-2-1b, B-2-2b, B-3-1b | 400 | COCKENZIE | 55.9673 | -2.968 | COCKENZIE 400kV
COCK4R | SPT | B-2-1b, B-2-2b, B-3-1b | 400 | COCKENZIE | 55.9673 | -2.968 | COCKENZIE 400kV
COFD4A | SHET | B-2-2a | 400 | COACHFORD | 53.3864 | -3.0861 | COACHFORD 400kV
COFD4B | SHET | B-2-2a | 400 | COACHFORD | 53.3864 | -3.0861 | COACHFORD 400kV
COGA1- | SHET | B-2-1a, B-3-1a | 132 | CORRIEGARTH WIND FARM | 57.1924 | -4.4017 | CORRIEGARTH WIND FARM 132kV
COGA1C | SHET | B-2-1a | 132 | CORRIEGARTH WIND FARM | 57.1924 | -4.4017 | CORRIEGARTH WIND FARM 132kV
COGA3- | SHET | B-3-1a | 33 | CORRIEGARTH WIND FARM | 57.1924 | -4.4017 | CORRIEGARTH WIND FARM 33kV
COGL4J | SHET | B-2-2a | 400 | COIRE GLAS PUMPED STORAGE |  |  | COIRE GLAS PUMPED STORAGE 400kV
COGL4K | SHET | B-2-2a | 400 | COIRE GLAS PUMPED STORAGE |  |  | COIRE GLAS PUMPED STORAGE 400kV
CONL2Q | SPT | B-2-2b | 275 | CONLAND |  |  | CONLAND 275kV
CONL2R | SPT | B-2-2b | 275 | CONLAND |  |  | CONLAND 275kV
CONL4- | SPT | B-2-2b | 400 | CONLAND |  |  | CONLAND 400kV
CONN1C | SHET | B-2-1a, B-2-2a | 132 | CONNAGILL | 58.5131 | -3.8801 | CONNAGILL 132kV
CONN1D | SHET | B-2-2a | 132 | CONNAGILL | 58.5131 | -3.8801 | CONNAGILL 132kV
CONN1J | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | CONNAGILL | 58.5131 | -3.8801 | CONNAGILL 132kV
CONN1K | SHET | B-2-2a, B-3-2a | 132 | CONNAGILL | 58.5131 | -3.8801 | CONNAGILL 132kV
CONN2J | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 275 | CONNAGILL | 58.5131 | -3.8801 | CONNAGILL 275kV
CONN2K | SHET | B-2-2a, B-3-2a | 275 | CONNAGILL | 58.5131 | -3.8801 | CONNAGILL 275kV
CONQ11 | NGET | B-3-1c | 132 | CONNAHS QUAY | 53.2299 | -3.0739 | CONNAHS QUAY 132kV
CONQ12 | NGET | B-3-1c | 132 | CONNAHS QUAY | 53.2299 | -3.0739 | CONNAHS QUAY 132kV
CONQ13 | NGET | B-3-1c | 132 | CONNAHS QUAY | 53.2299 | -3.0739 | CONNAHS QUAY 132kV
CONQ41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | CONNAHS QUAY | 53.2299 | -3.0739 | CONNAHS QUAY 400kV
CONQ42 | NGET | B-2-2c | 400 | CONNAHS QUAY | 53.2299 | -3.0739 | CONNAHS QUAY 400kV
CORI1J | SHET | B-2-1a, B-3-1a | 132 | CORRIEMOILLIE | 57.6339 | -4.7703 | CORRIEMOILLIE 132kV
CORI1K | SHET | B-2-1a | 132 | CORRIEMOILLIE | 57.6339 | -4.7703 | CORRIEMOILLIE 132kV
CORI1P | SHET | B-2-1a | 132 | CORRIEMOILLIE | 57.6339 | -4.7703 | CORRIEMOILLIE 132kV
CORI1Q | SHET | B-2-1a | 132 | CORRIEMOILLIE | 57.6339 | -4.7703 | CORRIEMOILLIE 132kV
CORI3- | SHET | B-3-1a | 33 | CORRIEMOILLIE | 57.6339 | -4.7703 | CORRIEMOILLIE 33kV
CORI3J | SHET | B-3-1a | 33 | CORRIEMOILLIE | 57.6339 | -4.7703 | CORRIEMOILLIE 33kV
COSO41 | NGET | B-2-1c | 400 | CORYTON SOUTH | 51.5129 | 0.5067 | CORYTON SOUTH 400kV
COST1- | SHET | B-2-2a, B-3-2a | 132 | COSTA HEAD |  |  | COSTA HEAD 132kV
COST1A | SHET | B-2-2a | 132 | COSTA HEAD |  |  | COSTA HEAD 132kV
COST3- | SHET | B-3-2a | 33 | COSTA HEAD |  |  | COSTA HEAD 33kV
COTT41 | NGET | B-2-1c, B-2-2c, B-4-2c | 400 | COTTAM | 53.3007 | -0.78123 | COTTAM 400kV
COTT42 | NGET | B-2-1c, B-2-2c | 400 | COTTAM | 53.3007 | -0.78123 | COTTAM 400kV
COTT43 | NGET | B-2-2c | 400 | COTTAM | 53.3007 | -0.78123 | COTTAM 400kV
COUA1Q | SHET | B-2-1a, B-3-1a | 132 | COUPAR ANGUS | 56.5383 | -3.2744 | COUPAR ANGUS 132kV
COUA1R | SHET | B-2-1a, B-3-1a | 132 | COUPAR ANGUS | 56.5383 | -3.2744 | COUPAR ANGUS 132kV
COUA3- | SHET | B-3-1a | 33 | COUPAR ANGUS | 56.5383 | -3.2744 | COUPAR ANGUS 33kV
COVE11 | NGET | B-3-1c, B-4-1c | 132 | COVENTRY | 52.4565 | -1.4638 | COVENTRY 132kV
COVE12 | NGET | B-3-1c, B-4-1c | 132 | COVENTRY | 52.4565 | -1.4638 | COVENTRY 132kV
COVE21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | COVENTRY | 52.4565 | -1.4638 | COVENTRY 275kV
COWL11 | NGET | B-3-1c, B-4-1c | 132 | COWLEY | 51.7115 | -1.1905 | COWLEY 132kV
COWL12 | NGET | B-3-1c | 132 | COWLEY | 51.7115 | -1.1905 | COWLEY 132kV
COWL41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | COWLEY | 51.7115 | -1.1905 | COWLEY 400kV
COWT2A | NGET | B-2-1c | 275 | COWBRIDGE TEE | 51.4635 | -3.4483 | COWBRIDGE TEE 275kV
COYL1- | SPT | B-2-1b, B-3-1b | 132 | COYLTON | 55.4473 | -4.4334 | COYLTON 132kV
COYL2- | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | COYLTON | 55.4473 | -4.4334 | COYLTON 275kV
COYL3- | SPT | B-3-1b | 33 | COYLTON | 55.4473 | -4.4334 | COYLTON 33kV
COYT1T | SPT | B-2-1b | 132 | COYLTON TEE | 55.4473 | -4.4334 | COYLTON TEE 132kV
COYW2S | SPT | B-2-1b, B-2-2b | 275 | COYLTON WEST | 55.4473 | -4.4334 | COYLTON WEST 275kV
COYW2T | SPT | B-2-1b, B-2-2b | 275 | COYLTON WEST | 55.4473 | -4.4334 | COYLTON WEST 275kV
CRAI1- | SHET | B-2-1a, B-3-1a | 132 | CRAIGIEBUCKLER | 57.1314 | -2.1552 | CRAIGIEBUCKLER 132kV
CRAI1P | SHET | B-2-1a | 132 | CRAIGIEBUCKLER | 57.1314 | -2.1552 | CRAIGIEBUCKLER 132kV
CRAI1Q | SHET | B-2-1a, B-3-1a | 132 | CRAIGIEBUCKLER | 57.1314 | -2.1552 | CRAIGIEBUCKLER 132kV
CRAI1R | SHET | B-2-1a | 132 | CRAIGIEBUCKLER | 57.1314 | -2.1552 | CRAIGIEBUCKLER 132kV
CRAI3- | SHET | B-3-1a | 33 | CRAIGIEBUCKLER | 57.1314 | -2.1552 | CRAIGIEBUCKLER 33kV
CRAR1R | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | CRARAE | 56.1315 | -5.2656 | CRARAE 132kV
CRAR3- | SHET | B-3-1a, B-3-2a | 33 | CRARAE | 56.1315 | -5.2656 | CRARAE 33kV
CRAS2- | SHET | B-2-2a, B-3-2a | 275 | CRARAE SOUTH | 56.1315 | -5.2656 | CRARAE SOUTH 275kV
CRAS3- | SHET | B-3-2a | 33 | CRARAE SOUTH | 56.1315 | -5.2656 | CRARAE SOUTH 33kV
CRCK2- | SPT | B-2-2b, B-3-2b | 275 | CARRICK | 54.7128 | -5.8457 | CARRICK 275kV
CRCK3- | SPT | B-3-2b | 33 | CARRICK | 54.7128 | -5.8457 | CARRICK 33kV
CRDH1J | SHET | B-2-2a, B-3-2a | 132 | CREAG DHUBH |  |  | CREAG DHUBH 132kV
CRDH1K | SHET | B-2-2a, B-3-2a | 132 | CREAG DHUBH |  |  | CREAG DHUBH 132kV
CRDH2J | SHET | B-2-2a, B-3-2a | 275 | CREAG DHUBH |  |  | CREAG DHUBH 275kV
CRDH2K | SHET | B-2-2a, B-3-2a | 275 | CREAG DHUBH |  |  | CREAG DHUBH 275kV
CRDY3A | SPT | B-2-1b, B-2-2b | 33 | CROSSDYKES | 51.9219 | -2.5903 | CROSSDYKES 33kV
CRDY3B | SPT | B-2-1b, B-2-2b | 33 | CROSSDYKES | 51.9219 | -2.5903 | CROSSDYKES 33kV
CREA1- | SHET | B-2-1a, B-3-1a | 132 | CREAG RIABHACH WINDFARM | 58.2109 | -4.5044 | CREAG RIABHACH WINDFARM 132kV
CREA1A | SHET | B-2-1a | 132 | CREAG RIABHACH WINDFARM | 58.2109 | -4.5044 | CREAG RIABHACH WINDFARM 132kV
CREA1B | SHET | B-2-1a | 132 | CREAG RIABHACH WINDFARM | 58.2109 | -4.5044 | CREAG RIABHACH WINDFARM 132kV
CREA3- | SHET | B-3-1a | 33 | CREAG RIABHACH WINDFARM | 58.2109 | -4.5044 | CREAG RIABHACH WINDFARM 33kV
CREB11 | NGET | B-3-1c | 132 | CREYKE BECK | 53.8007 | -0.41528 | CREYKE BECK 132kV
CREB12 | NGET | B-3-1c | 132 | CREYKE BECK | 53.8007 | -0.41528 | CREYKE BECK 132kV
CREB2A | NGET | B-2-1c, B-3-1c | 275 | CREYKE BECK | 53.8007 | -0.41528 | CREYKE BECK 275kV
CREB2B | NGET | B-2-1c, B-3-1c | 275 | CREYKE BECK | 53.8007 | -0.41528 | CREYKE BECK 275kV
CREB41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | CREYKE BECK | 53.8007 | -0.41528 | CREYKE BECK 400kV
CREB42 | NGET | B-2-2c | 400 | CREYKE BECK | 53.8007 | -0.41528 | CREYKE BECK 400kV
CRMU2J | SHET | B-2-2a, B-3-2a | 275 | CRAIG MURRAIL |  |  | CRAIG MURRAIL 275kV
CRMU2K | SHET | B-2-2a, B-3-2a | 275 | CRAIG MURRAIL |  |  | CRAIG MURRAIL 275kV
CRMU3- | SHET | B-3-2a | 33 | CRAIG MURRAIL |  |  | CRAIG MURRAIL 33kV
CROO1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | CROOKSTON | 55.8212 | -4.3656 | CROOKSTON 132kV
CROO1R | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | CROOKSTON | 55.8212 | -4.3656 | CROOKSTON 132kV
CROO3J | SPT | B-3-1b | 33 | CROOKSTON | 55.8212 | -4.3656 | CROOKSTON 33kV
CROO3K | SPT | B-3-1b | 33 | CROOKSTON | 55.8212 | -4.3656 | CROOKSTON 33kV
CRSN1Q | SHET | B-2-2a, B-3-2a | 132 | CROSSAIG NORTH | 51.9219 | -2.5903 | CROSSAIG NORTH 132kV
CRSN1R | SHET | B-2-2a, B-3-2a | 132 | CROSSAIG NORTH | 51.9219 | -2.5903 | CROSSAIG NORTH 132kV
CRSN2Q | SHET | B-2-2a, B-3-2a | 275 | CROSSAIG NORTH | 51.9219 | -2.5903 | CROSSAIG NORTH 275kV
CRSN2R | SHET | B-2-2a, B-3-2a | 275 | CROSSAIG NORTH | 51.9219 | -2.5903 | CROSSAIG NORTH 275kV
CRSS1J | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | CROSSAIG | 55.6976 | -5.4589 | CROSSAIG 132kV
CRSS1K | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | CROSSAIG | 55.6976 | -5.4589 | CROSSAIG 132kV
CRSS1Q | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | CROSSAIG | 55.6976 | -5.4589 | CROSSAIG 132kV
CRSS1R | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | CROSSAIG | 55.6976 | -5.4589 | CROSSAIG 132kV
CRSS1X | SHET | B-3-2a | 132 | CROSSAIG | 55.6976 | -5.4589 | CROSSAIG 132kV
CRSS1Y | SHET | B-3-2a | 132 | CROSSAIG | 55.6976 | -5.4589 | CROSSAIG 132kV
CRSS2A | SHET | B-2-1a, B-3-1a, B-3-2a | 275 | CROSSAIG | 55.6976 | -5.4589 | CROSSAIG 275kV
CRSS2B | SHET | B-2-1a, B-3-1a, B-3-2a | 275 | CROSSAIG | 55.6976 | -5.4589 | CROSSAIG 275kV
CRSS2C | SHET | B-2-1a | 275 | CROSSAIG | 55.6976 | -5.4589 | CROSSAIG 275kV
CRSS2D | SHET | B-2-1a | 275 | CROSSAIG | 55.6976 | -5.4589 | CROSSAIG 275kV
CRSS3- | SHET | B-3-1a | 33 | CROSSAIG | 55.6976 | -5.4589 | CROSSAIG 33kV
CRSS3W | SHET | B-4-1a | 33 | CROSSAIG | 55.6976 | -5.4589 | CROSSAIG 33kV
CRSS3X | SHET | B-4-1a | 33 | CROSSAIG | 55.6976 | -5.4589 | CROSSAIG 33kV
CRUA2A | SPT | B-2-2b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2A | SPT | B-2-2b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2A | SPT | B-2-2b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2B | SPT | B-2-2b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2B | SPT | B-2-2b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2B | SPT | B-2-2b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2Q | SPT | B-2-1b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2Q | SPT | B-2-1b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2Q | SPT | B-2-1b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2R | SPT | B-2-1b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2R | SPT | B-2-1b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2R | SPT | B-2-1b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2S | SPT | B-2-2b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2S | SPT | B-2-2b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2S | SPT | B-2-2b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2T | SPT | B-2-2b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2T | SPT | B-2-2b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRUA2T | SPT | B-2-2b | 275 | CRUACHAN | 56.4026 | -5.1131 | CRUACHAN 275kV
CRYR1- | SPT | B-3-1b | 132 | CRYSTAL RIG | 55.9144 | -2.5409 | CRYSTAL RIG 132kV
CRYR1A | SPT | B-2-1b, B-3-1b | 132 | CRYSTAL RIG | 55.9144 | -2.5409 | CRYSTAL RIG 132kV
CRYR31 | SPT | B-3-1b | 33 | CRYSTAL RIG | 55.9144 | -2.5409 | CRYSTAL RIG 33kV
CRYR32 | SPT | B-3-1b | 33 | CRYSTAL RIG | 55.9144 | -2.5409 | CRYSTAL RIG 33kV
CRYR3V | SPT | B-4-1b | 33 | CRYSTAL RIG | 55.9144 | -2.5409 | CRYSTAL RIG 33kV
CRYR4- | SPT | B-2-1b, B-2-2b, B-3-1b | 400 | CRYSTAL RIG | 55.9144 | -2.5409 | CRYSTAL RIG 400kV
CULJ31 | NGET | B-3-1c | 33 | CULHAM JET | 51.6612 | -1.2283 | CULHAM JET 33kV
CULJ32 | NGET | B-3-1c | 33 | CULHAM JET | 51.6612 | -1.2283 | CULHAM JET 33kV
CULJ33 | NGET | B-3-1c | 33 | CULHAM JET | 51.6612 | -1.2283 | CULHAM JET 33kV
CULJ4A | NGET | B-2-1c, B-3-1c | 400 | CULHAM JET | 51.6612 | -1.2283 | CULHAM JET 400kV
CULL1A | SHET | B-2-2a, B-3-2a | 132 | CULLIGRAN | 57.4257 | -4.7026 | CULLIGRAN 132kV
CULL1Q | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | CULLIGRAN | 57.4257 | -4.7026 | CULLIGRAN 132kV
CULL5- | SHET | B-3-1a, B-3-2a | 11 | CULLIGRAN | 57.4257 | -4.7026 | CULLIGRAN 11kV
CULR2- | SPT | B-2-2b | 275 | CULROSS | 51.9219 | -2.5903 | CULROSS 275kV
CULR2T | SPT | B-2-2b | 275 | CULROSS | 51.9219 | -2.5903 | CULROSS 275kV
CUMB1Q | SPT | B-2-1b, B-3-1b | 132 | CUMBERNAULD | 55.9468 | -3.9632 | CUMBERNAULD 132kV
CUMB1R | SPT | B-2-1b, B-3-1b | 132 | CUMBERNAULD | 55.9468 | -3.9632 | CUMBERNAULD 132kV
CUMB3- | SPT | B-3-1b | 33 | CUMBERNAULD | 55.9468 | -3.9632 | CUMBERNAULD 33kV
CUMH3- | SPT | B-2-1b, B-2-2b | 33 | CUMBERHEAD WF SUBSTATION |  |  | CUMBERHEAD WF SUBSTATION 33kV
CUMW1- | SPT | B-2-2b, B-3-2b | 132 | CUMBERHEAD WEST |  |  | CUMBERHEAD WEST 132kV
CUMW3- | SPT | B-3-2b | 33 | CUMBERHEAD WEST |  |  | CUMBERHEAD WEST 33kV
CUPA1Q | SPT | B-2-1b, B-3-1b | 132 | CUPAR | 56.3136 | -3.0367 | CUPAR 132kV
CUPA1R | SPT | B-2-1b, B-3-1b | 132 | CUPAR | 56.3136 | -3.0367 | CUPAR 132kV
CUPA3- | SPT | B-3-1b | 33 | CUPAR | 56.3136 | -3.0367 | CUPAR 33kV
CURR1A | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | CURRIE | 55.9036 | -3.3097 | CURRIE 132kV
CURR1B | SPT | B-2-1b, B-3-1b | 132 | CURRIE | 55.9036 | -3.3097 | CURRIE 132kV
CURR2- | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | CURRIE | 55.9036 | -3.3097 | CURRIE 275kV
CURR3W | SPT | B-4-1b | 33 | CURRIE | 55.9036 | -3.3097 | CURRIE 33kV
CURR5- | SPT | B-3-1b | 11 | CURRIE | 55.9036 | -3.3097 | CURRIE 11kV
DAAS2- | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | DALLAS SUBSTATION | 57.5569 | -3.421 | DALLAS SUBSTATION 275kV
DAAS3- | SHET | B-3-1a | 33 | DALLAS SUBSTATION | 57.5569 | -3.421 | DALLAS SUBSTATION 33kV
DAER1- | SPT | B-2-2b, B-3-2b | 132 | DAER WINDFARM |  |  | DAER WINDFARM 132kV
DAER3- | SPT | B-3-2b | 33 | DAER WINDFARM |  |  | DAER WINDFARM 33kV
DAIN41 | NGET | B-2-1c, B-2-2c | 400 | DAINES | 53.4257 | -2.3791 | DAINES 400kV
DALB2A | SHET, SPT | B-2-2a, B-2-2b | 275 | DALMALLY BORDER NODE | 56.4193 | -5.0133 | DALMALLY BORDER NODE 275kV
DALB2A | SHET, SPT | B-2-2a, B-2-2b | 275 | DALMALLY BORDER NODE | 56.4193 | -5.0133 | DALMALLY BORDER NODE 275kV
DALB2B | SHET, SPT | B-2-2a, B-2-2b | 275 | DALMALLY BORDER NODE | 56.4193 | -5.0133 | DALMALLY BORDER NODE 275kV
DALB2B | SHET, SPT | B-2-2a, B-2-2b | 275 | DALMALLY BORDER NODE | 56.4193 | -5.0133 | DALMALLY BORDER NODE 275kV
DALL2- | SPT | B-2-1b, B-2-2b | 275 | DALMALLY | 56.4193 | -5.0133 | DALMALLY 275kV
DALM1- | SPT | B-2-1b, B-3-1b | 132 | DALMARNOCK | 55.8357 | -4.2028 | DALMARNOCK 132kV
DALM2Q | SPT | B-2-1b, B-3-1b | 275 | DALMARNOCK | 55.8357 | -4.2028 | DALMARNOCK 275kV
DALM2R | SPT | B-2-1b, B-3-1b | 275 | DALMARNOCK | 55.8357 | -4.2028 | DALMARNOCK 275kV
DALM3- | SPT | B-3-1b | 33 | DALMARNOCK | 55.8357 | -4.2028 | DALMARNOCK 33kV
DAMC41 | NGET | B-2-1c | 400 | DAMHEAD CREEK | 51.4244 | 0.59866 | DAMHEAD CREEK 400kV
DEAN1Q | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | DEANIE |  |  | DEANIE 132kV
DEAN5- | SHET | B-3-1a, B-3-2a | 11 | DEANIE |  |  | DEANIE 11kV
DEAW1- | SHET | B-2-2a, B-3-2a | 132 | DEANIE WEST |  |  | DEANIE WEST 132kV
DEAW1A | SHET | B-2-2a | 132 | DEANIE WEST |  |  | DEANIE WEST 132kV
DEAW5- | SHET | B-3-2a | 11 | DEANIE WEST |  |  | DEANIE WEST 11kV
DEBS2- | SPT | B-2-2b, B-3-2b | 275 | DEVILLA BATTERY STORAGE FACILITY |  |  | DEVILLA BATTERY STORAGE FACILITY 275kV
DEBS3A | SPT | B-3-2b | 33 | DEVILLA BATTERY STORAGE FACILITY |  |  | DEVILLA BATTERY STORAGE FACILITY 33kV
DEBS3B | SPT | B-3-2b | 33 | DEVILLA BATTERY STORAGE FACILITY |  |  | DEVILLA BATTERY STORAGE FACILITY 33kV
DEBS3C | SPT | B-3-2b | 33 | DEVILLA BATTERY STORAGE FACILITY |  |  | DEVILLA BATTERY STORAGE FACILITY 33kV
DEBS3D | SPT | B-3-2b | 33 | DEVILLA BATTERY STORAGE FACILITY |  |  | DEVILLA BATTERY STORAGE FACILITY 33kV
DEBS3E | SPT | B-3-2b | 33 | DEVILLA BATTERY STORAGE FACILITY |  |  | DEVILLA BATTERY STORAGE FACILITY 33kV
DELL1- | SHET | B-2-2a | 132 | DELL | 55.848 | -4.244 | DELL 132kV
DELL1A | SHET | B-2-2a | 132 | DELL | 55.848 | -4.244 | DELL 132kV
DELL1B | SHET | B-2-2a | 132 | DELL | 55.848 | -4.244 | DELL 132kV
DENN1- | SPT | B-2-1b, B-3-1b | 132 | DENNY NORTH | 56.0411 | -3.8904 | DENNY NORTH 132kV
DENN2- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 275 | DENNY NORTH | 56.0411 | -3.8904 | DENNY NORTH 275kV
DENN2T | SPT | B-2-2b | 275 | DENNY NORTH | 56.0411 | -3.8904 | DENNY NORTH 275kV
DENN4- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 400 | DENNY NORTH | 56.0411 | -3.8904 | DENNY NORTH 400kV
DENS1Q | SHET | B-2-1a | 132 | DENSIDE |  |  | DENSIDE 132kV
DENS1R | SHET | B-2-1a | 132 | DENSIDE |  |  | DENSIDE 132kV
DESA1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | DERSALLOCH | 55.3195 | -4.4703 | DERSALLOCH 132kV
DESA3- | SPT | B-3-1b | 33 | DERSALLOCH | 55.3195 | -4.4703 | DERSALLOCH 33kV
DEVM1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | DEVOL MOOR | 55.915 | -4.7082 | DEVOL MOOR 132kV
DEVM3- | SPT | B-3-1b | 33 | DEVOL MOOR | 55.915 | -4.7082 | DEVOL MOOR 33kV
DEVM4- | SPT | B-2-1b, B-2-2b, B-3-1b | 400 | DEVOL MOOR | 55.915 | -4.7082 | DEVOL MOOR 400kV
DEVO1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | DEVONSIDE | 56.1375 | -3.7805 | DEVONSIDE 132kV
DEVO3- | SPT | B-3-1b | 33 | DEVONSIDE | 56.1375 | -3.7805 | DEVONSIDE 33kV
DEWP2Q | SPT | B-2-1b, B-3-1b | 275 | DEWAR PLACE | 55.9473 | -3.2105 | DEWAR PLACE 275kV
DEWP2R | SPT | B-2-1b, B-3-1b | 275 | DEWAR PLACE | 55.9473 | -3.2105 | DEWAR PLACE 275kV
DEWP3- | SPT | B-3-1b, B-4-1b | 33 | DEWAR PLACE | 55.9473 | -3.2105 | DEWAR PLACE 33kV
DIDC41 | NGET | B-2-1c, B-3-1c | 400 | DIDCOT | 51.6256 | -1.2592 | DIDCOT 400kV
DINO41 | NGET | B-2-1c, B-2-2c | 400 | DINORWIG | 53.1215 | -4.1001 | DINORWIG 400kV
DISS4A | NGET | B-2-1c, B-2-2c | 400 | DISS | 52.3736 | 1.1235 | DISS 400kV
DISS4B | NGET | B-2-1c | 400 | DISS | 52.3736 | 1.1235 | DISS 400kV
DLCH1A | SHET | B-2-1a, B-2-2a | 132 | DALCHORK | 58.0528 | -4.4033 | DALCHORK 132kV
DLCH1B | SHET | B-2-1a, B-2-2a | 132 | DALCHORK | 58.0528 | -4.4033 | DALCHORK 132kV
DONO1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | DOUGLAS NORTH COLLECTOR | 55.5917 | -3.8332 | DOUGLAS NORTH COLLECTOR 132kV
DONO3A | SPT | B-2-1b, B-2-2b, B-3-1b | 33 | DOUGLAS NORTH COLLECTOR | 55.5917 | -3.8332 | DOUGLAS NORTH COLLECTOR 33kV
DORE11 | SHET | B-2-1a, B-3-1a | 132 | DORENELL WIND FARM | 57.3785 | -3.0992 | DORENELL WIND FARM 132kV
DORE12 | SHET | B-2-1a, B-3-1a | 132 | DORENELL WIND FARM | 57.3785 | -3.0992 | DORENELL WIND FARM 132kV
DORE31 | SHET | B-3-1a | 33 | DORENELL WIND FARM | 57.3785 | -3.0992 | DORENELL WIND FARM 33kV
DORE32 | SHET | B-3-1a | 33 | DORENELL WIND FARM | 57.3785 | -3.0992 | DORENELL WIND FARM 33kV
DOUN1- | SHET | B-2-2a, B-3-1a, B-3-2a | 132 | DOUNREAY | 58.5752 | -3.7542 | DOUNREAY 132kV
DOUN2- | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 275 | DOUNREAY | 58.5752 | -3.7542 | DOUNREAY 275kV
DOUN2A | SHET | B-2-2a, B-3-2a | 275 | DOUNREAY | 58.5752 | -3.7542 | DOUNREAY 275kV
DOUN2B | SHET | B-2-2a | 275 | DOUNREAY | 58.5752 | -3.7542 | DOUNREAY 275kV
DOUN2C | SHET | B-2-2a | 275 | DOUNREAY | 58.5752 | -3.7542 | DOUNREAY 275kV
DOUN3- | SHET | B-3-1a, B-3-2a | 33 | DOUNREAY | 58.5752 | -3.7542 | DOUNREAY 33kV
DOUN3W | SHET | B-4-1a | 33 | DOUNREAY | 58.5752 | -3.7542 | DOUNREAY 33kV
DOUN3X | SHET | B-4-1a | 33 | DOUNREAY | 58.5752 | -3.7542 | DOUNREAY 33kV
DOUN3Y | SHET | B-4-2a | 33 | DOUNREAY | 58.5752 | -3.7542 | DOUNREAY 33kV
DRAK11 | NGET | B-3-1c | 132 | DRAKELOW | 52.7738 | -1.653 | DRAKELOW 132kV
DRAK21 | NGET | B-2-1c, B-3-1c | 275 | DRAKELOW | 52.7738 | -1.653 | DRAKELOW 275kV
DRAK41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | DRAKELOW | 52.7738 | -1.653 | DRAKELOW 400kV
DRAX11 | NGET | B-3-1c | 132 | DRAX | 53.7362 | -0.99241 | DRAX 132kV
DRAX41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | DRAX | 53.7362 | -0.99241 | DRAX 400kV
DRAX42 | NGET | B-2-1c, B-3-1c | 400 | DRAX | 53.7362 | -0.99241 | DRAX 400kV
DRCR1Q | SPT | B-2-1b, B-3-1b | 132 | DRUMCROSS | 55.9064 | -3.5866 | DRUMCROSS 132kV
DRCR1R | SPT | B-2-1b, B-3-1b | 132 | DRUMCROSS | 55.9064 | -3.5866 | DRUMCROSS 132kV
DRCR3- | SPT | B-3-1b | 33 | DRUMCROSS | 55.9064 | -3.5866 | DRUMCROSS 33kV
DRUM2Q | SPT | B-2-1b, B-3-1b | 275 | DRUMCHAPEL | 55.9159 | -4.3485 | DRUMCHAPEL 275kV
DRUM2R | SPT | B-2-1b, B-3-1b | 275 | DRUMCHAPEL | 55.9159 | -4.3485 | DRUMCHAPEL 275kV
DRUM3- | SPT | B-3-1b | 33 | DRUMCHAPEL | 55.9159 | -4.3485 | DRUMCHAPEL 33kV
DUBE1A | SHET | B-2-2a | 132 | DUNBEATH | 58.2654 | -3.4349 | DUNBEATH 132kV
DUBE1B | SHET | B-2-2a | 132 | DUNBEATH | 58.2654 | -3.4349 | DUNBEATH 132kV
DUBE1C | SHET | B-2-2a | 132 | DUNBEATH | 58.2654 | -3.4349 | DUNBEATH 132kV
DUBE1Q | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | DUNBEATH | 58.2654 | -3.4349 | DUNBEATH 132kV
DUBE3- | SHET | B-3-1a | 33 | DUNBEATH | 58.2654 | -3.4349 | DUNBEATH 33kV
DUCC1J | SHET | B-2-1a | 132 | DUNMORE CABLE COMPOUND |  |  | DUNMORE CABLE COMPOUND 132kV
DUCC1K | SHET | B-2-1a | 132 | DUNMORE CABLE COMPOUND |  |  | DUNMORE CABLE COMPOUND 132kV
DUDH1Q | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | DUDHOPE | 56.4631 | -2.9785 | DUDHOPE 132kV
DUDH1R | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | DUDHOPE | 56.4631 | -2.9785 | DUDHOPE 132kV
DUDH3- | SHET | B-3-1a, B-3-2a | 33 | DUDHOPE | 56.4631 | -2.9785 | DUDHOPE 33kV
DUGR1Q | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | DUNVEGAN GRID | 57.4328 | -6.54 | DUNVEGAN GRID 132kV
DUGR3- | SHET | B-3-1a | 33 | DUNVEGAN GRID | 57.4328 | -6.54 | DUNVEGAN GRID 33kV
DUMF1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | DUMFRIES | 55.0672 | -3.5915 | DUMFRIES 132kV
DUMF3A | SPT | B-3-1b | 33 | DUMFRIES | 55.0672 | -3.5915 | DUMFRIES 33kV
DUMF3B | SPT | B-3-1b | 33 | DUMFRIES | 55.0672 | -3.5915 | DUMFRIES 33kV
DUMF3I | SPT | B-3-1b | 33 | DUMFRIES | 55.0672 | -3.5915 | DUMFRIES 33kV
DUNB1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | DUNBAR | 55.9777 | -2.5739 | DUNBAR 132kV
DUNB1R | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | DUNBAR | 55.9777 | -2.5739 | DUNBAR 132kV
DUNB1S | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | DUNBAR | 55.9777 | -2.5739 | DUNBAR 132kV
DUNB1T | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | DUNBAR | 55.9777 | -2.5739 | DUNBAR 132kV
DUNB3A | SPT | B-3-1b | 33 | DUNBAR | 55.9777 | -2.5739 | DUNBAR 33kV
DUNB3B | SPT | B-3-1b | 33 | DUNBAR | 55.9777 | -2.5739 | DUNBAR 33kV
DUNE1- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 132 | DUNLAW EXTENSION |  |  | DUNLAW EXTENSION 132kV
DUNE3- | SPT | B-2-1b, B-2-2b, B-3-1b | 33 | DUNLAW EXTENSION |  |  | DUNLAW EXTENSION 33kV
DUNE3A | SPT | B-3-2b | 33 | DUNLAW EXTENSION |  |  | DUNLAW EXTENSION 33kV
DUNF1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | DUNFERMLINE | 56.0892 | -3.4503 | DUNFERMLINE 132kV
DUNF1R | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | DUNFERMLINE | 56.0892 | -3.4503 | DUNFERMLINE 132kV
DUNF3- | SPT | B-3-1b | 33 | DUNFERMLINE | 56.0892 | -3.4503 | DUNFERMLINE 33kV
DUNG21 | NGET | B-3-1c | 275 | DUNGENESS | 50.915 | 0.94743 | DUNGENESS 275kV
DUNG41 | NGET | B-2-1c, B-3-1c | 400 | DUNGENESS | 50.915 | 0.94743 | DUNGENESS 400kV
DUNH1Q | SPT | B-2-1b | 132 | DUNHILL | 55.3131 | -4.2044 | DUNHILL 132kV
DUNH1R | SPT | B-2-1b | 132 | DUNHILL | 55.3131 | -4.2044 | DUNHILL 132kV
DUNH1S | SPT | B-2-1b, B-3-1b | 132 | DUNHILL | 55.3131 | -4.2044 | DUNHILL 132kV
DUNH1T | SPT | B-2-1b, B-3-1b | 132 | DUNHILL | 55.3131 | -4.2044 | DUNHILL 132kV
DUNH3- | SPT | B-3-1b | 33 | DUNHILL | 55.3131 | -4.2044 | DUNHILL 33kV
DUNM1- | SHET | B-2-1a, B-3-1a | 132 | DUNMAGLASS | 57.2712 | -4.3071 | DUNMAGLASS 132kV
DUNM1C | SHET | B-2-1a | 132 | DUNMAGLASS | 57.2712 | -4.3071 | DUNMAGLASS 132kV
DUNM1T | SHET | B-2-1a, B-2-2a | 132 | DUNMAGLASS | 57.2712 | -4.3071 | DUNMAGLASS 132kV
DUNM3- | SHET | B-3-1a | 33 | DUNMAGLASS | 57.2712 | -4.3071 | DUNMAGLASS 33kV
DUNO1Q | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | DUNOON | 55.9758 | -4.9485 | DUNOON 132kV
DUNO1R | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | DUNOON | 55.9758 | -4.9485 | DUNOON 132kV
DUNO3- | SHET | B-3-1a, B-3-2a | 33 | DUNOON | 55.9758 | -4.9485 | DUNOON 33kV
DWEX3- | SPT | B-2-2b | 33 | DOUGLAS WEST EXTENSION | 55.558 | -3.872 | DOUGLAS WEST EXTENSION 33kV
DYCE1J | SHET | B-2-1a | 132 | DYCE | 57.2162 | -2.1902 | DYCE 132kV
DYCE1Q | SHET | B-2-1a, B-3-1a | 132 | DYCE | 57.2162 | -2.1902 | DYCE 132kV
DYCE1R | SHET | B-2-1a, B-3-1a | 132 | DYCE | 57.2162 | -2.1902 | DYCE 132kV
DYCE1T | SHET | B-2-1a | 132 | DYCE | 57.2162 | -2.1902 | DYCE 132kV
DYCE1U | SHET | B-2-1a | 132 | DYCE | 57.2162 | -2.1902 | DYCE 132kV
DYCE3- | SHET | B-3-1a | 33 | DYCE | 57.2162 | -2.1902 | DYCE 33kV
EALI21 | NGET | B-2-1c, B-3-1c | 275 | EALING | 51.5019 | -0.29614 | EALING 275kV
EALI61 | NGET | B-3-1c | 66 | EALING | 51.5019 | -0.29614 | EALING 66kV
EARR21 | SHET | B-2-2a | 275 | EARRAGHAIL |  |  | EARRAGHAIL 275kV
EARR2A | SHET | B-2-2a | 275 | EARRAGHAIL |  |  | EARRAGHAIL 275kV
EARR2B | SHET | B-2-2a, B-3-2a | 275 | EARRAGHAIL |  |  | EARRAGHAIL 275kV
EARR3- | SHET | B-3-2a | 33 | EARRAGHAIL |  |  | EARRAGHAIL 33kV
EASO11 | NGET | B-3-1c | 132 | EATON SOCON | 52.2146 | -0.30164 | EATON SOCON 132kV
EASO12 | NGET | B-3-1c | 132 | EATON SOCON | 52.2146 | -0.30164 | EATON SOCON 132kV
EASO41 | NGET | B-2-1c, B-3-1c | 400 | EATON SOCON | 52.2146 | -0.30164 | EATON SOCON 400kV
EASO4A | NGET | B-2-1c, B-3-1c | 400 | EATON SOCON | 52.2146 | -0.30164 | EATON SOCON 400kV
EASO4B | NGET | B-2-1c | 400 | EATON SOCON | 52.2146 | -0.30164 | EATON SOCON 400kV
EAST1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | EARLSTOUN | 55.1123 | -4.1742 | EARLSTOUN 132kV
EAST5- | SPT | B-3-1b | 11 | EARLSTOUN | 55.1123 | -4.1742 | EARLSTOUN 11kV
ECCF1J | SPT | B-2-1b | 132 | ECCLEFECHAN | 55.0662 | -3.2853 | ECCLEFECHAN 132kV
ECCF1K | SPT | B-2-1b | 132 | ECCLEFECHAN | 55.0662 | -3.2853 | ECCLEFECHAN 132kV
ECCL1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | ECCLES | 55.67 | -2.3316 | ECCLES 132kV
ECCL3- | SPT | B-3-1b | 33 | ECCLES | 55.67 | -2.3316 | ECCLES 33kV
ECCL3V | SPT | B-4-1b | 33 | ECCLES | 55.67 | -2.3316 | ECCLES 33kV
ECCL4A | SPT | B-2-1b, B-2-2b, B-3-1b, B-4-2b | 400 | ECCLES | 55.67 | -2.3316 | ECCLES 400kV
ECCL4B | SPT | B-2-1b, B-2-2b, B-3-1b, B-4-2b | 400 | ECCLES | 55.67 | -2.3316 | ECCLES 400kV
ECCL4C | SPT | B-2-1b | 400 | ECCLES | 55.67 | -2.3316 | ECCLES 400kV
ECCL4D | SPT | B-2-1b | 400 | ECCLES | 55.67 | -2.3316 | ECCLES 400kV
ECLA11 | NGET | B-3-1c | 132 | EAST CLAYDON | 51.9263 | -0.90719 | EAST CLAYDON 132kV
ECLA12 | NGET | B-3-1c, B-4-1c | 132 | EAST CLAYDON | 51.9263 | -0.90719 | EAST CLAYDON 132kV
ECLA41 | NGET | B-2-1c, B-3-1c, B-4-1c, B-4-2c | 400 | EAST CLAYDON | 51.9263 | -0.90719 | EAST CLAYDON 400kV
EDAY1- | SHET | B-2-2a | 132 | EDAY | 59.1852 | -2.7658 | EDAY 132kV
EDAY1A | SHET | B-2-2a | 132 | EDAY | 59.1852 | -2.7658 | EDAY 132kV
EDAY1B | SHET | B-2-2a | 132 | EDAY | 59.1852 | -2.7658 | EDAY 132kV
EDIN1- | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | EDINBANE 132/33KV | 54.6117 | -5.884 | EDINBANE 132/33KV 132kV
EDIN1A | SHET | B-2-2a, B-4-2a | 132 | EDINBANE 132/33KV | 54.6117 | -5.884 | EDINBANE 132/33KV 132kV
EDIN1B | SHET | B-2-2a, B-4-2a | 132 | EDINBANE 132/33KV | 54.6117 | -5.884 | EDINBANE 132/33KV 132kV
EDIN1C | SHET | B-2-2a | 132 | EDINBANE 132/33KV | 54.6117 | -5.884 | EDINBANE 132/33KV 132kV
EDIN1D | SHET | B-2-2a | 132 | EDINBANE 132/33KV | 54.6117 | -5.884 | EDINBANE 132/33KV 132kV
EDIN1J | SHET | B-2-2a, B-3-2a | 132 | EDINBANE 132/33KV | 54.6117 | -5.884 | EDINBANE 132/33KV 132kV
EDIN1K | SHET | B-2-2a, B-3-2a | 132 | EDINBANE 132/33KV | 54.6117 | -5.884 | EDINBANE 132/33KV 132kV
EDIN3- | SHET | B-3-1a, B-3-2a | 33 | EDINBANE 132/33KV | 54.6117 | -5.884 | EDINBANE 132/33KV 33kV
EDIN3A | SHET | B-3-2a | 33 | EDINBANE 132/33KV | 54.6117 | -5.884 | EDINBANE 132/33KV 33kV
EDIN8A | SHET | B-3-2a, B-4-2a | 22 | EDIN (Node Name used) | 54.6117 | -5.884 | EDIN (Node Name used) 22kV
EDIN8B | SHET | B-3-2a, B-4-2a | 22 | EDIN (Node Name used) | 54.6117 | -5.884 | EDIN (Node Name used) 22kV
EERH2- | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | EASTERHOUSE | 55.8787 | -4.0727 | EASTERHOUSE 275kV
EERH3- | SPT | B-3-1b | 33 | EASTERHOUSE | 55.8787 | -4.0727 | EASTERHOUSE 33kV
EGGB41 | NGET | B-2-1c, B-2-2c | 400 | EGGBOROUGH | 53.7134 | -1.1298 | EGGBOROUGH 400kV
EGGB42 | NGET | B-2-1c, B-2-2c | 400 | EGGBOROUGH | 53.7134 | -1.1298 | EGGBOROUGH 400kV
EKIL2Q | SPT | B-2-1b, B-2-2b | 275 | EAST KILBRIDE | 55.7864 | -4.1941 | EAST KILBRIDE 275kV
EKIL2R | SPT | B-2-1b, B-2-2b | 275 | EAST KILBRIDE | 55.7864 | -4.1941 | EAST KILBRIDE 275kV
EKIL2S | SPT | B-2-1b, B-3-1b | 275 | EAST KILBRIDE | 55.7864 | -4.1941 | EAST KILBRIDE 275kV
EKIL2T | SPT | B-2-1b, B-3-1b | 275 | EAST KILBRIDE | 55.7864 | -4.1941 | EAST KILBRIDE 275kV
EKIL3A | SPT | B-2-1b, B-3-1b | 33 | EAST KILBRIDE | 55.7864 | -4.1941 | EAST KILBRIDE 33kV
EKIL3B | SPT | B-2-1b, B-3-1b | 33 | EAST KILBRIDE | 55.7864 | -4.1941 | EAST KILBRIDE 33kV
EKIS2- | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | EAST KILBRIDE SOUTH | 55.7402 | -4.1636 | EAST KILBRIDE SOUTH 275kV
EKIS3A | SPT | B-3-1b | 33 | EAST KILBRIDE SOUTH | 55.7402 | -4.1636 | EAST KILBRIDE SOUTH 33kV
EKIS3B | SPT | B-3-1b | 33 | EAST KILBRIDE SOUTH | 55.7402 | -4.1636 | EAST KILBRIDE SOUTH 33kV
ELCH1- | SHET | B-2-2a, B-3-2a | 132 | ELCHIES |  |  | ELCHIES 132kV
ELCH3- | SHET | B-3-2a | 33 | ELCHIES |  |  | ELCHIES 33kV
ELDE1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | ELDERSLIE | 55.8408 | -4.4643 | ELDERSLIE 132kV
ELDE1R | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | ELDERSLIE | 55.8408 | -4.4643 | ELDERSLIE 132kV
ELDE3- | SPT | B-3-1b | 33 | ELDERSLIE | 55.8408 | -4.4643 | ELDERSLIE 33kV
ELGI1L | SHET | B-2-1a | 132 | ELGIN | 57.6642 | -3.3207 | ELGIN 132kV
ELGI1M | SHET | B-2-1a | 132 | ELGIN | 57.6642 | -3.3207 | ELGIN 132kV
ELGI1Q | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | ELGIN | 57.6642 | -3.3207 | ELGIN 132kV
ELGI1R | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | ELGIN | 57.6642 | -3.3207 | ELGIN 132kV
ELGI3- | SHET | B-3-1a | 33 | ELGIN | 57.6642 | -3.3207 | ELGIN 33kV
ELIB1- | SHET | B-2-2a | 132 | ELLIBISTER SWITCHING STATION |  |  | ELLIBISTER SWITCHING STATION 132kV
ELIB1A | SHET | B-2-2a | 132 | ELLIBISTER SWITCHING STATION |  |  | ELLIBISTER SWITCHING STATION 132kV
ELLA11 | NGET | B-3-1c | 132 | ELLAND | 53.6939 | -1.8237 | ELLAND 132kV
ELLA12 | NGET | B-3-1c | 132 | ELLAND | 53.6939 | -1.8237 | ELLAND 132kV
ELLA21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | ELLAND | 53.6939 | -1.8237 | ELLAND 275kV
ELST11 | NGET | B-3-1c | 132 | ELSTREE | 51.6615 | -0.34538 | ELSTREE 132kV
ELST11 | NGET | B-3-1c | 132 | ELSTREE | 51.6615 | -0.34538 | ELSTREE 132kV
ELST12 | NGET | B-2-1c, B-3-1c | 132 | ELSTREE | 51.6615 | -0.34538 | ELSTREE 132kV
ELST12 | NGET | B-2-1c, B-3-1c | 132 | ELSTREE | 51.6615 | -0.34538 | ELSTREE 132kV
ELST13 | NGET | B-3-1c | 132 | ELSTREE | 51.6615 | -0.34538 | ELSTREE 132kV
ELST13 | NGET | B-3-1c | 132 | ELSTREE | 51.6615 | -0.34538 | ELSTREE 132kV
ELST21 | NGET | B-2-1c, B-3-1c | 275 | ELSTREE | 51.6615 | -0.34538 | ELSTREE 275kV
ELST22 | NGET | B-2-1c, B-3-1c | 275 | ELSTREE | 51.6615 | -0.34538 | ELSTREE 275kV
ELST41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c, B-4-2c | 400 | ELSTREE | 51.6615 | -0.34538 | ELSTREE 400kV
ELST4A | NGET | B-2-1c, B-2-2c | 400 | ELSTREE | 51.6615 | -0.34538 | ELSTREE 400kV
ELST4B | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | ELSTREE | 51.6615 | -0.34538 | ELSTREE 400kV
ELVA1- | SPT | B-2-2b, B-3-1b | 132 | ELVANFOOT | 55.4382 | -3.6715 | ELVANFOOT 132kV
ELVA2Q | SPT | B-2-1b, B-3-1b | 275 | ELVANFOOT | 55.4382 | -3.6715 | ELVANFOOT 275kV
ELVA2R | SPT | B-2-1b, B-3-1b | 275 | ELVANFOOT | 55.4382 | -3.6715 | ELVANFOOT 275kV
ELVA3A | SPT | B-2-1b, B-3-1b | 33 | ELVANFOOT | 55.4382 | -3.6715 | ELVANFOOT 33kV
ELVA3V | SPT | B-4-1b | 33 | ELVANFOOT | 55.4382 | -3.6715 | ELVANFOOT 33kV
ELVA4- | SPT | B-2-1b, B-2-2b, B-3-1b, B-4-1b | 400 | ELVANFOOT | 55.4382 | -3.6715 | ELVANFOOT 400kV
EMMO4J | SHET | B-2-2a, B-3-2a | 400 | EMMOCK |  |  | EMMOCK 400kV
EMMO4K | SHET | B-2-2a, B-3-2a | 400 | EMMOCK |  |  | EMMOCK 400kV
ENDE11 | NGET | B-3-1c | 132 | ENDERBY | 52.5976 | -1.217 | ENDERBY 132kV
ENDE41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | ENDERBY | 52.5976 | -1.217 | ENDERBY 400kV
ENEI1- | SHET | B-2-2a | 132 | ENERGY ISLES WIND FARM |  |  | ENERGY ISLES WIND FARM 132kV
ENEI1N | SHET | B-2-2a | 132 | ENERGY ISLES WIND FARM |  |  | ENERGY ISLES WIND FARM 132kV
ENHI1- | SPT | B-2-1b | 132 | ENOCH HILL WIND FARM |  |  | ENOCH HILL WIND FARM 132kV
ENHI3- | SPT | B-2-2b | 33 | ENOCH HILL WIND FARM |  |  | ENOCH HILL WIND FARM 33kV
ERED2- | SHET | B-2-2a, B-3-2a | 275 | EREDINE | 56.2354 | -5.2781 | EREDINE 275kV
ERED3- | SHET | B-3-2a | 33 | EREDINE | 56.2354 | -5.2781 | EREDINE 33kV
ERRO1A | SHET | B-2-1a, B-3-1a | 132 | ERROCHTY | 56.7075 | -4.0096 | ERROCHTY 132kV
ERRO1B | SHET | B-2-1a, B-3-1a | 132 | ERROCHTY | 56.7075 | -4.0096 | ERROCHTY 132kV
ERRO1J | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | ERROCHTY | 56.7075 | -4.0096 | ERROCHTY 132kV
ERRO1K | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | ERROCHTY | 56.7075 | -4.0096 | ERROCHTY 132kV
ERRO1T | SHET | B-2-1a, B-3-1a | 132 | ERROCHTY | 56.7075 | -4.0096 | ERROCHTY 132kV
ERRO3- | SHET | B-3-2a | 33 | ERROCHTY | 56.7075 | -4.0096 | ERROCHTY 33kV
ERRO5J | SHET | B-3-1a | 11 | ERROCHTY | 56.7075 | -4.0096 | ERROCHTY 11kV
ERRO5L | SHET | B-3-1a | 11 | ERROCHTY | 56.7075 | -4.0096 | ERROCHTY 11kV
ERSK1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | ERSKINE | 55.9036 | -4.4828 | ERSKINE 132kV
ERSK1R | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | ERSKINE | 55.9036 | -4.4828 | ERSKINE 132kV
ERSK3- | SPT | B-3-1b | 33 | ERSKINE | 55.9036 | -4.4828 | ERSKINE 33kV
ESST1- | SPT | B-2-1b | 132 | ESSENSIDE |  |  | ESSENSIDE 132kV
ESST1Q | SPT | B-2-1b | 132 | ESSENSIDE |  |  | ESSENSIDE 132kV
EUCH1- | SPT | B-2-2b, B-3-2b | 132 | EUCHANHEAD |  |  | EUCHANHEAD 132kV
EUCH3- | SPT | B-3-2b | 33 | EUCHANHEAD |  |  | EUCHANHEAD 33kV
EWEH1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | EWE HILL | 55.1425 | -3.1788 | EWE HILL 132kV
EWEH3- | SPT | B-2-1b, B-2-2b, B-3-1b | 33 | EWE HILL | 55.1425 | -3.1788 | EWE HILL 33kV
EXET11 | NGET | B-3-1c, B-4-1c | 132 | EXETER | 50.7676 | -3.4052 | EXETER 132kV
EXET41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | EXETER | 50.7676 | -3.4052 | EXETER 400kV
FAAR1Q | SHET | B-2-1a, B-3-1a | 132 | FARR WINDFARM | 57.3363 | -4.161 | FARR WINDFARM 132kV
FAAR1R | SHET | B-2-1a, B-3-1a | 132 | FARR WINDFARM | 57.3363 | -4.161 | FARR WINDFARM 132kV
FAAR3J | SHET | B-3-1a | 33 | FARR WINDFARM | 57.3363 | -4.161 | FARR WINDFARM 33kV
FAAR3K | SHET | B-3-1a | 33 | FARR WINDFARM | 57.3363 | -4.161 | FARR WINDFARM 33kV
FALL3A | SPT | B-3-1b | 33 | FALLAGO | 55.8255 | -2.6668 | FALLAGO 33kV
FALL3B | SPT | B-3-1b | 33 | FALLAGO | 55.8255 | -2.6668 | FALLAGO 33kV
FALL3C | SPT | B-3-2b | 33 | FALLAGO | 55.8255 | -2.6668 | FALLAGO 33kV
FALL4- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 400 | FALLAGO | 55.8255 | -2.6668 | FALLAGO 400kV
FARI1J | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | FARIGAIG | 57.3183 | -4.3746 | FARIGAIG 132kV
FARI1K | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | FARIGAIG | 57.3183 | -4.3746 | FARIGAIG 132kV
FARI2J | SHET | B-2-1a, B-3-1a, B-3-2a | 275 | FARIGAIG | 57.3183 | -4.3746 | FARIGAIG 275kV
FARI2K | SHET | B-2-1a, B-3-1a, B-3-2a | 275 | FARIGAIG | 57.3183 | -4.3746 | FARIGAIG 275kV
FASI1- | SPT | B-2-2b | 132 | FAW SIDE |  |  | FAW SIDE 132kV
FASI1A | SPT | B-2-2b | 132 | FAW SIDE |  |  | FAW SIDE 132kV
FASI1B | SPT | B-2-2b | 132 | FAW SIDE |  |  | FAW SIDE 132kV
FASN1A | SHET | B-2-2a, B-3-2a | 132 | FASNAKYLE | 57.3301 | -4.7935 | FASNAKYLE 132kV
FASN1B | SHET | B-2-2a, B-3-2a | 132 | FASNAKYLE | 57.3301 | -4.7935 | FASNAKYLE 132kV
FASN2- | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 275 | FASNAKYLE | 57.3301 | -4.7935 | FASNAKYLE 275kV
FASN3- | SHET | B-3-1a, B-3-2a | 33 | FASNAKYLE | 57.3301 | -4.7935 | FASNAKYLE 33kV
FASQ1- | SHET | B-2-2a | 132 | FASQUE |  |  | FASQUE 132kV
FASQ1J | SHET | B-2-2a, B-3-2a | 132 | FASQUE |  |  | FASQUE 132kV
FASQ3- | SHET | B-3-2a | 33 | FASQUE |  |  | FASQUE 33kV
FAUG1- | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 132kV
FAUG1J | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 132kV
FAUG1K | SHET | B-2-1a, B-3-1a | 132 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 132kV
FAUG1M | SHET | B-2-1a, B-2-2a | 132 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 132kV
FAUG1N | SHET | B-2-1a, B-2-2a | 132 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 132kV
FAUG1P | SHET | B-2-1a, B-2-2a | 132 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 132kV
FAUG1Q | SHET | B-2-1a, B-3-1a | 132 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 132kV
FAUG1R | SHET | B-2-2a | 132 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 132kV
FAUG1S | SHET | B-2-2a | 132 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 132kV
FAUG2J | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 275 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 275kV
FAUG2K | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 275 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 275kV
FAUG2T | SHET | B-2-2a, B-3-2a | 275 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 275kV
FAUG3- | SHET | B-3-1a | 33 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 33kV
FAUG3W | SHET | B-4-1a | 33 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 33kV
FAUG3X | SHET | B-4-1a | 33 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 33kV
FAUG3Y | SHET | B-4-1a | 33 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 33kV
FAUG3Z | SHET | B-4-1a | 33 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 33kV
FAUG4J | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 400 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 400kV
FAUG4K | SHET | B-2-1a, B-2-2a, B-3-1a | 400 | FORT AUGUSTUS | 57.1366 | -4.7199 | FORT AUGUSTUS 400kV
FAWL11 | NGET | B-3-1c | 132 | FAWLEY | 50.8217 | -1.3286 | FAWLEY 132kV
FAWL41 | NGET | B-2-1c, B-3-1c | 400 | FAWLEY | 50.8217 | -1.3286 | FAWLEY 400kV
FECK21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | FECKENHAM | 52.2499 | -1.9719 | FECKENHAM 275kV
FECK41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c, B-4-2c | 400 | FECKENHAM | 52.2499 | -1.9719 | FECKENHAM 400kV
FECK61 | NGET | B-3-1c | 66 | FECKENHAM | 52.2499 | -1.9719 | FECKENHAM 66kV
FELL1- | SPT | B-2-2b, B-3-2b | 132 | FELL WIND FARM |  |  | FELL WIND FARM 132kV
FELL3- | SPT | B-3-2b | 33 | FELL WIND FARM |  |  | FELL WIND FARM 33kV
FENW4A | NGET | B-2-1c | 400 | FENWICK TEE | 53.6394 | -1.1025 | FENWICK TEE 400kV
FERO1- | SHET | B-2-1a, B-3-1a | 132 | FERNOCH WIND |  |  | FERNOCH WIND 132kV
FERO1S | SHET | B-2-1a, B-2-2a | 132 | FERNOCH WIND |  |  | FERNOCH WIND 132kV
FERO3- | SHET | B-3-1a | 33 | FERNOCH WIND |  |  | FERNOCH WIND 33kV
FERR11 | NGET | B-3-1c | 132 | FERRYBRIDGE | 53.7173 | -1.2849 | FERRYBRIDGE 132kV
FERR21 | NGET | B-2-1c, B-3-1c | 275 | FERRYBRIDGE | 53.7173 | -1.2849 | FERRYBRIDGE 275kV
FERR22 | NGET | B-2-1c, B-3-1c | 275 | FERRYBRIDGE | 53.7173 | -1.2849 | FERRYBRIDGE 275kV
FERR23 | NGET | B-2-1c, B-3-1c | 275 | FERRYBRIDGE | 53.7173 | -1.2849 | FERRYBRIDGE 275kV
FERR2A | NGET | B-2-1c, B-3-1c | 275 | FERRYBRIDGE | 53.7173 | -1.2849 | FERRYBRIDGE 275kV
FERR2B | NGET | B-2-1c | 275 | FERRYBRIDGE | 53.7173 | -1.2849 | FERRYBRIDGE 275kV
FERR4A | NGET | B-2-1c, B-3-1c | 400 | FERRYBRIDGE | 53.7173 | -1.2849 | FERRYBRIDGE 400kV
FERR61 | NGET | B-3-1c | 66 | FERRYBRIDGE | 53.7173 | -1.2849 | FERRYBRIDGE 66kV
FETT1- | SHET | B-2-2a, B-3-1a, B-3-2a | 132 | FETTERESSO | 56.9655 | -2.3491 | FETTERESSO 132kV
FETT2P | SHET | B-2-1a, B-2-2a | 275 | FETTERESSO | 56.9655 | -2.3491 | FETTERESSO 275kV
FETT2Q | SHET | B-2-1a, B-2-2a | 275 | FETTERESSO | 56.9655 | -2.3491 | FETTERESSO 275kV
FETT2R | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 275 | FETTERESSO | 56.9655 | -2.3491 | FETTERESSO 275kV
FETT3S | SHET | B-3-1a | 33 | FETTERESSO | 56.9655 | -2.3491 | FETTERESSO 33kV
FETT4J | SHET | B-2-2a, B-3-2a | 400 | FETTERESSO | 56.9655 | -2.3491 | FETTERESSO 400kV
FETT4K | SHET | B-2-2a, B-3-2a | 400 | FETTERESSO | 56.9655 | -2.3491 | FETTERESSO 400kV
FETT4Q | SHET | B-2-2a | 400 | FETTERESSO | 56.9655 | -2.3491 | FETTERESSO 400kV
FETT4R | SHET | B-2-2a | 400 | FETTERESSO | 56.9655 | -2.3491 | FETTERESSO 400kV
FFES21 | NGET | B-2-1c | 275 | FFESTINIOG | 52.9807 | -3.969 | FFESTINIOG 275kV
FFES22 | NGET | B-2-1c | 275 | FFESTINIOG | 52.9807 | -3.969 | FFESTINIOG 275kV
FIDD1A | SHET | B-2-1a | 132 | FIDDES | 56.9245 | -2.3026 | FIDDES 132kV
FIDD1B | SHET | B-2-1a, B-3-1a | 132 | FIDDES | 56.9245 | -2.3026 | FIDDES 132kV
FIDD1Q | SHET | B-2-1a, B-3-1a | 132 | FIDDES | 56.9245 | -2.3026 | FIDDES 132kV
FIDD1R | SHET | B-2-1a, B-3-1a | 132 | FIDDES | 56.9245 | -2.3026 | FIDDES 132kV
FIDD3- | SHET | B-3-1a | 33 | FIDDES | 56.9245 | -2.3026 | FIDDES 33kV
FIDF11 | NGET | B-3-1c | 132 | FIDDLERS FERRY | 53.3713 | -2.6891 | FIDDLERS FERRY 132kV
FIDF12 | NGET | B-3-1c | 132 | FIDDLERS FERRY | 53.3713 | -2.6891 | FIDDLERS FERRY 132kV
FIDF21 | NGET | B-2-1c, B-3-1c | 275 | FIDDLERS FERRY | 53.3713 | -2.6891 | FIDDLERS FERRY 275kV
FIGS2- | SPT | B-2-2b | 275 | FIFE GRID SERVICES |  |  | FIFE GRID SERVICES 275kV
FINL1Q | SHET | B-2-1a, B-3-1a | 132 | FINLARIG |  |  | FINLARIG 132kV
FINL5- | SHET | B-3-1a | 11 | FINLARIG |  |  | FINLARIG 11kV
FINN1Q | SPT | B-2-1b, B-3-1b | 132 | FINNIESTON | 55.865 | -4.286 | FINNIESTON 132kV
FINN1R | SPT | B-2-1b, B-3-1b | 132 | FINNIESTON | 55.865 | -4.286 | FINNIESTON 132kV
FINN3- | SPT | B-3-1b | 33 | FINNIESTON | 55.865 | -4.286 | FINNIESTON 33kV
FINS1- | SHET | B-2-2a, B-3-2a, B-4-2a | 132 | ORKNEY FINSTOWN | 51.924 | -1.7701 | ORKNEY FINSTOWN 132kV
FINS2A | SHET | B-2-2a, B-3-2a | 275 | ORKNEY FINSTOWN | 51.924 | -1.7701 | ORKNEY FINSTOWN 275kV
FINS2B | SHET | B-2-2a | 275 | ORKNEY FINSTOWN | 51.924 | -1.7701 | ORKNEY FINSTOWN 275kV
FINS2C | SHET | B-2-2a | 275 | ORKNEY FINSTOWN | 51.924 | -1.7701 | ORKNEY FINSTOWN 275kV
FINS3- | SHET | B-3-2a | 33 | ORKNEY FINSTOWN | 51.924 | -1.7701 | ORKNEY FINSTOWN 33kV
FINS3Y | SHET | B-4-2a | 33 | ORKNEY FINSTOWN | 51.924 | -1.7701 | ORKNEY FINSTOWN 33kV
FLEE11 | NGET | B-3-1c, B-4-1c | 132 | FLEET | 51.2513 | -0.88336 | FLEET 132kV
FLEE12 | NGET | B-3-1c | 132 | FLEET | 51.2513 | -0.88336 | FLEET 132kV
FLEE41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | FLEET | 51.2513 | -0.88336 | FLEET 400kV
FLIB41 | NGET | B-2-1c | 400 | FLINTSHIRE BRIDGE | 53.2383 | -3.0455 | FLINTSHIRE BRIDGE 400kV
FNLN4A | SHET | B-2-2a | 400 | FANELLAN |  |  | FANELLAN 400kV
FNLN4B | SHET | B-2-2a | 400 | FANELLAN |  |  | FANELLAN 400kV
FNLN4R | SHET | B-2-2a | 400 | FANELLAN |  |  | FANELLAN 400kV
FOGG1Q | SHET | B-2-1a | 132 | FOGGIETON |  |  | FOGGIETON 132kV
FOGG1R | SHET | B-2-1a | 132 | FOGGIETON |  |  | FOGGIETON 132kV
FOUR21 | NGET | B-2-1c, B-3-1c | 275 | FOURSTONES | 55.0118 | -2.1642 | FOURSTONES 275kV
FOUR31 | NGET | B-3-1c | 33 | FOURSTONES | 55.0118 | -2.1642 | FOURSTONES 33kV
FOUR71 | NGET | B-3-1c | 25 | FOUR (Node Name used) | 55.0118 | -2.1642 | FOUR (Node Name used) 25kV
FOUX41 | NGET | B-2-2c | 400 | FOUR CROSSES | 52.7611 | -3.0864 | FOUR CROSSES 400kV
FOYE2- | SHET | B-2-1a, B-2-2a | 275 | FOYERS | 57.2691 | -4.4743 | FOYERS 275kV
FOYE2- | SHET | B-2-1a, B-2-2a | 275 | FOYERS | 57.2691 | -4.4743 | FOYERS 275kV
FOYE2J | SHET | B-2-1a, B-2-2a | 275 | FOYERS | 57.2691 | -4.4743 | FOYERS 275kV
FOYE2J | SHET | B-2-1a, B-2-2a | 275 | FOYERS | 57.2691 | -4.4743 | FOYERS 275kV
FRAS1Q | SHET | B-2-1a, B-3-1a | 132 | FRASERBURGH | 57.6859 | -2.0244 | FRASERBURGH 132kV
FRAS1R | SHET | B-2-1a, B-3-1a | 132 | FRASERBURGH | 57.6859 | -2.0244 | FRASERBURGH 132kV
FRAS3- | SHET | B-3-1a | 33 | FRASERBURGH | 57.6859 | -2.0244 | FRASERBURGH 33kV
FRIN4A | NGET | B-2-1c | 400 | FRISTON NORTH | 52.1976 | 1.5295 | FRISTON NORTH 400kV
FRIN4B | NGET | B-2-1c | 400 | FRISTON NORTH | 52.1976 | 1.5295 | FRISTON NORTH 400kV
FRIS41 | NGET | B-2-1c | 400 | FRISTON | 52.1976 | 1.5295 | FRISTON 400kV
FRIS4A | NGET | B-2-1c | 400 | FRISTON | 52.1976 | 1.5295 | FRISTON 400kV
FRIS4B | NGET | B-2-1c | 400 | FRISTON | 52.1976 | 1.5295 | FRISTON 400kV
FRIS4C | NGET | B-2-1c | 400 | FRISTON | 52.1976 | 1.5295 | FRISTON 400kV
FRIS4D | NGET | B-2-1c | 400 | FRISTON | 52.1976 | 1.5295 | FRISTON 400kV
FROD11 | NGET | B-3-1c | 132 | FRODSHAM | 53.3087 | -2.716 | FRODSHAM 132kV
FROD21 | NGET | B-2-1c, B-3-1c | 275 | FRODSHAM | 53.3087 | -2.716 | FRODSHAM 275kV
FROD22 | NGET | B-2-1c, B-3-1c | 275 | FRODSHAM | 53.3087 | -2.716 | FRODSHAM 275kV
FROD41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | FRODSHAM | 53.3087 | -2.716 | FRODSHAM 400kV
FWIL1Q | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | FORT WILLIAM | 56.8204 | -5.0779 | FORT WILLIAM 132kV
FWIL1R | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | FORT WILLIAM | 56.8204 | -5.0779 | FORT WILLIAM 132kV
FWIL3- | SHET | B-3-1a | 33 | FORT WILLIAM | 56.8204 | -5.0779 | FORT WILLIAM 33kV
FYRI1J | SHET | B-2-1a, B-3-1a | 132 | FYRISH | 57.7001 | -4.3001 | FYRISH 132kV
FYRI1K | SHET | B-2-1a, B-3-1a | 132 | FYRISH | 57.7001 | -4.3001 | FYRISH 132kV
FYRI2J | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | FYRISH | 57.7001 | -4.3001 | FYRISH 275kV
FYRI2K | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | FYRISH | 57.7001 | -4.3001 | FYRISH 275kV
FYRI2L | SHET | B-2-2a | 275 | FYRISH | 57.7001 | -4.3001 | FYRISH 275kV
FYRI2M | SHET | B-2-2a | 275 | FYRISH | 57.7001 | -4.3001 | FYRISH 275kV
GALA0J | SPT | B-3-2b | Unknown | GALA (Node Name used) | 55.6109 | -2.7719 | GALA (Node Name used) UnknownkV
GALA0K | SPT | B-3-2b | Unknown | GALA (Node Name used) | 55.6109 | -2.7719 | GALA (Node Name used) UnknownkV
GALA1- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 132 | GALASHIELS | 55.6109 | -2.7719 | GALASHIELS 132kV
GALA1- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 132 | GALASHIELS | 55.6109 | -2.7719 | GALASHIELS 132kV
GALA3- | SPT | B-3-1b | 33 | GALASHIELS | 55.6109 | -2.7719 | GALASHIELS 33kV
GALN1Q | SPT | B-2-2b, B-3-2b | 132 | GALA NORTH |  |  | GALA NORTH 132kV
GALN1R | SPT | B-2-2b, B-3-2b | 132 | GALA NORTH |  |  | GALA NORTH 132kV
GALN4- | SPT | B-2-2b, B-3-2b | 400 | GALA NORTH |  |  | GALA NORTH 400kV
GARB1Q | SHET, SPT | B-2-1a, B-2-1b, B-2-2a | 132 | GARELOCH BOUNDARY |  |  | GARELOCH BOUNDARY 132kV
GARB1Q | SHET, SPT | B-2-1a, B-2-1b, B-2-2a | 132 | GARELOCH BOUNDARY |  |  | GARELOCH BOUNDARY 132kV
GARB1R | SHET, SPT | B-2-1a, B-2-1b, B-2-2a | 132 | GARELOCH BOUNDARY |  |  | GARELOCH BOUNDARY 132kV
GARB1R | SHET, SPT | B-2-1a, B-2-1b, B-2-2a | 132 | GARELOCH BOUNDARY |  |  | GARELOCH BOUNDARY 132kV
GARB1S | SHET, SPT | B-2-1a, B-2-1b, B-2-2a | 132 | GARELOCH BOUNDARY |  |  | GARELOCH BOUNDARY 132kV
GARB1S | SHET, SPT | B-2-1a, B-2-1b, B-2-2a | 132 | GARELOCH BOUNDARY |  |  | GARELOCH BOUNDARY 132kV
GARB1T | SHET, SPT | B-2-1a, B-2-1b, B-2-2a | 132 | GARELOCH BOUNDARY |  |  | GARELOCH BOUNDARY 132kV
GARB1T | SHET, SPT | B-2-1a, B-2-1b, B-2-2a | 132 | GARELOCH BOUNDARY |  |  | GARELOCH BOUNDARY 132kV
GARE1S | SPT | B-2-1b | 132 | GARELOCH | 56.084 | -4.831 | GARELOCH 132kV
GARE1T | SPT | B-2-1b | 132 | GARELOCH | 56.084 | -4.831 | GARELOCH 132kV
GART4A | NGET | B-2-1c | 400 | GARTH CABLE COMPOUND | 53.6437 | -0.72549 | GARTH CABLE COMPOUND 400kV
GART4B | NGET | B-2-1c, B-2-2c | 400 | GARTH CABLE COMPOUND | 53.6437 | -0.72549 | GARTH CABLE COMPOUND 400kV
GAWH1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | GALAWHISTLE | 55.5625 | -3.9467 | GALAWHISTLE 132kV
GAWH3- | SPT | B-2-1b, B-3-1b | 33 | GALAWHISTLE | 55.5625 | -3.9467 | GALAWHISTLE 33kV
GHPS1- | SPT | B-2-2b, B-3-2b | 132 | GLENMUCKLOCH HYDRO PUMPED STORAGE |  |  | GLENMUCKLOCH HYDRO PUMPED STORAGE 132kV
GHPS3A | SPT | B-3-2b | 33 | GLENMUCKLOCH HYDRO PUMPED STORAGE |  |  | GLENMUCKLOCH HYDRO PUMPED STORAGE 33kV
GHPS3B | SPT | B-3-2b | 33 | GLENMUCKLOCH HYDRO PUMPED STORAGE |  |  | GLENMUCKLOCH HYDRO PUMPED STORAGE 33kV
GHPS4- | SPT | B-2-2b, B-3-2b | 400 | GLENMUCKLOCH HYDRO PUMPED STORAGE |  |  | GLENMUCKLOCH HYDRO PUMPED STORAGE 400kV
GIFF2Q | SPT | B-2-1b, B-3-1b, B-3-2b | 275 | GIFFNOCK | 55.798 | -4.3 | GIFFNOCK 275kV
GIFF2R | SPT | B-2-1b, B-3-1b, B-3-2b | 275 | GIFFNOCK | 55.798 | -4.3 | GIFFNOCK 275kV
GIFF3A | SPT | B-3-1b, B-3-2b | 33 | GIFFNOCK | 55.798 | -4.3 | GIFFNOCK 33kV
GIFF3B | SPT | B-3-1b, B-3-2b | 33 | GIFFNOCK | 55.798 | -4.3 | GIFFNOCK 33kV
GILB1J | SHET | B-2-2a | 132 | GILLS BAY SUBSTATION |  |  | GILLS BAY SUBSTATION 132kV
GILB1K | SHET | B-2-2a | 132 | GILLS BAY SUBSTATION |  |  | GILLS BAY SUBSTATION 132kV
GILB1L | SHET | B-2-2a | 132 | GILLS BAY SUBSTATION |  |  | GILLS BAY SUBSTATION 132kV
GILB1M | SHET | B-2-2a | 132 | GILLS BAY SUBSTATION |  |  | GILLS BAY SUBSTATION 132kV
GLAG1Q | SHET | B-2-1a, B-2-2a | 132 | GLENAGNES | 56.4621 | -2.9963 | GLENAGNES 132kV
GLAG1R | SHET | B-2-1a, B-2-2a | 132 | GLENAGNES | 56.4621 | -2.9963 | GLENAGNES 132kV
GLAG1S | SHET | B-2-2a | 132 | GLENAGNES | 56.4621 | -2.9963 | GLENAGNES 132kV
GLAG1T | SHET | B-2-2a | 132 | GLENAGNES | 56.4621 | -2.9963 | GLENAGNES 132kV
GLAP3- | SPT | B-2-1b | 33 | GLEN APP | 55.0225 | -5.006 | GLEN APP 33kV
GLDO1G | SHET | B-2-1a, B-3-1a | 132 | GLENDOE SUBSTATION | 57.143 | -4.6449 | GLENDOE SUBSTATION 132kV
GLDO8- | SHET | B-3-1a | 22 | GLDO (Node Name used) | 57.143 | -4.6449 | GLDO (Node Name used) 22kV
GLDY1- | SHET | B-2-2a | 132 | GLENDYE |  |  | GLENDYE 132kV
GLEN1Q | SHET | B-2-1a, B-3-1a | 132 | GLENMORISTON | 57.2018 | -4.7202 | GLENMORISTON 132kV
GLEN5- | SHET | B-3-1a | 11 | GLENMORISTON | 57.2018 | -4.7202 | GLENMORISTON 11kV
GLFA1- | SHET | B-2-1a, B-3-1a | 132 | GLENFARCLAS | 57.4157 | -3.3158 | GLENFARCLAS 132kV
GLFA3- | SHET | B-3-1a | 33 | GLENFARCLAS | 57.4157 | -3.3158 | GLENFARCLAS 33kV
GLGL1- | SPT | B-2-2b | 132 | GLENGLASS | 55.3375 | -4.0176 | GLENGLASS 132kV
GLGL1B | SPT | B-2-2b | 132 | GLENGLASS | 55.3375 | -4.0176 | GLENGLASS 132kV
GLGL1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | GLENGLASS | 55.3375 | -4.0176 | GLENGLASS 132kV
GLGL1R | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | GLENGLASS | 55.3375 | -4.0176 | GLENGLASS 132kV
GLGL3- | SPT | B-2-1b, B-2-2b, B-3-1b | 33 | GLENGLASS | 55.3375 | -4.0176 | GLENGLASS 33kV
GLKO1- | SHET | B-2-1a | 132 | GLEN KYLLACHY | 57.3152 | -4.0878 | GLEN KYLLACHY 132kV
GLLE1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | GLENLEE | 55.0996 | -4.1855 | GLENLEE 132kV
GLLE5- | SPT | B-3-1b | 11 | GLENLEE | 55.0996 | -4.1855 | GLENLEE 11kV
GLLU1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | GLENLUCE | 54.882 | -4.8071 | GLENLUCE 132kV
GLLU1R | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | GLENLUCE | 54.882 | -4.8071 | GLENLUCE 132kV
GLLU3- | SPT | B-3-1b | 33 | GLENLUCE | 54.882 | -4.8071 | GLENLUCE 33kV
GLMU3- | SPT | B-2-2b | 33 | GLENMUCKLOCH |  |  | GLENMUCKLOCH 33kV
GLNI1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | GLENNISTON | 56.1114 | -3.272 | GLENNISTON 132kV
GLNI3- | SPT | B-3-1b | 33 | GLENNISTON | 56.1114 | -3.272 | GLENNISTON 33kV
GLNU1- | SHET | B-2-2a, B-3-2a | 132 | GLEN ULLINISH WINDFARM |  |  | GLEN ULLINISH WINDFARM 132kV
GLNU3- | SHET | B-3-2a | 33 | GLEN ULLINISH WINDFARM |  |  | GLEN ULLINISH WINDFARM 33kV
GLRB2- | SHET, SPT | B-2-1a, B-2-1b, B-2-2a, B-2-2b | 275 | GLENROTHES BOUNDARY | 56.2068 | -3.2003 | GLENROTHES BOUNDARY 275kV
GLRB2- | SHET, SPT | B-2-1a, B-2-1b, B-2-2a, B-2-2b | 275 | GLENROTHES BOUNDARY | 56.2068 | -3.2003 | GLENROTHES BOUNDARY 275kV
GLRB4- | SHET, SPT | B-2-2a, B-2-2b | 400 | GLENROTHES BOUNDARY | 56.2068 | -3.2003 | GLENROTHES BOUNDARY 400kV
GLRB4- | SHET, SPT | B-2-2a, B-2-2b | 400 | GLENROTHES BOUNDARY | 56.2068 | -3.2003 | GLENROTHES BOUNDARY 400kV
GLRO2- | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | GLENROTHES | 56.2068 | -3.2003 | GLENROTHES 275kV
GLRO3A | SPT | B-3-1b | 33 | GLENROTHES | 56.2068 | -3.2003 | GLENROTHES 33kV
GLRO3B | SPT | B-3-1b | 33 | GLENROTHES | 56.2068 | -3.2003 | GLENROTHES 33kV
GLUE1- | SHET | B-2-2a | 132 | GLEN ULLINISH EXTENSION |  |  | GLEN ULLINISH EXTENSION 132kV
GNSH1- | SPT | B-2-2b, B-3-2b | 132 | GLENSHIMMEROCH |  |  | GLENSHIMMEROCH 132kV
GNSH3- | SPT | B-3-2b | 33 | GLENSHIMMEROCH |  |  | GLENSHIMMEROCH 33kV
GORG1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | GORGIE | 55.9361 | -3.2365 | GORGIE 132kV
GORG1R | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | GORGIE | 55.9361 | -3.2365 | GORGIE 132kV
GORG3- | SPT | B-3-1b | 33 | GORGIE | 55.9361 | -3.2365 | GORGIE 33kV
GORW2- | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | GORDONBUSH WINDFARM | 58.1149 | -3.9572 | GORDONBUSH WINDFARM 275kV
GORW3- | SHET | B-3-1a | 33 | GORDONBUSH WINDFARM | 58.1149 | -3.9572 | GORDONBUSH WINDFARM 33kV
GOVA1Q | SPT | B-2-1b, B-3-1b | 132 | GOVAN | 55.8549 | -4.3169 | GOVAN 132kV
GOVA1R | SPT | B-2-1b, B-3-1b | 132 | GOVAN | 55.8549 | -4.3169 | GOVAN 132kV
GOVA3- | SPT | B-3-1b | 33 | GOVAN | 55.8549 | -4.3169 | GOVAN 33kV
GRAI11 | NGET | B-3-1c | 132 | GRAIN | 51.4451 | 0.71579 | GRAIN 132kV
GRAI41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | GRAIN | 51.4451 | 0.71579 | GRAIN 400kV
GRAN61 | NGET | B-3-1c | 66 | GRANGE | 51.5629 | -3.7539 | GRANGE 66kV
GREM1J | SHET | B-2-2a, B-3-2a | 132 | GREMISTA | 60.1666 | -1.1643 | GREMISTA 132kV
GREM1K | SHET | B-2-2a, B-3-2a | 132 | GREMISTA | 60.1666 | -1.1643 | GREMISTA 132kV
GREM1L | SHET | B-2-2a | 132 | GREMISTA | 60.1666 | -1.1643 | GREMISTA 132kV
GREM1M | SHET | B-2-2a | 132 | GREMISTA | 60.1666 | -1.1643 | GREMISTA 132kV
GREM1N | SHET | B-2-2a, B-3-2a | 132 | GREMISTA | 60.1666 | -1.1643 | GREMISTA 132kV
GREM1P | SHET | B-2-2a | 132 | GREMISTA | 60.1666 | -1.1643 | GREMISTA 132kV
GREM1Q | SHET | B-2-2a | 132 | GREMISTA | 60.1666 | -1.1643 | GREMISTA 132kV
GREM3- | SHET | B-3-2a | 33 | GREMISTA | 60.1666 | -1.1643 | GREMISTA 33kV
GREN11 | NGET | B-3-1c, B-4-1c | 132 | GRENDON | 52.2431 | -0.72894 | GRENDON 132kV
GREN12 | NGET | B-3-1c | 132 | GRENDON | 52.2431 | -0.72894 | GRENDON 132kV
GREN41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | GRENDON | 52.2431 | -0.72894 | GRENDON 400kV
GRIF1S | SHET | B-2-1a, B-3-1a | 132 | GRIFFIN WINDFARM (SSE) |  |  | GRIFFIN WINDFARM (SSE) 132kV
GRIF1T | SHET | B-2-1a, B-3-1a | 132 | GRIFFIN WINDFARM (SSE) |  |  | GRIFFIN WINDFARM (SSE) 132kV
GRIF36 | SHET | B-3-1a | 33 | GRIFFIN WINDFARM (SSE) |  |  | GRIFFIN WINDFARM (SSE) 33kV
GRIF38 | SHET | B-3-1a | 33 | GRIFFIN WINDFARM (SSE) |  |  | GRIFFIN WINDFARM (SSE) 33kV
GRIW11 | NGET | B-3-1c | 132 | GRIMSBY WEST | 53.5653 | -0.15236 | GRIMSBY WEST 132kV
GRIW12 | NGET | B-3-1c | 132 | GRIMSBY WEST | 53.5653 | -0.15236 | GRIMSBY WEST 132kV
GRIW41 | NGET | B-2-1c, B-3-1c | 400 | GRIMSBY WEST | 53.5653 | -0.15236 | GRIMSBY WEST 400kV
GRMO2- | SPT | B-2-1b, B-3-1b | 275 | GRANGEMOUTH | 56.005 | -3.6946 | GRANGEMOUTH 275kV
GRMO3A | SPT | B-2-1b | 33 | GRANGEMOUTH | 56.005 | -3.6946 | GRANGEMOUTH 33kV
GRMO3C | SPT | B-2-1b, B-3-1b | 33 | GRANGEMOUTH | 56.005 | -3.6946 | GRANGEMOUTH 33kV
GRNA1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | GRETNA | 55.0322 | -3.052 | GRETNA 132kV
GRNA3U | SPT | B-4-2b | 33 | GRETNA | 55.0322 | -3.052 | GRETNA 33kV
GRNA4- | SPT | B-2-1b, B-2-2b, B-3-1b | 400 | GRETNA | 55.0322 | -3.052 | GRETNA 400kV
GRNA4C | SPT | B-2-1b, B-2-2b | 400 | GRETNA | 55.0322 | -3.052 | GRETNA 400kV
GRNS4L | SHET | B-2-2a | 400 | GREENS | 53.4811 | -2.1477 | GREENS 400kV
GRNS4M | SHET | B-2-2a | 400 | GREENS | 53.4811 | -2.1477 | GREENS 400kV
GRNV4- | SHET | B-2-2a | 400 | GREEN VOLT OFFSHORE WIND FARM |  |  | GREEN VOLT OFFSHORE WIND FARM 400kV
GRST2A | NGET | B-2-1c, B-4-1c | 275 | GREYSTONES | 54.5753 | -1.1247 | GREYSTONES 275kV
GRST2B | NGET | B-2-1c, B-4-1c | 275 | GREYSTONES | 54.5753 | -1.1247 | GREYSTONES 275kV
GRST61 | NGET | B-3-1c | 66 | GREYSTONES | 54.5753 | -1.1247 | GREYSTONES 66kV
GRTO61 | NGET | B-3-1c | 66 | GRANGETOWN | 54.5805 | -1.1488 | GRANGETOWN 66kV
GRUB1Q | SHET | B-2-1a, B-3-1a | 132 | GRUDIE BRIDGE | 57.6194 | -4.8312 | GRUDIE BRIDGE 132kV
GRUB1R | SHET | B-2-1a, B-3-1a | 132 | GRUDIE BRIDGE | 57.6194 | -4.8312 | GRUDIE BRIDGE 132kV
GRUB3- | SHET | B-3-1a | 33 | GRUDIE BRIDGE | 57.6194 | -4.8312 | GRUDIE BRIDGE 33kV
GWYD41 | NGET | B-2-2c | 400 | GWYDDELWERN | 51.6336 | -3.8278 | GWYDDELWERN 400kV
GWYN4A | NGET | B-2-1c, B-2-2c | 400 | GWYNEDD | 53.181 | -4.1487 | GWYNEDD 400kV
GWYN4B | NGET | B-2-1c, B-2-2c | 400 | GWYNEDD | 53.181 | -4.1487 | GWYNEDD 400kV
HACK11 | NGET | B-3-1c | 132 | HACKNEY | 51.5589 | -0.04435 | HACKNEY 132kV
HACK21 | NGET | B-2-2c | 275 | HACKNEY | 51.5589 | -0.04435 | HACKNEY 275kV
HACK22 | NGET | B-2-2c | 275 | HACKNEY | 51.5589 | -0.04435 | HACKNEY 275kV
HACK2A | NGET | B-2-1c, B-3-1c, B-3-2c | 275 | HACKNEY | 51.5589 | -0.04435 | HACKNEY 275kV
HACK2B | NGET | B-2-1c, B-3-1c, B-3-2c | 275 | HACKNEY | 51.5589 | -0.04435 | HACKNEY 275kV
HACK41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 400 | HACKNEY | 51.5589 | -0.04435 | HACKNEY 400kV
HACK61 | NGET | B-3-1c, B-3-2c | 66 | HACKNEY | 51.5589 | -0.04435 | HACKNEY 66kV
HADH1- | SPT | B-2-1b, B-3-1b | 132 | HADYARD HILL | 55.2504 | -4.7075 | HADYARD HILL 132kV
HADH3- | SPT | B-3-1b | 33 | HADYARD HILL | 55.2504 | -4.7075 | HADYARD HILL 33kV
HAGH3- | SPT | B-2-1b | 33 | HAGSHAW HILL PHASE 2 |  |  | HAGSHAW HILL PHASE 2 33kV
HAGR1Q | SPT | B-2-1b, B-3-1b | 132 | HAGGS ROAD | 55.8286 | -4.2955 | HAGGS ROAD 132kV
HAGR1R | SPT | B-2-1b, B-3-1b | 132 | HAGGS ROAD | 55.8286 | -4.2955 | HAGGS ROAD 132kV
HAGR3- | SPT | B-3-1b | 33 | HAGGS ROAD | 55.8286 | -4.2955 | HAGGS ROAD 33kV
HAHA3- | SPT | B-2-1b | 33 | HAGSHAW HILL PHASE 1 |  |  | HAGSHAW HILL PHASE 1 33kV
HAKB1- | NGET, SPT | B-2-1b, B-2-1c, B-2-2b | 132 | HARKER BORDER NODE | 55.0304 | -3.0331 | HARKER BORDER NODE 132kV
HAKB4- | NGET, SPT | B-2-1b, B-2-1c, B-2-2b, B-2-2c | 400 | HARKER BORDER NODE | 55.0304 | -3.0331 | HARKER BORDER NODE 400kV
HAKB4- | NGET, SPT | B-2-1b, B-2-1c, B-2-2b, B-2-2c | 400 | HARKER BOUNDARY | 55.0304 | -3.0331 | HARKER BOUNDARY 400kV
HAKB4B | NGET, SPT | B-2-1b, B-2-1c, B-2-2b, B-2-2c | 400 | HARKER BORDER NODE | 55.0304 | -3.0331 | HARKER BORDER NODE 400kV
HAKB4B | NGET, SPT | B-2-1b, B-2-1c, B-2-2b, B-2-2c | 400 | HARKER BOUNDARY | 55.0304 | -3.0331 | HARKER BOUNDARY 400kV
HAMB4A | NGET | B-2-1c, B-2-2c | 400 | HAMBLETON | 53.8788 | -2.9878 | HAMBLETON 400kV
HAMB4B | NGET | B-2-1c, B-2-2c | 400 | HAMBLETON | 53.8788 | -2.9878 | HAMBLETON 400kV
HAMH1A | NGET | B-2-1c | 132 | HAMS HALL | 52.531 | -1.7143 | HAMS HALL 132kV
HAMH1B | NGET | B-2-1c | 132 | HAMS HALL | 52.531 | -1.7143 | HAMS HALL 132kV
HAMH2A | NGET | B-2-1c, B-3-1c | 275 | HAMS HALL | 52.531 | -1.7143 | HAMS HALL 275kV
HAMH41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | HAMS HALL | 52.531 | -1.7143 | HAMS HALL 400kV
HARE1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | HARESTANES | 55.2643 | -3.5608 | HARESTANES 132kV
HARE3A | SPT | B-3-1b | 33 | HARESTANES | 55.2643 | -3.5608 | HARESTANES 33kV
HARE3B | SPT | B-3-1b | 33 | HARESTANES | 55.2643 | -3.5608 | HARESTANES 33kV
HARG11 | NGET | B-3-2c | 132 | HARKER GIS | 54.942 | -2.9627 | HARKER GIS 132kV
HARG21 | NGET | B-3-2c | 275 | HARKER GIS | 54.942 | -2.9627 | HARKER GIS 275kV
HARG2A | NGET | B-3-2c | 275 | HARKER GIS | 54.942 | -2.9627 | HARKER GIS 275kV
HARG41 | NGET | B-2-2c, B-3-2c, B-4-2c | 400 | HARKER GIS | 54.942 | -2.9627 | HARKER GIS 400kV
HARI1- | SHET | B-2-2a | 132 | HARRIS | 57.8459 | -6.8304 | HARRIS 132kV
HARK11 | NGET | B-3-1c, B-3-2c | 132 | HARKER | 54.9411 | -2.9616 | HARKER 132kV
HARK12 | NGET | B-3-1c, B-3-2c | 132 | HARKER | 54.9411 | -2.9616 | HARKER 132kV
HARK13 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 132 | HARKER | 54.9411 | -2.9616 | HARKER 132kV
HARK21 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c, B-4-1c, B-4-2c | 275 | HARKER | 54.9411 | -2.9616 | HARKER 275kV
HARK23 | NGET | B-2-1c, B-2-2c | 275 | HARKER | 54.9411 | -2.9616 | HARKER 275kV
HARK24 | NGET | B-2-1c, B-2-2c | 275 | HARKER | 54.9411 | -2.9616 | HARKER 275kV
HARK41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c, B-4-1c, B-4-2c | 400 | HARKER | 54.9411 | -2.9616 | HARKER 400kV
HARM21 | NGET | B-2-1c, B-3-1c | 275 | HARTMOOR | 54.7005 | -1.292 | HARTMOOR 275kV
HARM61 | NGET | B-3-1c | 66 | HARTMOOR | 54.7005 | -1.292 | HARTMOOR 66kV
HARR3- | SPT | B-2-1b | 33 | HARTING RIG WIND FARM |  |  | HARTING RIG WIND FARM 33kV
HATL21 | NGET | B-2-1c | 275 | HARTLEPOOL | 54.6357 | -1.1832 | HARTLEPOOL 275kV
HAWI1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | HAWICK | 55.4331 | -2.8015 | HAWICK 132kV
HAWI1B | SPT | B-2-1b, B-2-2b | 132 | HAWICK | 55.4331 | -2.8015 | HAWICK 132kV
HAWI1C | SPT | B-2-2b | 132 | HAWICK | 55.4331 | -2.8015 | HAWICK 132kV
HAWI1D | SPT | B-2-2b | 132 | HAWICK | 55.4331 | -2.8015 | HAWICK 132kV
HAWI3- | SPT | B-3-1b | 33 | HAWICK | 55.4331 | -2.8015 | HAWICK 33kV
HAWP21 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 275 | HAWTHORN PIT | 54.8054 | -1.4031 | HAWTHORN PIT 275kV
HAWP2A | NGET | B-2-1c | 275 | HAWTHORN PIT | 54.8054 | -1.4031 | HAWTHORN PIT 275kV
HAWP41 | NGET | B-2-2c, B-3-2c | 400 | HAWTHORN PIT | 54.8054 | -1.4031 | HAWTHORN PIT 400kV
HAWP4A | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | HAWTHORN PIT | 54.8054 | -1.4031 | HAWTHORN PIT 400kV
HAWP61 | NGET | B-3-1c | 66 | HAWTHORN PIT | 54.8054 | -1.4031 | HAWTHORN PIT 66kV
HAZE1- | SPT | B-2-2b | 132 | HAZELSIDE |  |  | HAZELSIDE 132kV
HAZE1T | SPT | B-2-2b | 132 | HAZELSIDE |  |  | HAZELSIDE 132kV
HBES4- | SPT | B-2-2b | 400 | HUNTERSTON BATTERY STORAGE | 55.7199 | -4.8927 | HUNTERSTON BATTERY STORAGE 400kV
HEDO21 | NGET | B-2-1c | 275 | HEDON (GIS) | 53.7475 | -0.23436 | HEDON (GIS) 275kV
HELE1Q | SPT | B-2-1b, B-3-1b | 132 | HELENSBURGH | 56.0226 | -4.7087 | HELENSBURGH 132kV
HELE1R | SPT | B-2-1b, B-3-1b | 132 | HELENSBURGH | 56.0226 | -4.7087 | HELENSBURGH 132kV
HELE3- | SPT | B-3-1b | 33 | HELENSBURGH | 56.0226 | -4.7087 | HELENSBURGH 33kV
HEND11 | NGET | B-2-1c | 132 | HENDON | 51.5948 | -0.25829 | HENDON 132kV
HESF4- | SPT | B-2-2b | 400 | HUNTERSTON ENERGY STORAGE FACILITY | 55.7199 | -4.8927 | HUNTERSTON ENERGY STORAGE FACILITY 400kV
HEST3- | SHET | B-3-2a | 33 | HESTA HEAD |  |  | HESTA HEAD 33kV
HEYS11 | NGET | B-3-1c | 132 | HEYSHAM | 54.0323 | -2.8911 | HEYSHAM 132kV
HEYS41 | NGET | B-2-1c, B-3-1c | 400 | HEYSHAM | 54.0323 | -2.8911 | HEYSHAM 400kV
HIBU41 | NGET | B-2-1c, B-3-1c | 400 | HIGHBURY | 51.5614 | -0.1137 | HIGHBURY 400kV
HICL1- | SHET | B-2-2a | 132 | HIGH CONSTELLATION |  |  | HIGH CONSTELLATION 132kV
HIGM21 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 275 | HIGH MARNHAM | 53.228 | -0.79574 | HIGH MARNHAM 275kV
HIGM41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 400 | HIGH MARNHAM | 53.228 | -0.79574 | HIGH MARNHAM 400kV
HIGM4A | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 400 | HIGH MARNHAM | 53.228 | -0.79574 | HIGH MARNHAM 400kV
HIMB21 | NGET | B-2-2c, B-3-2c | 275 | HIMB (Node Name used) | 53.228 | -0.79574 | HIMB (Node Name used) 275kV
HIMB41 | NGET | B-2-2c, B-3-2c | 400 | HIGH MARNHAM SUBSTATION-B | 53.228 | -0.79574 | HIGH MARNHAM SUBSTATION-B 400kV
HINP21 | NGET | B-3-1c | 275 | HINKLEY POINT | 51.2078 | -3.1277 | HINKLEY POINT 275kV
HINP22 | NGET | B-3-1c | 275 | HINKLEY POINT | 51.2078 | -3.1277 | HINKLEY POINT 275kV
HINP41 | NGET | B-2-1c, B-3-1c | 400 | HINKLEY POINT | 51.2078 | -3.1277 | HINKLEY POINT 400kV
HLND1- | SPT | B-2-2b, B-3-2b | 132 | HEATHLAND | 51.5069 | -3.1976 | HEATHLAND 132kV
HLND3- | SPT | B-3-2b | 33 | HEATHLAND | 51.5069 | -3.1976 | HEATHLAND 33kV
HOLM1- | SPT | B-2-2b | 132 | HOLM HILL |  |  | HOLM HILL 132kV
HOLM1T | SPT | B-2-2b | 132 | HOLM HILL |  |  | HOLM HILL 132kV
HOME1- | SHET | B-2-2a, B-3-2a | 132 | HOLLANDMEY |  |  | HOLLANDMEY 132kV
HOME3- | SHET | B-3-2a | 33 | HOLLANDMEY |  |  | HOLLANDMEY 33kV
HORI1- | SPT | B-2-2b, B-3-2b | 132 | HOPSRIG COLLECTOR | 58.2775 | -6.3083 | HOPSRIG COLLECTOR 132kV
HORI3A | SPT | B-3-2b | 33 | HOPSRIG COLLECTOR | 58.2775 | -6.3083 | HOPSRIG COLLECTOR 33kV
HORI3B | SPT | B-3-2b | 33 | HOPSRIG COLLECTOR | 58.2775 | -6.3083 | HOPSRIG COLLECTOR 33kV
HUCR4- | SPT | B-2-2b | 400 | HUNTERSTON CRYOBATTERY | 55.7199 | -4.8927 | HUNTERSTON CRYOBATTERY 400kV
HUCS4- | SPT | B-2-1b, B-2-2b, B-4-1b | 400 | HUNTERSTON CONVERTER STATION | 55.7199 | -4.8927 | HUNTERSTON CONVERTER STATION 400kV
HUER1- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 132 | HUNTERSTON | 55.7199 | -4.8927 | HUNTERSTON 132kV
HUER4- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 400 | HUNTERSTON | 55.7199 | -4.8927 | HUNTERSTON 400kV
HUMR31 | NGET | B-3-1c | 33 | HUMBER REFINERY | 53.6384 | -0.23849 | HUMBER REFINERY 33kV
HUMR41 | NGET | B-2-1c, B-3-1c | 400 | HUMBER REFINERY | 53.6384 | -0.23849 | HUMBER REFINERY 400kV
HUNE1- | SPT | B-2-2b, B-3-2b | 132 | HUNTERSTON EAST | 55.7199 | -4.8883 | HUNTERSTON EAST 132kV
HUNE4- | SPT | B-2-1b, B-2-2b, B-3-2b, B-4-2b | 400 | HUNTERSTON EAST | 55.7199 | -4.8883 | HUNTERSTON EAST 400kV
HUNF1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | HUNTERSTON FARM | 55.7199 | -4.8927 | HUNTERSTON FARM 132kV
HUNF1R | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | HUNTERSTON FARM | 55.7199 | -4.8927 | HUNTERSTON FARM 132kV
HUNF3- | SPT | B-3-1b | 33 | HUNTERSTON FARM | 55.7199 | -4.8927 | HUNTERSTON FARM 33kV
HUNN2A | SPT | B-2-1b, B-3-1b | 275 | HUNTERSTON NORTH | 55.721 | -4.8864 | HUNTERSTON NORTH 275kV
HUNN2A | SPT | B-2-1b, B-3-1b | 275 | HUNTERSTON NORTH | 55.721 | -4.8864 | HUNTERSTON NORTH 275kV
HUNN2B | SPT | B-2-1b, B-3-1b | 275 | HUNTERSTON NORTH | 55.721 | -4.8864 | HUNTERSTON NORTH 275kV
HUNN2B | SPT | B-2-1b, B-3-1b | 275 | HUNTERSTON NORTH | 55.721 | -4.8864 | HUNTERSTON NORTH 275kV
HUNN2C | SHET, SPT | B-2-1a, B-2-1b | 275 | HUNTERSTON NORTH | 55.721 | -4.8864 | HUNTERSTON NORTH 275kV
HUNN2C | SHET, SPT | B-2-1a, B-2-1b | 275 | HUNTERSTON NORTH | 55.721 | -4.8864 | HUNTERSTON NORTH 275kV
HUNN2D | SHET, SPT | B-2-1a, B-2-1b | 275 | HUNTERSTON NORTH | 55.721 | -4.8864 | HUNTERSTON NORTH 275kV
HUNN2D | SHET, SPT | B-2-1a, B-2-1b | 275 | HUNTERSTON NORTH | 55.721 | -4.8864 | HUNTERSTON NORTH 275kV
HUNN3W | SPT | B-4-1b | 33 | HUNTERSTON NORTH | 55.721 | -4.8864 | HUNTERSTON NORTH 33kV
HUNN3X | SPT | B-4-1b | 33 | HUNTERSTON NORTH | 55.721 | -4.8864 | HUNTERSTON NORTH 33kV
HUNN4A | SPT | B-2-1b, B-3-1b | 400 | HUNTERSTON NORTH | 55.721 | -4.8864 | HUNTERSTON NORTH 400kV
HUNN4B | SPT | B-2-1b, B-3-1b | 400 | HUNTERSTON NORTH | 55.721 | -4.8864 | HUNTERSTON NORTH 400kV
HURL4A | SHET | B-2-2a | 400 | HURLIE |  |  | HURLIE 400kV
HURL4B | SHET | B-2-2a | 400 | HURLIE |  |  | HURLIE 400kV
HURS1B | NGET | B-3-1c | 132 | HURST | 51.4327 | 0.1546 | HURST 132kV
HURS1C | NGET | B-3-1c | 132 | HURST | 51.4327 | 0.1546 | HURST 132kV
HURS1D | NGET | B-3-1c | 132 | HURST | 51.4327 | 0.1546 | HURST 132kV
HURS21 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 275 | HURST | 51.4327 | 0.1546 | HURST 275kV
HUTT11 | NGET | B-3-1c | 132 | HUTTON | 54.2975 | -2.6709 | HUTTON 132kV
HUTT41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | HUTTON | 54.2975 | -2.6709 | HUTTON 400kV
HUTT42 | NGET | B-2-1c | 400 | HUTTON | 54.2975 | -2.6709 | HUTTON 400kV
HUTT43 | NGET | B-2-1c | 400 | HUTTON | 54.2975 | -2.6709 | HUTTON 400kV
HUTT71 | NGET | B-3-1c | 25 | HUTTON | 54.2975 | -2.6709 | HUTTON 25kV
IMPP31 | NGET | B-3-1c | 33 | IMPERIAL PARK | 51.5479 | -3.0309 | IMPERIAL PARK 33kV
IMPP41 | NGET | B-2-1c, B-3-1c | 400 | IMPERIAL PARK | 51.5479 | -3.0309 | IMPERIAL PARK 400kV
INCE11 | NGET | B-2-1c | 132 | INCE | 53.2778 | -2.8112 | INCE 132kV
INDQ11 | NGET | B-3-1c, B-4-1c | 132 | INDIAN QUEENS | 50.395 | -4.8989 | INDIAN QUEENS 132kV
INDQ41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | INDIAN QUEENS | 50.395 | -4.8989 | INDIAN QUEENS 400kV
INGA1Q | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | INVERGARRY | 57.072 | -4.7737 | INVERGARRY 132kV
INGA5- | SHET | B-3-1a | 11 | INVERGARRY | 57.072 | -4.7737 | INVERGARRY 11kV
INKE1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | INVERKEITHING | 56.0424 | -3.3903 | INVERKEITHING 132kV
INKE1R | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | INVERKEITHING | 56.0424 | -3.3903 | INVERKEITHING 132kV
INKE3- | SPT | B-3-1b | 33 | INVERKEITHING | 56.0424 | -3.3903 | INVERKEITHING 33kV
INNE1J | SHET | B-2-1a, B-3-1a | 132 | INVERNESS | 57.4536 | -4.2466 | INVERNESS 132kV
INNE1K | SHET | B-2-1a, B-3-1a | 132 | INVERNESS | 57.4536 | -4.2466 | INVERNESS 132kV
INNE1L | SHET | B-2-1a, B-3-1a | 132 | INVERNESS | 57.4536 | -4.2466 | INVERNESS 132kV
INNE1Q | SHET | B-2-1a | 132 | INVERNESS | 57.4536 | -4.2466 | INVERNESS 132kV
INNE1R | SHET | B-2-1a | 132 | INVERNESS | 57.4536 | -4.2466 | INVERNESS 132kV
INNE3- | SHET | B-3-1a | 33 | INVERNESS | 57.4536 | -4.2466 | INVERNESS 33kV
INRU1Q | SHET | B-2-1a, B-2-2a | 132 | INVERUGIE |  |  | INVERUGIE 132kV
INRU1R | SHET | B-2-1a, B-2-2a | 132 | INVERUGIE |  |  | INVERUGIE 132kV
INRU1S | SHET | B-2-1a | 132 | INVERUGIE |  |  | INVERUGIE 132kV
INVB2A | SHET, SPT | B-2-1b, B-3-1a, B-3-2a | 275 | INVERANAN BOUNDARY | 56.3261 | -4.7245 | INVERANAN BOUNDARY 275kV
INVB2A | SHET, SPT | B-2-1b, B-3-1a, B-3-2a | 275 | INVERARNAN BORDER NODE | 56.3261 | -4.7245 | INVERARNAN BORDER NODE 275kV
INVB2B | SHET, SPT | B-2-1b, B-3-1a, B-3-2a | 275 | INVERANAN BOUNDARY | 56.3261 | -4.7245 | INVERANAN BOUNDARY 275kV
INVB2B | SHET, SPT | B-2-1b, B-3-1a, B-3-2a | 275 | INVERARNAN BORDER NODE | 56.3261 | -4.7245 | INVERARNAN BORDER NODE 275kV
INVE1J | SHET | B-2-1a, B-2-2a | 132 | INVERARAY | 56.2624 | -5.0413 | INVERARAY 132kV
INVE1K | SHET | B-2-1a, B-2-2a | 132 | INVERARAY | 56.2624 | -5.0413 | INVERARAY 132kV
INVR1- | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | INVERARNAN | 56.3261 | -4.7245 | INVERARNAN 132kV
INVR1A | SHET | B-2-1a | 132 | INVERARNAN | 56.3261 | -4.7245 | INVERARNAN 132kV
INVR1B | SHET | B-2-1a | 132 | INVERARNAN | 56.3261 | -4.7245 | INVERARNAN 132kV
INVR1C | SHET | B-2-1a | 132 | INVERARNAN | 56.3261 | -4.7245 | INVERARNAN 132kV
INVR1D | SHET | B-2-1a | 132 | INVERARNAN | 56.3261 | -4.7245 | INVERARNAN 132kV
INVR1L | SHET | B-3-2a | 132 | INVERARNAN | 56.3261 | -4.7245 | INVERARNAN 132kV
INVR1M | SHET | B-3-2a | 132 | INVERARNAN | 56.3261 | -4.7245 | INVERARNAN 132kV
INVR2- | SPT | B-2-1b, B-2-2b | 275 | INVERARNAN | 56.3261 | -4.7245 | INVERARNAN 275kV
INWI1Q | SPT | B-2-1b, B-2-2b | 132 | INNERWICK | 58.442 | -3.1051 | INNERWICK 132kV
INWI1R | SPT | B-2-1b, B-2-2b | 132 | INNERWICK | 58.442 | -3.1051 | INNERWICK 132kV
IROA11 | NGET | B-2-1c, B-3-1c, B-4-1c | 132 | IRON ACTON | 51.5698 | -2.4807 | IRON ACTON 132kV
IROA12 | NGET | B-2-1c, B-3-1c | 132 | IRON ACTON | 51.5698 | -2.4807 | IRON ACTON 132kV
IROA13 | NGET | B-2-1c, B-3-1c | 132 | IRON ACTON | 51.5698 | -2.4807 | IRON ACTON 132kV
IROA21 | NGET | B-2-1c, B-3-1c | 275 | IRON ACTON | 51.5698 | -2.4807 | IRON ACTON 275kV
IRON11 | NGET | B-3-1c, B-4-1c | 132 | IRONBRIDGE | 52.632 | -2.5143 | IRONBRIDGE 132kV
IRON12 | NGET | B-3-1c, B-4-1c | 132 | IRONBRIDGE | 52.632 | -2.5143 | IRONBRIDGE 132kV
IRON13 | NGET | B-3-1c | 132 | IRONBRIDGE | 52.632 | -2.5143 | IRONBRIDGE 132kV
IRON41 | NGET | B-2-1c, B-3-1c, B-4-1c, B-4-2c | 400 | IRONBRIDGE | 52.632 | -2.5143 | IRONBRIDGE 400kV
ISLI11 | NGET | B-3-1c | 132 | ISLINGTON | 51.5494 | -0.11462 | ISLINGTON 132kV
IVER11 | NGET | B-3-1c | 132 | IVER | 51.5441 | -0.49887 | IVER 132kV
IVER21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | IVER | 51.5441 | -0.49887 | IVER 275kV
IVER22 | NGET | B-2-1c, B-3-1c | 275 | IVER | 51.5441 | -0.49887 | IVER 275kV
IVER2A | NGET | B-2-1c, B-3-1c | 275 | IVER | 51.5441 | -0.49887 | IVER 275kV
IVER4A | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | IVER | 51.5441 | -0.49887 | IVER 400kV
IVER4B | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | IVER | 51.5441 | -0.49887 | IVER 400kV
IVER61 | NGET | B-3-1c | 66 | IVER | 51.5441 | -0.49887 | IVER 66kV
JOHN1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | JOHNSTONE | 55.8457 | -4.5064 | JOHNSTONE 132kV
JOHN1R | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | JOHNSTONE | 55.8457 | -4.5064 | JOHNSTONE 132kV
JOHN3- | SPT | B-3-1b | 33 | JOHNSTONE | 55.8457 | -4.5064 | JOHNSTONE 33kV
JORD21 | NGET | B-2-1c, B-3-1c | 275 | JORDANTHORPE | 53.3295 | -1.458 | JORDANTHORPE 275kV
JORD31 | NGET | B-3-1c, B-4-1c | 33 | JORDANTHORPE | 53.3295 | -1.458 | JORDANTHORPE 33kV
JUNA1T | SPT | B-2-1b, B-2-2b | 132 | JUNCTION A |  |  | JUNCTION A 132kV
JUNB1- | SPT | B-2-1b, B-2-2b | 132 | JUNCTION B |  |  | JUNCTION B 132kV
JUNB1A | SPT | B-2-2b | 132 | JUNCTION B |  |  | JUNCTION B 132kV
JUNV1- | NGET, SPT | B-2-1b, B-2-1c, B-2-2b, B-2-2c | 132 | JUNCTION V | 54.9411 | -2.9616 | JUNCTION V 132kV
JUNV1A | SPT | B-2-2b | 132 | JUNCTION V | 54.9411 | -2.9616 | JUNCTION V 132kV
KAIM2- | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | KAIMES | 55.8926 | -3.166 | KAIMES 275kV
KAIM3- | SPT | B-2-1b | 33 | KAIMES | 55.8926 | -3.166 | KAIMES 33kV
KAIM3A | SPT | B-2-1b, B-3-1b | 33 | KAIMES | 55.8926 | -3.166 | KAIMES 33kV
KAIM3B | SPT | B-2-1b, B-3-1b | 33 | KAIMES | 55.8926 | -3.166 | KAIMES 33kV
KEAD11 | NGET | B-3-1c | 132 | KEADBY | 53.5981 | -0.75621 | KEADBY 132kV
KEAD41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | KEADBY | 53.5981 | -0.75621 | KEADBY 400kV
KEAD42 | NGET | B-2-1c, B-3-1c | 400 | KEADBY | 53.5981 | -0.75621 | KEADBY 400kV
KEAD43 | NGET | B-2-1c | 400 | KEADBY | 53.5981 | -0.75621 | KEADBY 400kV
KEAD44 | NGET | B-2-1c | 400 | KEADBY | 53.5981 | -0.75621 | KEADBY 400kV
KEAD4C | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | KEADBY | 53.5981 | -0.75621 | KEADBY 400kV
KEAD4D | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | KEADBY | 53.5981 | -0.75621 | KEADBY 400kV
KEAR11 | NGET | B-3-1c, B-4-1c | 132 | KEARSLEY | 53.5373 | -2.3585 | KEARSLEY 132kV
KEAR21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | KEARSLEY | 53.5373 | -2.3585 | KEARSLEY 275kV
KEAR31 | NGET | B-3-1c | 33 | KEARSLEY | 53.5373 | -2.3585 | KEARSLEY 33kV
KEAR41 | NGET | B-2-1c, B-3-1c | 400 | KEARSLEY | 53.5373 | -2.3585 | KEARSLEY 400kV
KEIH3- | SPT | B-2-1b, B-2-2b | 33 | KEITHSHILL | 57.5403 | -2.9396 | KEITHSHILL 33kV
KEIT1- | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | KEITH | 57.5403 | -2.9396 | KEITH 132kV
KEIT1J | SHET | B-2-1a | 132 | KEITH | 57.5403 | -2.9396 | KEITH 132kV
KEIT1K | SHET | B-2-1a | 132 | KEITH | 57.5403 | -2.9396 | KEITH 132kV
KEIT1M | SHET | B-2-2a | 132 | KEITH | 57.5403 | -2.9396 | KEITH 132kV
KEIT1N | SHET | B-2-2a | 132 | KEITH | 57.5403 | -2.9396 | KEITH 132kV
KEIT2Q | SHET | B-2-1a, B-3-1a | 275 | KEITH | 57.5403 | -2.9396 | KEITH 275kV
KEIT2R | SHET | B-2-1a, B-3-1a | 275 | KEITH | 57.5403 | -2.9396 | KEITH 275kV
KEIT3- | SHET | B-2-1a, B-3-1a | 33 | KEITH | 57.5403 | -2.9396 | KEITH 33kV
KEIT3A | SHET | B-2-1a, B-3-1a | 33 | KEITH | 57.5403 | -2.9396 | KEITH 33kV
KEMS11 | NGET | B-3-1c | 132 | KEMSLEY | 51.3683 | 0.74147 | KEMSLEY 132kV
KEMS41 | NGET | B-2-1c, B-3-1c | 400 | KEMSLEY | 51.3683 | 0.74147 | KEMSLEY 400kV
KEMS4A | NGET | B-2-1c, B-3-1c | 400 | KEMSLEY | 51.3683 | 0.74147 | KEMSLEY 400kV
KEMS4B | NGET | B-2-1c, B-3-1c | 400 | KEMSLEY | 51.3683 | 0.74147 | KEMSLEY 400kV
KENE3- | SPT | B-3-1b | 33 | KENNOXHEAD WINDFARM EXTENSION |  |  | KENNOXHEAD WINDFARM EXTENSION 33kV
KENG41 | NGET | B-2-1c | 400 | KENSAL GREEN | 51.5262 | -0.22404 | KENSAL GREEN 400kV
KENN1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | KENNOXHEAD |  |  | KENNOXHEAD 132kV
KENN3- | SPT | B-3-1b | 33 | KENNOXHEAD |  |  | KENNOXHEAD 33kV
KEOO1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | KENDOON | 55.1637 | -4.1914 | KENDOON 132kV
KEOO1Q | SPT | B-2-2b | 132 | KENDOON | 55.1637 | -4.1914 | KENDOON 132kV
KEOO5- | SPT | B-3-1b | 11 | KENDOON | 55.1637 | -4.1914 | KENDOON 11kV
KERG1- | SHET | B-2-1a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KERG1A | SHET | B-2-2a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KERG1B | SHET | B-2-2a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KERG1J | SHET | B-2-1a, B-2-2a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KERG1K | SHET | B-2-1a, B-2-2a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KERG1L | SHET | B-2-2a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KERG1M | SHET | B-2-2a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KERG1N | SHET | B-2-2a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KERG1P | SHET | B-2-1a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KERG1Q | SHET | B-2-1a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KERG1R | SHET | B-2-1a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KERG1T | SHET | B-2-1a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KERG1U | SHET | B-2-2a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KERG1V | SHET | B-2-2a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KERG1W | SHET | B-2-2a | 132 | KERGORD | 60.295 | -1.2727 | KERGORD 132kV
KIBY11 | NGET | B-3-1c, B-4-1c | 132 | KIRKBY | 53.4692 | -2.8477 | KIRKBY 132kV
KIBY21 | NGET | B-2-1c, B-3-1c | 275 | KIRKBY | 53.4692 | -2.8477 | KIRKBY 275kV
KIER1Q | SPT | B-2-1b, B-3-1b | 132 | KILLERMONT | 55.9036 | -4.3105 | KILLERMONT 132kV
KIER1R | SPT | B-2-1b, B-3-1b | 132 | KILLERMONT | 55.9036 | -4.3105 | KILLERMONT 132kV
KIER3- | SPT | B-3-1b | 33 | KILLERMONT | 55.9036 | -4.3105 | KILLERMONT 33kV
KIIN1- | SHET | B-2-1a, B-3-1a | 132 | KILLIN | 56.4774 | -4.3303 | KILLIN 132kV
KIIN3- | SHET | B-3-1a | 33 | KILLIN | 56.4774 | -4.3303 | KILLIN 33kV
KILB1Q | SPT | B-2-1b, B-3-1b | 132 | KILBOWIE | 55.9186 | -4.4107 | KILBOWIE 132kV
KILB1R | SPT | B-2-1b, B-3-1b | 132 | KILBOWIE | 55.9186 | -4.4107 | KILBOWIE 132kV
KILB3- | SPT | B-3-1b | 33 | KILBOWIE | 55.9186 | -4.4107 | KILBOWIE 33kV
KILB5- | SPT | B-3-1b | 11 | KILBOWIE | 55.9186 | -4.4107 | KILBOWIE 11kV
KILC1Q | SHET | B-2-1a, B-2-2a | 132 | KILLIN CASCADE GROUP | 56.4774 | -4.3303 | KILLIN CASCADE GROUP 132kV
KILG2- | SPT | B-2-1b, B-3-1b, B-4-1b | 275 | KILGALLIOCH | 55.0501 | -4.7647 | KILGALLIOCH 275kV
KILG3A | SPT | B-3-1b | 33 | KILGALLIOCH | 55.0501 | -4.7647 | KILGALLIOCH 33kV
KILG3B | SPT | B-3-1b | 33 | KILGALLIOCH | 55.0501 | -4.7647 | KILGALLIOCH 33kV
KILG3C | SPT | B-3-1b | 33 | KILGALLIOCH | 55.0501 | -4.7647 | KILGALLIOCH 33kV
KILL41 | NGET | B-2-1c | 400 | KILLINGHOLME | 53.6557 | -0.25722 | KILLINGHOLME 400kV
KILO1- | SHET | B-2-1a, B-3-1a | 132 | KINLOCHLEVEN | 56.1992 | -3.0397 | KINLOCHLEVEN 132kV
KILO3- | SHET | B-3-1a | 33 | KINLOCHLEVEN | 56.1992 | -3.0397 | KINLOCHLEVEN 33kV
KILS1- | SPT | B-2-1b, B-3-1b | 132 | KILMARNOCK SOUTH | 55.576 | -4.4657 | KILMARNOCK SOUTH 132kV
KILS2- | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | KILMARNOCK SOUTH | 55.576 | -4.4657 | KILMARNOCK SOUTH 275kV
KILS3- | SPT | B-3-1b | 33 | KILMARNOCK SOUTH | 55.576 | -4.4657 | KILMARNOCK SOUTH 33kV
KILS3U | SPT | B-4-1b | 33 | KILMARNOCK SOUTH | 55.576 | -4.4657 | KILMARNOCK SOUTH 33kV
KILS3X | SPT | B-4-1b | 33 | KILMARNOCK SOUTH | 55.576 | -4.4657 | KILMARNOCK SOUTH 33kV
KILS4- | SPT | B-2-1b, B-2-2b, B-3-1b | 400 | KILMARNOCK SOUTH | 55.576 | -4.4657 | KILMARNOCK SOUTH 400kV
KILS4T | SPT | B-2-1b, B-2-2b, B-3-1b | 400 | KILMARNOCK SOUTH | 55.576 | -4.4657 | KILMARNOCK SOUTH 400kV
KILT2Q | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | KILMARNOCK TOWN | 55.5982 | -4.4955 | KILMARNOCK TOWN 275kV
KILT2R | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | KILMARNOCK TOWN | 55.5982 | -4.4955 | KILMARNOCK TOWN 275kV
KILT3A | SPT | B-3-1b | 33 | KILMARNOCK TOWN | 55.5982 | -4.4955 | KILMARNOCK TOWN 33kV
KILW1Q | SPT | B-2-1b, B-3-1b | 132 | KILWINNING | 55.6648 | -4.6813 | KILWINNING 132kV
KILW1R | SPT | B-2-1b, B-3-1b | 132 | KILWINNING | 55.6648 | -4.6813 | KILWINNING 132kV
KILW3- | SPT | B-3-1b | 33 | KILWINNING | 55.6648 | -4.6813 | KILWINNING 33kV
KINA2J | SHET | B-2-1a, B-2-2a, B-4-1a, B-4-2a | 275 | KINARDOCHY |  |  | KINARDOCHY 275kV
KINA2K | SHET | B-2-1a, B-2-2a, B-4-1a, B-4-2a | 275 | KINARDOCHY |  |  | KINARDOCHY 275kV
KINA4A | SHET | B-2-2a, B-3-2a, B-4-2a | 400 | KINARDOCHY |  |  | KINARDOCHY 400kV
KINA4B | SHET | B-2-2a, B-3-2a, B-4-2a | 400 | KINARDOCHY |  |  | KINARDOCHY 400kV
KINB2J | SHET, SPT | B-2-1a, B-2-1b, B-2-2a, B-2-2b | 275 | KINCARDINE BOUNDARY | 56.0749 | -3.7333 | KINCARDINE BOUNDARY 275kV
KINB2J | SHET, SPT | B-2-1a, B-2-1b, B-2-2a, B-2-2b | 275 | KINCARDINE BORDER NODE | 56.0749 | -3.7333 | KINCARDINE BORDER NODE 275kV
KINB2K | SHET, SPT | B-2-1a, B-2-1b, B-2-2a, B-2-2b | 275 | KINCARDINE BOUNDARY | 56.0749 | -3.7333 | KINCARDINE BOUNDARY 275kV
KINB2K | SHET, SPT | B-2-1a, B-2-1b, B-2-2a, B-2-2b | 275 | KINCARDINE BORDER NODE | 56.0749 | -3.7333 | KINCARDINE BORDER NODE 275kV
KINB4J | SHET, SPT | B-2-2a, B-2-2b | 400 | KINCARDINE BOUNDARY | 56.0749 | -3.7333 | KINCARDINE BOUNDARY 400kV
KINB4J | SHET, SPT | B-2-2a, B-2-2b | 400 | KINCARDINE BORDER NODE | 56.0749 | -3.7333 | KINCARDINE BORDER NODE 400kV
KINB4K | SHET, SPT | B-2-2a, B-2-2b | 400 | KINCARDINE BOUNDARY | 56.0749 | -3.7333 | KINCARDINE BOUNDARY 400kV
KINB4K | SHET, SPT | B-2-2a, B-2-2b | 400 | KINCARDINE BORDER NODE | 56.0749 | -3.7333 | KINCARDINE BORDER NODE 400kV
KINC2- | SPT | B-2-1b, B-2-2b, B-4-2b | 275 | KINCARDINE | 56.0749 | -3.7333 | KINCARDINE 275kV
KINC4Q | SPT | B-2-2b | 400 | KINCARDINE | 56.0749 | -3.7333 | KINCARDINE 400kV
KINM2A | SHET | B-2-2a | 275 | KINMUCK |  |  | KINMUCK 275kV
KINM2B | SHET | B-2-2a | 275 | KINMUCK |  |  | KINMUCK 275kV
KINM2C | SHET | B-2-2a | 275 | KINMUCK |  |  | KINMUCK 275kV
KINN2A | SPT | B-2-2b, B-3-2b | 275 | KINCARDINE NORTH | 56.0749 | -3.7333 | KINCARDINE NORTH 275kV
KINN2B | SPT | B-2-2b, B-3-2b | 275 | KINCARDINE NORTH | 56.0749 | -3.7333 | KINCARDINE NORTH 275kV
KINN4- | SPT | B-2-2b, B-3-2b | 400 | KINCARDINE NORTH | 56.0749 | -3.7333 | KINCARDINE NORTH 400kV
KINO11 | NGET | B-3-1c | 132 | KINGSNORTH | 51.4186 | 0.59839 | KINGSNORTH 132kV
KINO41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | KINGSNORTH | 51.4186 | 0.59839 | KINGSNORTH 400kV
KINT1- | SHET | B-2-1a, B-3-1a, B-3-2a, B-4-1a | 132 | KINTORE | 57.2197 | -2.3811 | KINTORE 132kV
KINT1B | SHET | B-2-1a, B-4-1a | 132 | KINTORE | 57.2197 | -2.3811 | KINTORE 132kV
KINT1P | SHET | B-2-1a | 132 | KINTORE | 57.2197 | -2.3811 | KINTORE 132kV
KINT1R | SHET | B-2-1a | 132 | KINTORE | 57.2197 | -2.3811 | KINTORE 132kV
KINT1T | SHET | B-2-1a | 132 | KINTORE | 57.2197 | -2.3811 | KINTORE 132kV
KINT1U | SHET | B-2-1a | 132 | KINTORE | 57.2197 | -2.3811 | KINTORE 132kV
KINT2J | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | KINTORE | 57.2197 | -2.3811 | KINTORE 275kV
KINT2K | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 275 | KINTORE | 57.2197 | -2.3811 | KINTORE 275kV
KINT2L | SHET | B-2-2a | 275 | KINTORE | 57.2197 | -2.3811 | KINTORE 275kV
KINT2M | SHET | B-2-2a | 275 | KINTORE | 57.2197 | -2.3811 | KINTORE 275kV
KINT3- | SHET | B-3-1a, B-3-2a | 33 | KINTORE | 57.2197 | -2.3811 | KINTORE 33kV
KINT3W | SHET | B-4-1a | 33 | KINTORE | 57.2197 | -2.3811 | KINTORE 33kV
KINT3Y | SHET | B-4-1a | 33 | KINTORE | 57.2197 | -2.3811 | KINTORE 33kV
KINT4J | SHET | B-2-1a, B-2-2a, B-3-1a | 400 | KINTORE | 57.2197 | -2.3811 | KINTORE 400kV
KINT4K | SHET | B-2-1a, B-2-2a, B-3-1a | 400 | KINTORE | 57.2197 | -2.3811 | KINTORE 400kV
KION1- | SHET | B-2-2a, B-3-2a | 132 | KILMORACK NORTH |  |  | KILMORACK NORTH 132kV
KION1A | SHET | B-2-2a | 132 | KILMORACK NORTH |  |  | KILMORACK NORTH 132kV
KION1B | SHET | B-2-2a | 132 | KILMORACK NORTH |  |  | KILMORACK NORTH 132kV
KION5- | SHET | B-3-2a | 11 | KILMORACK NORTH |  |  | KILMORACK NORTH 11kV
KIOR1Q | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | KILMORACK |  |  | KILMORACK 132kV
KIOR5- | SHET | B-3-1a, B-3-2a | 11 | KILMORACK |  |  | KILMORACK 11kV
KIRK11 | NGET | B-3-1c | 132 | KIRKSTALL | 53.8062 | -1.5981 | KIRKSTALL 132kV
KIRK21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | KIRKSTALL | 53.8062 | -1.5981 | KIRKSTALL 275kV
KIRK2A | NGET | B-2-1c, B-3-1c | 275 | KIRKSTALL | 53.8062 | -1.5981 | KIRKSTALL 275kV
KITW11 | NGET | B-3-1c | 132 | KITWELL | 52.4308 | -2.0139 | KITWELL 132kV
KITW21 | NGET | B-2-1c, B-3-1c | 275 | KITWELL | 52.4308 | -2.0139 | KITWELL 275kV
KLYN41 | NGET | B-2-2c | 400 | KINGS LYNN | 52.7267 | 0.37878 | KINGS LYNN 400kV
KNAR11 | NGET | B-3-1c | 132 | KNARESBOROUGH | 54.0313 | -1.4878 | KNARESBOROUGH 132kV
KNAR21 | NGET | B-2-1c, B-2-2c, B-3-1c | 275 | KNARESBOROUGH | 54.0313 | -1.4878 | KNARESBOROUGH 275kV
KNOC1J | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | KNOCKNAGAEL | 57.4233 | -4.2461 | KNOCKNAGAEL 132kV
KNOC2J | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | KNOCKNAGAEL | 57.4233 | -4.2461 | KNOCKNAGAEL 275kV
KNOC2K | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | KNOCKNAGAEL | 57.4233 | -4.2461 | KNOCKNAGAEL 275kV
KNOC2L | SHET | B-2-1a, B-2-2a | 275 | KNOCKNAGAEL | 57.4233 | -4.2461 | KNOCKNAGAEL 275kV
KNOC2M | SHET | B-2-1a, B-2-2a | 275 | KNOCKNAGAEL | 57.4233 | -4.2461 | KNOCKNAGAEL 275kV
KNOC2N | SHET | B-2-1a, B-2-2a | 275 | KNOCKNAGAEL | 57.4233 | -4.2461 | KNOCKNAGAEL 275kV
KNOC2P | SHET | B-2-1a, B-2-2a | 275 | KNOCKNAGAEL | 57.4233 | -4.2461 | KNOCKNAGAEL 275kV
KNOK1- | SPT | B-2-2b, B-3-2b | 132 | KNOCKODHAR |  |  | KNOCKODHAR 132kV
KNOK3- | SPT | B-3-2b | 33 | KNOCKODHAR |  |  | KNOCKODHAR 33kV
KNSH1- | SPT | B-2-2b | 132 | KNOCKSHEE |  |  | KNOCKSHEE 132kV
KRKN1- | SHET | B-2-2a, B-3-2a | 132 | KIRKTON | 55.89 | -3.536 | KIRKTON 132kV
KRKN3- | SHET | B-3-2a | 33 | KIRKTON | 55.89 | -3.536 | KIRKTON 33kV
KYPE1- | SPT | B-2-1b, B-3-1b | 132 | KYPE MUIR |  |  | KYPE MUIR 132kV
KYPE3- | SPT | B-3-1b | 33 | KYPE MUIR |  |  | KYPE MUIR 33kV
KYPE3A | SPT | B-2-1b, B-3-1b | 33 | KYPE MUIR |  |  | KYPE MUIR 33kV
LACK21 | NGET | B-2-1c, B-3-1c | 275 | LACKENBY | 54.567 | -1.1317 | LACKENBY 275kV
LACK2A | NGET | B-2-1c, B-3-1c | 275 | LACKENBY | 54.567 | -1.1317 | LACKENBY 275kV
LACK2B | NGET | B-2-1c, B-3-1c | 275 | LACKENBY | 54.567 | -1.1317 | LACKENBY 275kV
LACK2C | NGET | B-2-1c | 275 | LACKENBY | 54.567 | -1.1317 | LACKENBY 275kV
LACK41 | NGET | B-2-1c, B-3-1c, B-4-2c | 400 | LACKENBY | 54.567 | -1.1317 | LACKENBY 400kV
LACK61 | NGET | B-3-1c | 66 | LACKENBY | 54.567 | -1.1317 | LACKENBY 66kV
LAGA41 | NGET | B-2-1c | 400 | LANGAGE | 50.3891 | -4.0127 | LANGAGE 400kV
LAGG1Q | SHET | B-2-1a | 132 | LAGGAN |  |  | LAGGAN 132kV
LAGG1R | SHET | B-2-1a | 132 | LAGGAN |  |  | LAGGAN 132kV
LAIR1- | SHET | B-2-1a, B-3-1a | 132 | LAIRG | 58.0304 | -4.3936 | LAIRG 132kV
LAIR3- | SHET | B-3-1a | 33 | LAIRG | 58.0304 | -4.3936 | LAIRG 33kV
LAIS1A | SHET | B-2-2a | 132 | LAIRG SOUTH | 58.0304 | -4.3936 | LAIRG SOUTH 132kV
LAIS1B | SHET | B-2-2a, B-3-2a | 132 | LAIRG SOUTH | 58.0304 | -4.3936 | LAIRG SOUTH 132kV
LAIS3- | SHET | B-3-2a | 33 | LAIRG SOUTH | 58.0304 | -4.3936 | LAIRG SOUTH 33kV
LALE11 | NGET | B-3-1c | 132 | LALEHAM | 51.4238 | -0.47062 | LALEHAM 132kV
LALE21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | LALEHAM | 51.4238 | -0.47062 | LALEHAM 275kV
LALE31 | NGET | B-3-1c | 33 | LALEHAM | 51.4238 | -0.47062 | LALEHAM 33kV
LAMB2- | SPT | B-2-1b, B-2-2b | 275 | LAMBHILL | 55.9038 | -4.2555 | LAMBHILL 275kV
LAMB2T | SPT | B-2-1b, B-2-2b | 275 | LAMBHILL | 55.9038 | -4.2555 | LAMBHILL 275kV
LAMB4T | SPT | B-2-2b | 400 | LAMBHILL | 55.9038 | -4.2555 | LAMBHILL 400kV
LAND11 | NGET | B-3-1c, B-4-1c | 132 | LANDULPH | 50.445 | -4.2426 | LANDULPH 132kV
LAND41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | LANDULPH | 50.445 | -4.2426 | LANDULPH 400kV
LAND42 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | LANDULPH | 50.445 | -4.2426 | LANDULPH 400kV
LEGA11 | NGET | B-3-1c | 132 | LEGACY | 53.0285 | -3.0538 | LEGACY 132kV
LEGA41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | LEGACY | 53.0285 | -3.0538 | LEGACY 400kV
LEGA4A | NGET | B-2-1c, B-3-1c | 400 | LEGACY | 53.0285 | -3.0538 | LEGACY 400kV
LEGA4B | NGET | B-2-1c, B-3-1c | 400 | LEGACY | 53.0285 | -3.0538 | LEGACY 400kV
LEGO1Q | SPT | B-2-2b, B-3-2b | 132 | LESMAHAGOW | 55.642 | -3.88 | LESMAHAGOW 132kV
LEGO1R | SPT | B-2-2b, B-3-2b | 132 | LESMAHAGOW | 55.642 | -3.88 | LESMAHAGOW 132kV
LEGO3- | SPT | B-3-2b | 33 | LESMAHAGOW | 55.642 | -3.88 | LESMAHAGOW 33kV
LEIB4A | NGET | B-2-1c | 400 | LEIGHTON BUZZARD | 51.9045 | -0.67766 | LEIGHTON BUZZARD 400kV
LEIB4B | NGET | B-2-1c | 400 | LEIGHTON BUZZARD | 51.9045 | -0.67766 | LEIGHTON BUZZARD 400kV
LEIS11 | NGET | B-2-1c, B-3-1c | 132 | LEISTON | 52.208 | 1.6112 | LEISTON 132kV
LEIS4A | NGET | B-2-1c, B-3-1c | 400 | LEISTON | 52.208 | 1.6112 | LEISTON 400kV
LEMR11 | NGET | B-2-1c, B-3-1c | 132 | LEA MARSTON | 52.5287 | -1.7088 | LEA MARSTON 132kV
LETH1- | SPT | B-2-2b, B-3-2b | 132 | LETHANS |  |  | LETHANS 132kV
LETH3- | SPT | B-3-2b | 33 | LETHANS |  |  | LETHANS 33kV
LEVE1Q | SPT | B-2-1b, B-3-1b | 132 | LEVEN | 56.1992 | -3.0397 | LEVEN 132kV
LEVE1R | SPT | B-2-1b, B-3-1b | 132 | LEVEN | 56.1992 | -3.0397 | LEVEN 132kV
LEVE3- | SPT | B-3-1b | 33 | LEVEN | 56.1992 | -3.0397 | LEVEN 33kV
LEVT1Q | SPT | B-2-1b | 132 | LEVEN TEE | 56.1992 | -3.0397 | LEVEN TEE 132kV
LEVT1R | SPT | B-2-1b | 132 | LEVEN TEE | 56.1992 | -3.0397 | LEVEN TEE 132kV
LEWI1J | SHET | B-2-2a, B-3-2a | 132 | LEWIS SUBSTATION |  |  | LEWIS SUBSTATION 132kV
LEWI1K | SHET | B-2-2a, B-3-2a | 132 | LEWIS SUBSTATION |  |  | LEWIS SUBSTATION 132kV
LEWI4- | SHET | B-2-2a | 400 | LEWIS SUBSTATION |  |  | LEWIS SUBSTATION 400kV
LEWI4J | SHET | B-2-2a, B-3-2a | 400 | LEWIS SUBSTATION |  |  | LEWIS SUBSTATION 400kV
LEWI4K | SHET | B-2-2a, B-3-2a | 400 | LEWIS SUBSTATION |  |  | LEWIS SUBSTATION 400kV
LEWI4R | SHET | B-2-2a | 400 | LEWIS SUBSTATION |  |  | LEWIS SUBSTATION 400kV
LHEU2- | SHET | B-2-2a | 275 | LOCH NAN EUN PSH |  |  | LOCH NAN EUN PSH 275kV
LHOR11 | NGET | B-3-2c | 132 | LITTLE HORSTED | 50.9417 | 0.12071 | LITTLE HORSTED 132kV
LHOR4A | NGET | B-2-2c, B-3-2c | 400 | LITTLE HORSTED | 50.9417 | 0.12071 | LITTLE HORSTED 400kV
LHOR4B | NGET | B-2-2c, B-3-2c | 400 | LITTLE HORSTED | 50.9417 | 0.12071 | LITTLE HORSTED 400kV
LIMK1- | SHET | B-2-2a | 132 | LIMEKILNS WINDFARM |  |  | LIMEKILNS WINDFARM 132kV
LIMK1A | SHET | B-2-2a | 132 | LIMEKILNS WINDFARM |  |  | LIMEKILNS WINDFARM 132kV
LING1Q | SPT | B-2-1b, B-3-1b | 132 | LIVINGSTON | 55.8828 | -3.4936 | LIVINGSTON 132kV
LING1R | SPT | B-2-1b, B-3-1b | 132 | LIVINGSTON | 55.8828 | -3.4936 | LIVINGSTON 132kV
LING3- | SPT | B-3-1b | 33 | LIVINGSTON | 55.8828 | -3.4936 | LIVINGSTON 33kV
LINM1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | LINNMILL | 55.672 | -3.8271 | LINNMILL 132kV
LINM1R | SPT | B-2-1b, B-3-1b | 132 | LINNMILL | 55.672 | -3.8271 | LINNMILL 132kV
LINM3- | SPT | B-3-1b | 33 | LINNMILL | 55.672 | -3.8271 | LINNMILL 33kV
LISD11 | NGET | B-3-1c | 132 | LISTER DRIVE | 53.4186 | -2.9242 | LISTER DRIVE 132kV
LISD21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | LISTER DRIVE | 53.4186 | -2.9242 | LISTER DRIVE 275kV
LISD2A | NGET | B-2-1c | 275 | LISTER DRIVE | 53.4186 | -2.9242 | LISTER DRIVE 275kV
LITB11 | NGET | B-3-1c | 132 | LITTLE BARFORD | 52.2049 | -0.26912 | LITTLE BARFORD 132kV
LITT11 | NGET | B-3-1c | 132 | LITTLEBROOK | 51.4647 | 0.23919 | LITTLEBROOK 132kV
LITT2A | NGET | B-2-1c, B-3-1c | 275 | LITTLEBROOK | 51.4647 | 0.23919 | LITTLEBROOK 275kV
LITT2B | NGET | B-2-1c, B-3-1c | 275 | LITTLEBROOK | 51.4647 | 0.23919 | LITTLEBROOK 275kV
LITT41 | NGET | B-2-1c, B-3-1c | 400 | LITTLEBROOK | 51.4647 | 0.23919 | LITTLEBROOK 400kV
LKEM2- | SHET | B-2-2a | 275 | LOCH KEMP PUMPED STORAGE |  |  | LOCH KEMP PUMPED STORAGE 275kV
LOAN2- | SPT | B-2-1b, B-2-2b, B-4-1b, B-4-2b | 275 | LONGANNET | 56.0505 | -3.6806 | LONGANNET 275kV
LOAN2- | SPT | B-2-1b, B-2-2b, B-4-1b, B-4-2b | 275 | LONGANNET | 56.0505 | -3.6806 | LONGANNET 275kV
LOAN2Q | SPT | B-2-1b, B-2-2b | 275 | LONGANNET | 56.0505 | -3.6806 | LONGANNET 275kV
LOAN2Q | SPT | B-2-1b, B-2-2b | 275 | LONGANNET | 56.0505 | -3.6806 | LONGANNET 275kV
LOAN2R | SPT | B-2-1b, B-2-2b | 275 | LONGANNET | 56.0505 | -3.6806 | LONGANNET 275kV
LOAN2R | SPT | B-2-1b, B-2-2b | 275 | LONGANNET | 56.0505 | -3.6806 | LONGANNET 275kV
LOAN2S | SPT | B-2-2b | 275 | LONGANNET | 56.0505 | -3.6806 | LONGANNET 275kV
LOAN2S | SPT | B-2-2b | 275 | LONGANNET | 56.0505 | -3.6806 | LONGANNET 275kV
LOAN2T | SPT | B-2-1b, B-2-2b | 275 | LONGANNET | 56.0505 | -3.6806 | LONGANNET 275kV
LOAN2T | SPT | B-2-1b, B-2-2b | 275 | LONGANNET | 56.0505 | -3.6806 | LONGANNET 275kV
LOAN4S | SPT | B-2-2b | 400 | LONGANNET | 56.0505 | -3.6806 | LONGANNET 400kV
LOCB1J | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | LOCH BUIDHE | 57.9508 | -4.2772 | LOCH BUIDHE 132kV
LOCB1K | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | LOCH BUIDHE | 57.9508 | -4.2772 | LOCH BUIDHE 132kV
LOCB1L | SHET | B-2-1a | 132 | LOCH BUIDHE | 57.9508 | -4.2772 | LOCH BUIDHE 132kV
LOCB1M | SHET | B-2-1a, B-2-2a | 132 | LOCH BUIDHE | 57.9508 | -4.2772 | LOCH BUIDHE 132kV
LOCB1R | SHET | B-2-1a, B-2-2a | 132 | LOCH BUIDHE | 57.9508 | -4.2772 | LOCH BUIDHE 132kV
LOCB1S | SHET | B-2-1a, B-2-2a | 132 | LOCH BUIDHE | 57.9508 | -4.2772 | LOCH BUIDHE 132kV
LOCB1T | SHET | B-2-1a | 132 | LOCH BUIDHE | 57.9508 | -4.2772 | LOCH BUIDHE 132kV
LOCB1U | SHET | B-2-1a, B-2-2a | 132 | LOCH BUIDHE | 57.9508 | -4.2772 | LOCH BUIDHE 132kV
LOCB2J | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | LOCH BUIDHE | 57.9508 | -4.2772 | LOCH BUIDHE 275kV
LOCB2K | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | LOCH BUIDHE | 57.9508 | -4.2772 | LOCH BUIDHE 275kV
LOCB2L | SHET | B-2-2a | 275 | LOCH BUIDHE | 57.9508 | -4.2772 | LOCH BUIDHE 275kV
LOCB2M | SHET | B-2-2a | 275 | LOCH BUIDHE | 57.9508 | -4.2772 | LOCH BUIDHE 275kV
LOCH1- | SHET | B-2-1a, B-3-1a | 132 | LOCHAY | 56.4848 | -4.3639 | LOCHAY 132kV
LOCH5J | SHET | B-3-1a | 11 | LOCHAY | 56.4848 | -4.3639 | LOCHAY 11kV
LOCH5K | SHET | B-3-1a | 11 | LOCHAY | 56.4848 | -4.3639 | LOCHAY 11kV
LOCL1J | SHET | B-2-2a, B-3-2a | 132 | LOCH LUNDIE |  |  | LOCH LUNDIE 132kV
LOCL1K | SHET | B-2-2a, B-3-2a | 132 | LOCH LUNDIE |  |  | LOCH LUNDIE 132kV
LOCL1Q | SHET | B-2-1a, B-2-2a | 132 | LOCH LUNDIE |  |  | LOCH LUNDIE 132kV
LOCL1R | SHET | B-2-1a, B-2-2a | 132 | LOCH LUNDIE |  |  | LOCH LUNDIE 132kV
LOCL4J | SHET | B-2-2a, B-3-2a | 400 | LOCH LUNDIE |  |  | LOCH LUNDIE 400kV
LOCL4K | SHET | B-2-2a, B-3-2a | 400 | LOCH LUNDIE |  |  | LOCH LUNDIE 400kV
LODR61 | NGET | B-3-1c, B-3-2c | 66 | LODGE ROAD | 51.5275 | -0.16956 | LODGE ROAD 66kV
LODR62 | NGET | B-3-1c | 66 | LODGE ROAD | 51.5275 | -0.16956 | LODGE ROAD 66kV
LOFI4A | NGET | B-2-1c | 400 | LONGFIELD | 51.3986 | 0.29875 | LONGFIELD 400kV
LOFI4B | NGET | B-2-1c | 400 | LONGFIELD | 51.3986 | 0.29875 | LONGFIELD 400kV
LORG1- | SPT | B-2-2b, B-3-2b | 132 | LORG | 55.2345 | -4.789 | LORG 132kV
LORG3- | SPT | B-3-2b | 33 | LORG | 55.2345 | -4.789 | LORG 33kV
LOSD1A | SHET | B-2-2a, B-3-2a | 132 | LONGSIDE | 53.4609 | -2.219 | LONGSIDE 132kV
LOSD1B | SHET | B-2-2a, B-3-2a | 132 | LONGSIDE | 53.4609 | -2.219 | LONGSIDE 132kV
LOSD4A | SHET | B-2-2a, B-3-2a | 400 | LONGSIDE | 53.4609 | -2.219 | LONGSIDE 400kV
LOSD4B | SHET | B-2-2a, B-3-2a | 400 | LONGSIDE | 53.4609 | -2.219 | LONGSIDE 400kV
LOSD4R | SHET | B-2-2a | 400 | LONGSIDE | 53.4609 | -2.219 | LONGSIDE 400kV
LOVE11 | NGET | B-3-1c | 132 | LOVEDEAN | 50.9174 | -1.04 | LOVEDEAN 132kV
LOVE12 | NGET | B-3-1c | 132 | LOVEDEAN | 50.9174 | -1.04 | LOVEDEAN 132kV
LOVE41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | LOVEDEAN | 50.9174 | -1.04 | LOVEDEAN 400kV
LUIC1Q | SHET | B-2-1a, B-3-1a | 132 | LUICHART | 57.5758 | -4.6899 | LUICHART 132kV
LUIC1R | SHET | B-2-1a, B-3-1a | 132 | LUICHART | 57.5758 | -4.6899 | LUICHART 132kV
LUIC5J | SHET | B-3-1a | 11 | LUICHART | 57.5758 | -4.6899 | LUICHART 11kV
LUIC5K | SHET | B-3-1a | 11 | LUICHART | 57.5758 | -4.6899 | LUICHART 11kV
LUMB1Q | SHET | B-2-1a | 132 | LUMBS |  |  | LUMBS 132kV
LUMB1R | SHET | B-2-1a | 132 | LUMBS |  |  | LUMBS 132kV
LUNA1Q | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | LUNANHEAD | 56.6543 | -2.8654 | LUNANHEAD 132kV
LUNA1R | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | LUNANHEAD | 56.6543 | -2.8654 | LUNANHEAD 132kV
LUNA3- | SHET | B-3-1a, B-3-2a | 33 | LUNANHEAD | 56.6543 | -2.8654 | LUNANHEAD 33kV
LUND1- | SHET | B-2-1a | 132 | LUNDAVRA |  |  | LUNDAVRA 132kV
LYND1Q | SHET | B-2-1a, B-3-1a | 132 | LYNDHURST | 51.432 | 0.15647 | LYNDHURST 132kV
LYND1R | SHET | B-2-1a, B-3-1a | 132 | LYNDHURST | 51.432 | 0.15647 | LYNDHURST 132kV
LYND3- | SHET | B-3-1a | 33 | LYNDHURST | 51.432 | 0.15647 | LYNDHURST 33kV
MACC21 | NGET | B-2-1c, B-3-1c | 275 | MACCLESFIELD | 53.2687 | -2.1215 | MACCLESFIELD 275kV
MACC31 | NGET | B-3-1c | 33 | MACCLESFIELD | 53.2687 | -2.1215 | MACCLESFIELD 33kV
MACC41 | NGET | B-2-1c, B-3-1c | 400 | MACCLESFIELD | 53.2687 | -2.1215 | MACCLESFIELD 400kV
MACD1Q | SHET | B-2-1a, B-3-1a | 132 | MACDUFF | 57.6639 | -2.4992 | MACDUFF 132kV
MACD1R | SHET | B-2-1a, B-3-1a | 132 | MACDUFF | 57.6639 | -2.4992 | MACDUFF 132kV
MACD3- | SHET | B-3-1a, B-4-1a | 33 | MACDUFF | 57.6639 | -2.4992 | MACDUFF 33kV
MAGA21 | NGET | B-2-1c, B-3-1c | 275 | MARGAM | 51.5629 | -3.7539 | MARGAM 275kV
MAHI1- | SPT | B-2-1b, B-3-1b | 132 | MARK HILL | 55.1379 | -4.7681 | MARK HILL 132kV
MAHI1B | SPT | B-2-2b | 132 | MARK HILL | 55.1379 | -4.7681 | MARK HILL 132kV
MAHI1C | SPT | B-2-2b, B-3-2b | 132 | MARK HILL | 55.1379 | -4.7681 | MARK HILL 132kV
MAHI2- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 275 | MARK HILL | 55.1379 | -4.7681 | MARK HILL 275kV
MAHI3- | SPT | B-2-1b, B-2-2b, B-3-1b | 33 | MARK HILL | 55.1379 | -4.7681 | MARK HILL 33kV
MAHI3U | SPT | B-4-1b | 33 | MARK HILL | 55.1379 | -4.7681 | MARK HILL 33kV
MANN11 | NGET | B-3-1c, B-4-1c | 132 | MANNINGTON | 50.8469 | -1.896 | MANNINGTON 132kV
MANN41 | NGET | B-2-1c, B-3-1c | 400 | MANNINGTON | 50.8469 | -1.896 | MANNINGTON 400kV
MANN82 | NGET | B-4-2c | 22 | MANN (Node Name used) | 50.8469 | -1.896 | MANN (Node Name used) 22kV
MARA4- | SHET | B-2-2a | 400 | MARRAM OFFSHORE |  |  | MARRAM OFFSHORE 400kV
MARH41 | NGET | B-2-1c | 400 | MARKET HARBOROUGH | 52.4647 | -0.88546 | MARKET HARBOROUGH 400kV
MARH42 | NGET | B-2-1c | 400 | MARKET HARBOROUGH | 52.4647 | -0.88546 | MARKET HARBOROUGH 400kV
MARH4A | NGET | B-2-1c | 400 | MARKET HARBOROUGH | 52.4647 | -0.88546 | MARKET HARBOROUGH 400kV
MARH4B | NGET | B-2-1c | 400 | MARKET HARBOROUGH | 52.4647 | -0.88546 | MARKET HARBOROUGH 400kV
MARV41 | NGET | B-2-1c | 400 | MARSTON VALE | 52.0568 | -0.52585 | MARSTON VALE 400kV
MARV4A | NGET | B-2-1c, B-2-2c | 400 | MARSTON VALE | 52.0568 | -0.52585 | MARSTON VALE 400kV
MARV4B | NGET | B-2-1c, B-2-2c | 400 | MARSTON VALE | 52.0568 | -0.52585 | MARSTON VALE 400kV
MAWO41 | NGET | B-2-1c | 400 | MARCHWOOD | 50.8984 | -1.4402 | MARCHWOOD 400kV
MAYB1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | MAYBOLE | 55.3423 | -4.6862 | MAYBOLE 132kV
MAYB3- | SPT | B-3-1b | 33 | MAYBOLE | 55.3423 | -4.6862 | MAYBOLE 33kV
MAYT1T | SPT | B-2-1b | 132 | MAYBOLE TEE | 55.3423 | -4.6862 | MAYBOLE TEE 132kV
MEAD1- | SPT | B-2-1b | 132 | MEADOWHEAD | 55.5843 | -4.6388 | MEADOWHEAD 132kV
MEAD1Q | SPT | B-2-1b | 132 | MEADOWHEAD | 55.5843 | -4.6388 | MEADOWHEAD 132kV
MEAD1R | SPT | B-2-1b | 132 | MEADOWHEAD | 55.5843 | -4.6388 | MEADOWHEAD 132kV
MEDB4A | NGET | B-2-1c | 400 | MEDBURN TEE B | 55.0287 | -1.7925 | MEDBURN TEE B 400kV
MEDB4B | NGET | B-2-1c | 400 | MEDBURN TEE B | 55.0287 | -1.7925 | MEDBURN TEE B 400kV
MEDW41 | NGET | B-2-1c | 400 | MEDWAY | 51.4401 | 0.69035 | MEDWAY 400kV
MELG1J | SHET | B-2-1a, B-3-1a | 132 | MELGARVE SUBSTATION | 57.0281 | -4.4723 | MELGARVE SUBSTATION 132kV
MELG1K | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | MELGARVE SUBSTATION | 57.0281 | -4.4723 | MELGARVE SUBSTATION 132kV
MELG4J | SHET | B-2-1a, B-3-1a, B-4-1a | 400 | MELGARVE SUBSTATION | 57.0281 | -4.4723 | MELGARVE SUBSTATION 400kV
MELG4K | SHET | B-2-1a, B-3-1a, B-4-1a | 400 | MELGARVE SUBSTATION | 57.0281 | -4.4723 | MELGARVE SUBSTATION 400kV
MELG8J | SHET | B-3-1a | 22 | MELG (Node Name used) | 57.0281 | -4.4723 | MELG (Node Name used) 22kV
MELG8K | SHET | B-3-1a | 22 | MELG (Node Name used) | 57.0281 | -4.4723 | MELG (Node Name used) 22kV
MELK11 | NGET | B-3-1c, B-4-1c | 132 | MELKSHAM | 51.3945 | -2.1508 | MELKSHAM 132kV
MELK2A | NGET | B-2-1c, B-3-1c | 275 | MELKSHAM | 51.3945 | -2.1508 | MELKSHAM 275kV
MELK2B | NGET | B-2-1c, B-3-1c | 275 | MELKSHAM | 51.3945 | -2.1508 | MELKSHAM 275kV
MELK41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c, B-4-2c | 400 | MELKSHAM | 51.3945 | -2.1508 | MELKSHAM 400kV
MEYG1- | SHET | B-2-2a | 132 | MEYGEN |  |  | MEYGEN 132kV
MFSN21 | NGET | B-3-2c | 275 | MONK FRYSTON NEW | 53.7563 | -1.2668 | MONK FRYSTON NEW 275kV
MFSN2A | NGET | B-2-2c | 275 | MONK FRYSTON NEW | 53.7563 | -1.2668 | MONK FRYSTON NEW 275kV
MFSN2B | NGET | B-2-2c | 275 | MONK FRYSTON NEW | 53.7563 | -1.2668 | MONK FRYSTON NEW 275kV
MFSN41 | NGET | B-2-2c | 400 | MONK FRYSTON NEW | 53.7563 | -1.2668 | MONK FRYSTON NEW 400kV
MIDL41 | NGET | B-2-1c | 400 | MIDDLETON | 54.0253 | -2.8813 | MIDDLETON 400kV
MIDM1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | MIDDLE MUIR |  |  | MIDDLE MUIR 132kV
MIDM3- | SPT | B-3-1b | 33 | MIDDLE MUIR |  |  | MIDDLE MUIR 33kV
MILC1R | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | MILTON OF CRAIGIE | 56.4746 | -2.9246 | MILTON OF CRAIGIE 132kV
MILC1S | SHET | B-2-1a, B-3-1a | 132 | MILTON OF CRAIGIE | 56.4746 | -2.9246 | MILTON OF CRAIGIE 132kV
MILC1T | SHET | B-2-1a | 132 | MILTON OF CRAIGIE | 56.4746 | -2.9246 | MILTON OF CRAIGIE 132kV
MILC1V | SHET | B-2-1a, B-2-2a | 132 | MILTON OF CRAIGIE | 56.4746 | -2.9246 | MILTON OF CRAIGIE 132kV
MILC3- | SHET | B-3-1a | 33 | MILTON OF CRAIGIE | 56.4746 | -2.9246 | MILTON OF CRAIGIE 33kV
MILH11 | NGET | B-3-1c | 132 | MILL HILL | 51.6179 | -0.20859 | MILL HILL 132kV
MILH12 | NGET | B-3-1c | 132 | MILL HILL | 51.6179 | -0.20859 | MILL HILL 132kV
MILH2A | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | MILL HILL | 51.6179 | -0.20859 | MILL HILL 275kV
MILH2B | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | MILL HILL | 51.6179 | -0.20859 | MILL HILL 275kV
MILP31 | NGET | B-3-1c | 33 | MILTON PARK | 51.6196 | -1.2963 | MILTON PARK 33kV
MILW1Q | SHET | B-2-1a, B-3-1a | 132 | MILLENIUM WIND |  |  | MILLENIUM WIND 132kV
MILW1S | SHET | B-2-1a | 132 | MILLENIUM WIND |  |  | MILLENIUM WIND 132kV
MILW3- | SHET | B-3-1a | 33 | MILLENIUM WIND |  |  | MILLENIUM WIND 33kV
MINN3- | SPT | B-2-1b | 33 | MINNYGAP | 55.256 | -3.5251 | MINNYGAP 33kV
MITY11 | NGET | B-3-1c | 132 | MINETY | 51.6078 | -2.0026 | MINETY 132kV
MITY12 | NGET | B-3-1c | 132 | MINETY | 51.6078 | -2.0026 | MINETY 132kV
MITY41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | MINETY | 51.6078 | -2.0026 | MINETY 400kV
MOFF1- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 132 | MOFFAT | 55.3022 | -3.4267 | MOFFAT 132kV
MOFF1A | SPT | B-2-2b, B-3-2b | 132 | MOFFAT | 55.3022 | -3.4267 | MOFFAT 132kV
MOFF3- | SPT | B-3-2b | 33 | MOFFAT | 55.3022 | -3.4267 | MOFFAT 33kV
MOFF3A | SPT | B-2-1b, B-3-1b | 33 | MOFFAT | 55.3022 | -3.4267 | MOFFAT 33kV
MOFF3U | SPT | B-4-1b | 33 | MOFFAT | 55.3022 | -3.4267 | MOFFAT 33kV
MOFF4- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b, B-4-1b | 400 | MOFFAT | 55.3022 | -3.4267 | MOFFAT 400kV
MOFF4C | SPT | B-2-1b, B-2-2b | 400 | MOFFAT | 55.3022 | -3.4267 | MOFFAT 400kV
MONF21 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c, B-4-1c | 275 | MONK FRYSTON | 53.7563 | -1.2668 | MONK FRYSTON 275kV
MONF22 | NGET | B-2-1c, B-2-2c, B-3-1c | 275 | MONK FRYSTON | 53.7563 | -1.2668 | MONK FRYSTON 275kV
MONF41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | MONK FRYSTON | 53.7563 | -1.2668 | MONK FRYSTON 400kV
MONF42 | NGET | B-3-2c | 400 | MONK FRYSTON | 53.7563 | -1.2668 | MONK FRYSTON 400kV
MONF4A | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 400 | MONK FRYSTON | 53.7563 | -1.2668 | MONK FRYSTON 400kV
MONQ3- | SPT | B-2-2b | 33 | MONQUHILL |  |  | MONQUHILL 33kV
MORF4- | SHET | B-2-1a | 400 | MORAY EAST ONSHORE | 57.4912 | -2.283 | MORAY EAST ONSHORE 400kV
MOSH1Q | SPT | B-2-1b, B-3-1b | 132 | MOSSMORRAN SHELL | 56.1062 | -3.2941 | MOSSMORRAN SHELL 132kV
MOSH1R | SPT | B-2-1b, B-3-1b | 132 | MOSSMORRAN SHELL | 56.1062 | -3.2941 | MOSSMORRAN SHELL 132kV
MOSH5J | SPT | B-3-1b | 11 | MOSSMORRAN SHELL | 56.1062 | -3.2941 | MOSSMORRAN SHELL 11kV
MOSH5K | SPT | B-3-1b | 11 | MOSSMORRAN SHELL | 56.1062 | -3.2941 | MOSSMORRAN SHELL 11kV
MOSM1A | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | MOSSMORRAN | 56.1062 | -3.2941 | MOSSMORRAN 132kV
MOSM1B | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | MOSSMORRAN | 56.1062 | -3.2941 | MOSSMORRAN 132kV
MOSM2- | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | MOSSMORRAN | 56.1062 | -3.2941 | MOSSMORRAN 275kV
MOSM3Q | SPT | B-3-1b | 33 | MOSSMORRAN | 56.1062 | -3.2941 | MOSSMORRAN 33kV
MOSM3R | SPT | B-3-1b | 33 | MOSSMORRAN | 56.1062 | -3.2941 | MOSSMORRAN 33kV
MOSM4- | SPT | B-2-2b | 400 | MOSSMORRAN | 56.1062 | -3.2941 | MOSSMORRAN 400kV
MOSS1Q | SHET | B-2-1a, B-3-1a | 132 | MOSSFORD | 53.3864 | -3.0861 | MOSSFORD 132kV
MOSS1R | SHET | B-2-1a, B-3-1a | 132 | MOSSFORD | 53.3864 | -3.0861 | MOSSFORD 132kV
MOSS1S | SHET | B-2-1a | 132 | MOSSFORD | 53.3864 | -3.0861 | MOSSFORD 132kV
MOSS1T | SHET | B-2-1a | 132 | MOSSFORD | 53.3864 | -3.0861 | MOSSFORD 132kV
MOSS5- | SHET | B-3-1a | 11 | MOSSFORD | 53.3864 | -3.0861 | MOSSFORD 11kV
MOTA1Q | SHET | B-2-1a, B-2-2a | 132 | MOULTAIVE |  |  | MOULTAIVE 132kV
MOTA1R | SHET | B-2-1a, B-2-2a | 132 | MOULTAIVE |  |  | MOULTAIVE 132kV
MOWO4- | SHET | B-2-1a | 400 | MORAY WEST ONSHORE |  |  | MORAY WEST ONSHORE 400kV
MOWO4- | SHET | B-2-1a | 400 | MORAY WEST ONSHORE |  |  | MORAY WEST ONSHORE 400kV
MSHL3- | SHET | B-3-2a | 33 | MOSSY HILL | 53.3753 | -2.9224 | MOSSY HILL 33kV
MUAI1A | SHET | B-2-2a, B-3-2a | 132 | MUAITHEBHEAL WIND FARM |  |  | MUAITHEBHEAL WIND FARM 132kV
MUAI3A | SHET | B-3-2a | 33 | MUAITHEBHEAL WIND FARM |  |  | MUAITHEBHEAL WIND FARM 33kV
MUAI3B | SHET | B-3-2a | 33 | MUAITHEBHEAL WIND FARM |  |  | MUAITHEBHEAL WIND FARM 33kV
MYBS1Q | SHET | B-2-1a, B-2-2a | 132 | MYBSTER | 58.4474 | -3.4251 | MYBSTER 132kV
MYBS1R | SHET | B-2-1a, B-2-2a | 132 | MYBSTER | 58.4474 | -3.4251 | MYBSTER 132kV
MYBS1S | SHET | B-2-1a, B-3-1a | 132 | MYBSTER | 58.4474 | -3.4251 | MYBSTER 132kV
MYBS1T | SHET | B-2-1a, B-3-1a | 132 | MYBSTER | 58.4474 | -3.4251 | MYBSTER 132kV
MYBS3J | SHET | B-3-1a | 33 | MYBSTER | 58.4474 | -3.4251 | MYBSTER 33kV
MYBS3K | SHET | B-3-1a | 33 | MYBSTER | 58.4474 | -3.4251 | MYBSTER 33kV
MYBS3M | SHET | B-2-1a, B-3-1a | 33 | MYBSTER | 58.4474 | -3.4251 | MYBSTER 33kV
MYBS3N | SHET | B-2-1a, B-3-1a | 33 | MYBSTER | 58.4474 | -3.4251 | MYBSTER 33kV
NAIR1Q | SHET | B-2-1a, B-3-1a | 132 | NAIRN | 57.5767 | -3.8476 | NAIRN 132kV
NAIR1R | SHET | B-2-1a, B-3-1a | 132 | NAIRN | 57.5767 | -3.8476 | NAIRN 132kV
NAIR3- | SHET | B-3-1a | 33 | NAIRN | 57.5767 | -3.8476 | NAIRN 33kV
NANT1Q | SHET | B-2-1a, B-3-1a | 132 | NANT (LOCH NANT) |  |  | NANT (LOCH NANT) 132kV
NANT5- | SHET | B-3-1a | 11 | NANT (LOCH NANT) |  |  | NANT (LOCH NANT) 11kV
NEAR2Q | SPT | B-2-1b, B-3-1b | 275 | NEWARTHILL | 55.8248 | -3.9467 | NEWARTHILL 275kV
NEAR2R | SPT | B-2-1b, B-3-1b | 275 | NEWARTHILL | 55.8248 | -3.9467 | NEWARTHILL 275kV
NEAR3- | SPT | B-3-1b | 33 | NEWARTHILL | 55.8248 | -3.9467 | NEWARTHILL 33kV
NECH11 | NGET | B-3-1c | 132 | NECHELLS | 52.5068 | -1.8524 | NECHELLS 132kV
NECH12 | NGET | B-3-1c | 132 | NECHELLS | 52.5068 | -1.8524 | NECHELLS 132kV
NECH21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | NECHELLS | 52.5068 | -1.8524 | NECHELLS 275kV
NECT41 | NGET | B-2-1c, B-2-2c | 400 | NECTON | 52.6698 | 0.79929 | NECTON 400kV
NECT4A | NGET | B-2-1c, B-2-2c | 400 | NECTON | 52.6698 | 0.79929 | NECTON 400kV
NECT4B | NGET | B-2-1c, B-2-2c | 400 | NECTON | 52.6698 | 0.79929 | NECTON 400kV
NECU1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | NEW CUMNOCK | 55.3457 | -4.3346 | NEW CUMNOCK 132kV
NECU1B | SPT | B-2-2b, B-3-2b | 132 | NEW CUMNOCK | 55.3457 | -4.3346 | NEW CUMNOCK 132kV
NECU1C | SPT | B-2-1b, B-2-2b, B-3-2b | 132 | NEW CUMNOCK | 55.3457 | -4.3346 | NEW CUMNOCK 132kV
NECU1Q | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 132 | NEW CUMNOCK | 55.3457 | -4.3346 | NEW CUMNOCK 132kV
NECU1R | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 132 | NEW CUMNOCK | 55.3457 | -4.3346 | NEW CUMNOCK 132kV
NECU2- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 275 | NEW CUMNOCK | 55.3457 | -4.3346 | NEW CUMNOCK 275kV
NEDE4J | SHET | B-2-1a, B-2-2a | 400 | NEW DEER | 57.492 | -2.2845 | NEW DEER 400kV
NEDE4K | SHET | B-2-1a, B-2-2a | 400 | NEW DEER | 57.492 | -2.2845 | NEW DEER 400kV
NEEP21 | NGET | B-2-1c, B-3-1c | 275 | NEEPSEND | 53.4067 | -1.4885 | NEEPSEND 275kV
NEEP31 | NGET | B-3-1c | 33 | NEEPSEND | 53.4067 | -1.4885 | NEEPSEND 33kV
NEEP4A | NGET | B-2-1c, B-3-1c | 400 | NEEPSEND | 53.4067 | -1.4885 | NEEPSEND 400kV
NEIL1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | NEILSTON | 55.8083 | -4.4782 | NEILSTON 132kV
NEIL1C | SPT | B-2-1b, B-3-1b | 132 | NEILSTON | 55.8083 | -4.4782 | NEILSTON 132kV
NEIL2- | SPT | B-2-1b, B-2-2b, B-3-1b, B-4-1b | 275 | NEILSTON | 55.8083 | -4.4782 | NEILSTON 275kV
NEIL2C | SPT | B-2-1b, B-3-1b | 275 | NEILSTON | 55.8083 | -4.4782 | NEILSTON 275kV
NEIL2D | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | NEILSTON | 55.8083 | -4.4782 | NEILSTON 275kV
NEIL3U | SPT | B-4-1b | 33 | NEILSTON | 55.8083 | -4.4782 | NEILSTON 33kV
NEIL3V | SPT | B-4-1b | 33 | NEILSTON | 55.8083 | -4.4782 | NEILSTON 33kV
NEIL4Q | SPT | B-2-1b, B-3-1b | 400 | NEILSTON | 55.8083 | -4.4782 | NEILSTON 400kV
NEIL4R | SPT | B-2-1b, B-3-1b | 400 | NEILSTON | 55.8083 | -4.4782 | NEILSTON 400kV
NETH3- | SPT | B-2-1b, B-2-2b | 33 | NETHERTON ENERGY | 53.4923 | -2.9703 | NETHERTON ENERGY 33kV
NETS1- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 132 | NEWTON STEWART | 54.9529 | -4.4992 | NEWTON STEWART 132kV
NETS3- | SPT | B-3-1b, B-3-2b | 33 | NEWTON STEWART | 54.9529 | -4.4992 | NEWTON STEWART 33kV
NEWX11 | NGET | B-3-1c | 132 | NEW CROSS | 51.4846 | -0.059541 | NEW CROSS 132kV
NEWX21 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c, B-4-1c | 275 | NEW CROSS | 51.4846 | -0.059541 | NEW CROSS 275kV
NEWX41 | NGET | B-2-2c, B-3-2c | 400 | NEW CROSS | 51.4846 | -0.059541 | NEW CROSS 400kV
NEWX61 | NGET | B-3-1c | 66 | NEW CROSS | 51.4846 | -0.059541 | NEW CROSS 66kV
NEWX62 | NGET | B-3-1c | 66 | NEW CROSS | 51.4846 | -0.059541 | NEW CROSS 66kV
NFLE11 | NGET | B-3-1c | 132 | NORTHFLEET EAST | 51.4288 | 0.33031 | NORTHFLEET EAST 132kV
NFLE12 | NGET | B-3-1c | 132 | NORTHFLEET EAST | 51.4288 | 0.33031 | NORTHFLEET EAST 132kV
NFLE41 | NGET | B-2-1c, B-3-1c | 400 | NORTHFLEET EAST | 51.4288 | 0.33031 | NORTHFLEET EAST 400kV
NHYD2A | NGET | B-2-1c, B-3-1c | 275 | NORTH HYDE | 51.4999 | -0.4114 | NORTH HYDE 275kV
NHYD2B | NGET | B-2-1c, B-3-1c | 275 | NORTH HYDE | 51.4999 | -0.4114 | NORTH HYDE 275kV
NHYD61 | NGET | B-3-1c | 66 | NORTH HYDE | 51.4999 | -0.4114 | NORTH HYDE 66kV
NINF11 | NGET | B-3-1c | 132 | NINFIELD | 50.8815 | 0.44775 | NINFIELD 132kV
NINF12 | NGET | B-3-1c | 132 | NINFIELD | 50.8815 | 0.44775 | NINFIELD 132kV
NINF41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | NINFIELD | 50.8815 | 0.44775 | NINFIELD 400kV
NLEI1- | SPT | B-2-2b, B-3-2b | 132 | NORTH LOWTHER ENERGY INITIATIVE |  |  | NORTH LOWTHER ENERGY INITIATIVE 132kV
NLEI3A | SPT | B-3-2b | 33 | NORTH LOWTHER ENERGY INITIATIVE |  |  | NORTH LOWTHER ENERGY INITIATIVE 33kV
NLEI3B | SPT | B-3-2b | 33 | NORTH LOWTHER ENERGY INITIATIVE |  |  | NORTH LOWTHER ENERGY INITIATIVE 33kV
NOKY1- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 132 | NORTH KYLE | 57.281 | -5.7097 | NORTH KYLE 132kV
NOKY3A | SPT | B-3-1b, B-3-2b | 33 | NORTH KYLE | 57.281 | -5.7097 | NORTH KYLE 33kV
NOKY3B | SPT | B-3-1b, B-3-2b | 33 | NORTH KYLE | 57.281 | -5.7097 | NORTH KYLE 33kV
NORL2A | NGET | B-2-1c, B-3-1c | 275 | NORTON LEES | 53.3485 | -1.4715 | NORTON LEES 275kV
NORL2B | NGET | B-2-1c, B-3-1c | 275 | NORTON LEES | 53.3485 | -1.4715 | NORTON LEES 275kV
NORL31 | NGET | B-3-1c | 33 | NORTON LEES | 53.3485 | -1.4715 | NORTON LEES 33kV
NORM11 | NGET | B-3-1c | 132 | NORWICH MAIN | 52.5741 | 1.2719 | NORWICH MAIN 132kV
NORM12 | NGET | B-3-1c | 132 | NORWICH MAIN | 52.5741 | 1.2719 | NORWICH MAIN 132kV
NORM1A | NGET | B-3-1c | 132 | NORWICH MAIN | 52.5741 | 1.2719 | NORWICH MAIN 132kV
NORM1B | NGET | B-3-1c | 132 | NORWICH MAIN | 52.5741 | 1.2719 | NORWICH MAIN 132kV
NORM41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | NORWICH MAIN | 52.5741 | 1.2719 | NORWICH MAIN 400kV
NORT11 | NGET | B-3-1c | 132 | NORTON | 54.5928 | -1.3673 | NORTON 132kV
NORT21 | NGET | B-2-1c, B-2-2c, B-3-1c | 275 | NORTON | 54.5928 | -1.3673 | NORTON 275kV
NORT41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-2c | 400 | NORTON | 54.5928 | -1.3673 | NORTON 400kV
NORW11 | NGET | B-2-1c | 132 | NORWICH | 52.5741 | 1.2719 | NORWICH 132kV
NORW12 | NGET | B-2-1c | 132 | NORWICH | 52.5741 | 1.2719 | NORWICH 132kV
NOTR11 | NGET | B-2-1c | 132 | NORWICH TROWSE | 52.6078 | 1.3079 | NORWICH TROWSE 132kV
NOTR12 | NGET | B-2-1c | 132 | NORWICH TROWSE | 52.6078 | 1.3079 | NORWICH TROWSE 132kV
NPIC4- | SHET | B-2-2a | 400 | SPIORAD NA MARA OFFSHORE WIND FARM |  |  | SPIORAD NA MARA OFFSHORE WIND FARM 400kV
NURS11 | NGET | B-3-1c | 132 | NURSLING | 50.9425 | -1.4867 | NURSLING 132kV
NURS41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | NURSLING | 50.9425 | -1.4867 | NURSLING 400kV
NURS4A | NGET | B-2-1c, B-3-1c | 400 | NURSLING | 50.9425 | -1.4867 | NURSLING 400kV
OBST4A | NGET | B-2-2c | 400 | OSBALDWICK TEE | 53.9566 | -1.0226 | OSBALDWICK TEE 400kV
OBST4B | NGET | B-2-2c | 400 | OSBALDWICK TEE | 53.9566 | -1.0226 | OSBALDWICK TEE 400kV
OCKH11 | NGET | B-3-1c | 132 | OCKER HILL | 52.5419 | -2.0297 | OCKER HILL 132kV
OCKH21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | OCKER HILL | 52.5419 | -2.0297 | OCKER HILL 275kV
OCKH2A | NGET | B-2-1c, B-3-1c | 275 | OCKER HILL | 52.5419 | -2.0297 | OCKER HILL 275kV
OFFE21 | NGET | B-2-1c, B-3-1c | 275 | OFFERTON | 54.8808 | -1.458 | OFFERTON 275kV
OFFE31 | NGET | B-3-1c | 33 | OFFERTON | 54.8808 | -1.458 | OFFERTON 33kV
OFFE32 | NGET | B-3-1c | 33 | OFFERTON | 54.8808 | -1.458 | OFFERTON 33kV
OFOA1- | SPT | B-2-2b, B-3-2b | 132 | OLD FOREST OF AE |  |  | OLD FOREST OF AE 132kV
OFOA1T | SPT | B-2-2b | 132 | OLD FOREST OF AE |  |  | OLD FOREST OF AE 132kV
OFOA3- | SPT | B-3-2b | 33 | OLD FOREST OF AE |  |  | OLD FOREST OF AE 33kV
OHLL1- | SPT | B-2-2b, B-3-2b | 132 | OVERHILL | 53.1914 | -2.5383 | OVERHILL 132kV
OHLL3- | SPT | B-3-2b | 33 | OVERHILL | 53.1914 | -2.5383 | OVERHILL 33kV
OLDB11 | NGET | B-3-1c | 132 | OLDBURY | 52.4994 | -2.023 | OLDBURY 132kV
OLDB21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | OLDBURY | 52.4994 | -2.023 | OLDBURY 275kV
OLDB2A | NGET | B-2-1c, B-3-1c | 275 | OLDBURY | 52.4994 | -2.023 | OLDBURY 275kV
OLDB4A | NGET | B-2-1c, B-3-1c | 400 | OLDBURY | 52.4994 | -2.023 | OLDBURY 400kV
OLDS12 | NGET | B-2-1c | 132 | OLDBURY ON SEVERN | 51.6473 | -2.5719 | OLDBURY ON SEVERN 132kV
ORLA1- | SPT | B-2-2b | 132 | ORANGE LANE |  |  | ORANGE LANE 132kV
ORRI1Q | SHET | B-2-1a, B-3-1a | 132 | ORRIN | 51.383 | -2.1694 | ORRIN 132kV
ORRI1R | SHET | B-2-1a, B-3-1a | 132 | ORRIN | 51.383 | -2.1694 | ORRIN 132kV
ORRI1S | SHET | B-2-1a | 132 | ORRIN | 51.383 | -2.1694 | ORRIN 132kV
ORRI1T | SHET | B-2-1a | 132 | ORRIN | 51.383 | -2.1694 | ORRIN 132kV
ORRI3- | SHET | B-3-1a | 33 | ORRIN | 51.383 | -2.1694 | ORRIN 33kV
ORRI5- | SHET | B-3-1a | 11 | ORRIN | 51.383 | -2.1694 | ORRIN 11kV
OSBA11 | NGET | B-3-1c, B-3-2c | 132 | OSBALDWICK | 53.9568 | -1.0225 | OSBALDWICK 132kV
OSBA41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | OSBALDWICK | 53.9568 | -1.0225 | OSBALDWICK 400kV
OSBA42 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 400 | OSBALDWICK | 53.9568 | -1.0225 | OSBALDWICK 400kV
OVER21 | NGET | B-2-2c, B-3-2c | 275 | YORK NORTH | 54.0036 | -1.1561 | YORK NORTH 275kV
OWFD1- | SHET | B-2-2a | 132 | OWF-100 |  |  | OWF-100 132kV
OWPL4- | SHET | B-2-2a | 400 | OWPL WINDFARM |  |  | OWPL WINDFARM 400kV
PADI11 | NGET | B-3-1c | 132 | PADIHAM | 53.7954 | -2.3211 | PADIHAM 132kV
PADI41 | NGET | B-2-1c, B-3-1c | 400 | PADIHAM | 53.7954 | -2.3211 | PADIHAM 400kV
PAFB4A | NGET | B-2-1c | 400 | PATFORD BRIDGE | 52.2916 | -1.0552 | PATFORD BRIDGE 400kV
PAFB4B | NGET | B-2-1c | 400 | PATFORD BRIDGE | 52.2916 | -1.0552 | PATFORD BRIDGE 400kV
PAIS1Q | SPT | B-2-1b | 132 | PAISLEY | 55.8402 | -4.4126 | PAISLEY 132kV
PAIS1R | SPT | B-2-1b | 132 | PAISLEY | 55.8402 | -4.4126 | PAISLEY 132kV
PAIS1S | SPT | B-2-1b, B-3-1b | 132 | PAISLEY | 55.8402 | -4.4126 | PAISLEY 132kV
PAIS1T | SPT | B-2-1b, B-3-1b | 132 | PAISLEY | 55.8402 | -4.4126 | PAISLEY 132kV
PAIS3- | SPT | B-3-1b | 33 | PAISLEY | 55.8402 | -4.4126 | PAISLEY 33kV
PART1Q | SPT | B-2-1b, B-3-1b | 132 | PARTICK | 55.8694 | -4.3162 | PARTICK 132kV
PART1R | SPT | B-2-1b, B-3-1b | 132 | PARTICK | 55.8694 | -4.3162 | PARTICK 132kV
PART3- | SPT | B-3-1b | 33 | PARTICK | 55.8694 | -4.3162 | PARTICK 33kV
PEHE1- | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | PETERHEAD | 57.4741 | -1.7975 | PETERHEAD 132kV
PEHE2- | SHET | B-2-1a, B-2-2a | 275 | PETERHEAD | 57.4741 | -1.7975 | PETERHEAD 275kV
PEHE2J | SHET | B-2-1a, B-3-1a | 275 | PETERHEAD | 57.4741 | -1.7975 | PETERHEAD 275kV
PEHE2K | SHET | B-2-1a, B-3-1a | 275 | PETERHEAD | 57.4741 | -1.7975 | PETERHEAD 275kV
PEHE2Q | SHET | B-2-1a, B-3-1a | 275 | PETERHEAD | 57.4741 | -1.7975 | PETERHEAD 275kV
PEHE2R | SHET | B-2-1a, B-3-1a | 275 | PETERHEAD | 57.4741 | -1.7975 | PETERHEAD 275kV
PEHE2S | SHET | B-2-1a | 275 | PETERHEAD | 57.4741 | -1.7975 | PETERHEAD 275kV
PEHE2T | SHET | B-2-1a | 275 | PETERHEAD | 57.4741 | -1.7975 | PETERHEAD 275kV
PEHE2U | SHET | B-2-1a | 275 | PETERHEAD | 57.4741 | -1.7975 | PETERHEAD 275kV
PEHE2V | SHET | B-2-1a | 275 | PETERHEAD | 57.4741 | -1.7975 | PETERHEAD 275kV
PEHE2W | SHET | B-2-1a | 275 | PETERHEAD | 57.4741 | -1.7975 | PETERHEAD 275kV
PEHE4J | SHET | B-2-1a, B-2-2a, B-3-1a | 400 | PETERHEAD | 57.4741 | -1.7975 | PETERHEAD 400kV
PEHE4K | SHET | B-2-1a, B-2-2a, B-3-1a | 400 | PETERHEAD | 57.4741 | -1.7975 | PETERHEAD 400kV
PEHE4L | SHET | B-2-2a | 400 | PETERHEAD | 57.4741 | -1.7975 | PETERHEAD 400kV
PEHEMEC1 | SHET | B-2-1a | Unknown | PEHE (Node Name used) | 57.4741 | -1.7975 | PEHE (Node Name used) UnknownkV
PEHEMEC2 | SHET | B-2-1a | Unknown | PEHE (Node Name used) | 57.4741 | -1.7975 | PEHE (Node Name used) UnknownkV
PEHEMEC3 | SHET | B-2-1a | Unknown | PEHE (Node Name used) | 57.4741 | -1.7975 | PEHE (Node Name used) UnknownkV
PEHEMEC4 | SHET | B-2-1a | Unknown | PEHE (Node Name used) | 57.4741 | -1.7975 | PEHE (Node Name used) UnknownkV
PEHEMEC5 | SHET | B-2-1a | Unknown | PEHE (Node Name used) | 57.4741 | -1.7975 | PEHE (Node Name used) UnknownkV
PEHEMEC6 | SHET | B-2-1a | Unknown | PEHE (Node Name used) | 57.4741 | -1.7975 | PEHE (Node Name used) UnknownkV
PEHERSV1 | SHET | B-2-1a | Unknown | PEHE (Node Name used) | 57.4741 | -1.7975 | PEHE (Node Name used) UnknownkV
PEHERSV2 | SHET | B-2-1a | Unknown | PEHE (Node Name used) | 57.4741 | -1.7975 | PEHE (Node Name used) UnknownkV
PEHG1Q | SHET | B-2-1a, B-3-1a | 132 | PETERHEAD GRANGE | 57.5087 | -1.8063 | PETERHEAD GRANGE 132kV
PEHG1R | SHET | B-2-1a, B-3-1a | 132 | PETERHEAD GRANGE | 57.5087 | -1.8063 | PETERHEAD GRANGE 132kV
PEHG3- | SHET | B-3-1a | 33 | PETERHEAD GRANGE | 57.5087 | -1.8063 | PETERHEAD GRANGE 33kV
PEHS5- | SHET | B-3-1a | 11 | PETERHEAD SHELL | 57.4741 | -1.7975 | PETERHEAD SHELL 11kV
PELH11 | NGET | B-3-1c | 132 | PELHAM | 51.9351 | 0.11868 | PELHAM 132kV
PELH12 | NGET | B-3-1c | 132 | PELHAM | 51.9351 | 0.11868 | PELHAM 132kV
PELH41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c, B-4-1c | 400 | PELHAM | 51.9351 | 0.11868 | PELHAM 400kV
PEMB11 | NGET | B-3-1c | 132 | PEMBROKE | 51.6821 | -4.9905 | PEMBROKE 132kV
PEMB41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | PEMBROKE | 51.6821 | -4.9905 | PEMBROKE 400kV
PENE11 | NGET | B-3-1c | 132 | PENWORTHAM EAST | 53.7463 | -2.7566 | PENWORTHAM EAST 132kV
PENI4A | NGET | B-2-2c | 400 | PENISARWAUN | 53.1542 | -4.1777 | PENISARWAUN 400kV
PENN11 | NGET | B-3-1c | 132 | PENN | 52.5569 | -2.2098 | PENN 132kV
PENN21 | NGET | B-2-1c, B-3-1c | 275 | PENN | 52.5569 | -2.2098 | PENN 275kV
PENN4A | NGET | B-2-1c, B-3-1c | 400 | PENN | 52.5569 | -2.2098 | PENN 400kV
PENN4B | NGET | B-2-1c, B-3-1c | 400 | PENN | 52.5569 | -2.2098 | PENN 400kV
PENT11 | NGET | B-3-1c | 132 | PENTIR | 53.1876 | -4.158 | PENTIR 132kV
PENT41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | PENTIR | 53.1876 | -4.158 | PENTIR 400kV
PENW11 | NGET | B-3-1c | 132 | PENWORTHAM WEST | 53.745 | -2.7581 | PENWORTHAM WEST 132kV
PERS1Q | SHET | B-2-1a, B-3-1a | 132 | PERSLEY | 57.1747 | -2.1392 | PERSLEY 132kV
PERS1R | SHET | B-2-1a, B-3-1a | 132 | PERSLEY | 57.1747 | -2.1392 | PERSLEY 132kV
PERS2Q | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | PERSLEY | 57.1747 | -2.1392 | PERSLEY 275kV
PERS2R | SHET | B-2-1a, B-3-1a | 275 | PERSLEY | 57.1747 | -2.1392 | PERSLEY 275kV
PERS3- | SHET | B-3-1a | 33 | PERSLEY | 57.1747 | -2.1392 | PERSLEY 33kV
PEWO2A | NGET | B-2-1c, B-3-1c | 275 | PENWORTHAM | 53.7433 | -2.7561 | PENWORTHAM 275kV
PEWO2B | NGET | B-2-1c, B-3-1c | 275 | PENWORTHAM | 53.7433 | -2.7561 | PENWORTHAM 275kV
PEWO2C | NGET | B-2-1c | 275 | PENWORTHAM | 53.7433 | -2.7561 | PENWORTHAM 275kV
PEWO2D | NGET | B-2-1c | 275 | PENWORTHAM | 53.7433 | -2.7561 | PENWORTHAM 275kV
PEWO41 | NGET | B-2-1c, B-3-1c, B-4-1c, B-4-2c | 400 | PENWORTHAM | 53.7433 | -2.7561 | PENWORTHAM 400kV
PEWO4A | NGET | B-2-1c, B-3-1c | 400 | PENWORTHAM | 53.7433 | -2.7561 | PENWORTHAM 400kV
PEWO4B | NGET | B-2-1c, B-3-1c | 400 | PENWORTHAM | 53.7433 | -2.7561 | PENWORTHAM 400kV
PITS21 | NGET | B-2-1c, B-2-2c, B-3-1c | 275 | PITSMOOR | 53.4007 | -1.4437 | PITSMOOR 275kV
PITS31 | NGET | B-3-1c, B-4-1c | 33 | PITSMOOR | 53.4007 | -1.4437 | PITSMOOR 33kV
PITS32 | NGET | B-3-1c | 33 | PITSMOOR | 53.4007 | -1.4437 | PITSMOOR 33kV
PLOE3- | SPT | B-2-2b | 33 | PENCLOE |  |  | PENCLOE 33kV
POAB11 | NGET | B-3-2c | 132 | POAB (Node Name used) | 51.7478 | -4.0668 | POAB (Node Name used) 132kV
POAB41 | NGET | B-2-2c, B-3-2c | 400 | PONT ABRAHAM | 51.7478 | -4.0668 | PONT ABRAHAM 400kV
POGB3- | SPT | B-2-1b, B-2-2b | 33 | POGBIE |  |  | POGBIE 33kV
POOB2Q | SPT | B-2-1b, B-3-1b | 275 | PORTOBELLO | 55.954 | -3.125 | PORTOBELLO 275kV
POOB2R | SPT | B-2-1b, B-3-1b | 275 | PORTOBELLO | 55.954 | -3.125 | PORTOBELLO 275kV
POOB3- | SPT | B-3-1b | 33 | PORTOBELLO | 55.954 | -3.125 | PORTOBELLO 33kV
POPP21 | NGET | B-2-1c, B-2-2c, B-3-1c | 275 | POPPLETON | 53.9751 | -1.1317 | POPPLETON 275kV
POPP31 | NGET | B-3-1c | 33 | POPPLETON | 53.9751 | -1.1317 | POPPLETON 33kV
PORA1R | SHET | B-2-1a, B-2-2a | 132 | PORT ANN | 56.0286 | -5.3567 | PORT ANN 132kV
PORA1S | SHET | B-2-1a, B-2-2a | 132 | PORT ANN | 56.0286 | -5.3567 | PORT ANN 132kV
PORA1T | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | PORT ANN | 56.0286 | -5.3567 | PORT ANN 132kV
PORA1U | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 132 | PORT ANN | 56.0286 | -5.3567 | PORT ANN 132kV
PORA3- | SHET | B-3-1a, B-3-2a | 33 | PORT ANN | 56.0286 | -5.3567 | PORT ANN 33kV
PORD2Q | SPT | B-2-1b, B-3-1b | 275 | PORT DUNDAS | 55.8741 | -4.2557 | PORT DUNDAS 275kV
PORD2R | SPT | B-2-1b, B-3-1b, B-3-2b | 275 | PORT DUNDAS | 55.8741 | -4.2557 | PORT DUNDAS 275kV
PORD3- | SPT | B-3-1b, B-3-2b | 33 | PORT DUNDAS | 55.8741 | -4.2557 | PORT DUNDAS 33kV
PORH11 | NGET | B-3-1c, B-4-1c | 132 | PORT HAM | 51.8792 | -2.2539 | PORT HAM 132kV
PRST3A | SPT | B-2-1b | 33 | PRIESTGILL |  |  | PRIESTGILL 33kV
PUDM41 | NGET | B-2-1c | 400 | PUDDING MILL LANE | 51.5314 | -0.014417 | PUDDING MILL LANE 400kV
PYLE11 | NGET | B-3-1c | 132 | PYLE | 51.5359 | -3.6878 | PYLE 132kV
PYLE21 | NGET | B-2-1c, B-3-1c | 275 | PYLE | 51.5359 | -3.6878 | PYLE 275kV
QUAN1- | SPT | B-2-2b, B-3-2b | 132 | QUANTANS HILL |  |  | QUANTANS HILL 132kV
QUAN3- | SPT | B-3-2b | 33 | QUANTANS HILL |  |  | QUANTANS HILL 33kV
QUER4A | NGET | B-2-1c | 400 | QUERNMOOR | 54.047 | -2.7418 | QUERNMOOR 400kV
QUER4B | NGET | B-2-1c | 400 | QUERNMOOR | 54.047 | -2.7418 | QUERNMOOR 400kV
QUOI1- | SHET | B-2-1a, B-3-1a | 132 | QUOICH | 57.0628 | -5.1235 | QUOICH 132kV
QUOI1Q | SHET | B-2-1a, B-2-2a | 132 | QUOICH | 57.0628 | -5.1235 | QUOICH 132kV
QUOI5- | SHET | B-3-1a | 11 | QUOICH | 57.0628 | -5.1235 | QUOICH 11kV
RAIN11 | NGET | B-3-1c, B-4-1c | 132 | RAINHILL | 53.4212 | -2.7389 | RAINHILL 132kV
RAIN12 | NGET | B-3-1c, B-4-1c | 132 | RAINHILL | 53.4212 | -2.7389 | RAINHILL 132kV
RAIN21 | NGET | B-2-1c, B-3-1c | 275 | RAINHILL | 53.4212 | -2.7389 | RAINHILL 275kV
RANN1Q | SHET | B-2-1a, B-3-1a | 132 | RANNOCH | 56.6933 | -4.4015 | RANNOCH 132kV
RANN1R | SHET | B-2-1a, B-3-1a | 132 | RANNOCH | 56.6933 | -4.4015 | RANNOCH 132kV
RANN3Q | SHET | B-3-1a | 33 | RANNOCH | 56.6933 | -4.4015 | RANNOCH 33kV
RASS11 | NGET | B-3-1c | 132 | RASSAU | 51.8083 | -3.2267 | RASSAU 132kV
RASS41 | NGET | B-2-1c, B-3-1c | 400 | RASSAU | 51.8083 | -3.2267 | RASSAU 400kV
RATS11 | NGET | B-3-1c | 132 | RATCLIFFE-ON-SOAR | 52.8638 | -1.256 | RATCLIFFE-ON-SOAR 132kV
RATS12 | NGET | B-3-1c | 132 | RATCLIFFE-ON-SOAR | 52.8638 | -1.256 | RATCLIFFE-ON-SOAR 132kV
RATS2A | NGET | B-2-1c, B-3-1c | 275 | RATCLIFFE-ON-SOAR | 52.8638 | -1.256 | RATCLIFFE-ON-SOAR 275kV
RATS41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | RATCLIFFE-ON-SOAR | 52.8638 | -1.256 | RATCLIFFE-ON-SOAR 400kV
RAVE3S | SPT | B-2-1b | 33 | RAVENSCRAIG |  |  | RAVENSCRAIG 33kV
RAVE3T | SPT | B-2-1b | 33 | RAVENSCRAIG |  |  | RAVENSCRAIG 33kV
RAYL41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | RAYLEIGH | 51.5941 | 0.56645 | RAYLEIGH 400kV
RAYM11 | NGET | B-3-1c | 132 | RAYLEIGH MAIN | 51.5937 | 0.5685 | RAYLEIGH MAIN 132kV
REBR21 | NGET | B-2-1c, B-3-1c | 275 | REDBRIDGE | 51.5885 | 0.042994 | REDBRIDGE 275kV
REBR22 | NGET | B-2-1c, B-3-1c | 275 | REDBRIDGE | 51.5885 | 0.042994 | REDBRIDGE 275kV
REBR31 | NGET | B-3-1c | 33 | REDBRIDGE | 51.5885 | 0.042994 | REDBRIDGE 33kV
REBR32 | NGET | B-3-1c | 33 | REDBRIDGE | 51.5885 | 0.042994 | REDBRIDGE 33kV
REDH1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | REDHOUSE | 56.1461 | -3.1461 | REDHOUSE 132kV
REDH3- | SPT | B-3-1b | 33 | REDHOUSE | 56.1461 | -3.1461 | REDHOUSE 33kV
REDM1Q | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | REDMOSS | 57.1085 | -2.0922 | REDMOSS 132kV
REDM1R | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | REDMOSS | 57.1085 | -2.0922 | REDMOSS 132kV
REDM3- | SHET | B-3-1a | 33 | REDMOSS | 57.1085 | -2.0922 | REDMOSS 33kV
REDS1A | SPT | B-2-2b, B-3-2b | 132 | REDSHAW |  |  | REDSHAW 132kV
REDS3A | SPT | B-3-2b | 33 | REDSHAW |  |  | REDSHAW 33kV
REDS4- | SPT | B-2-2b, B-3-2b | 400 | REDSHAW |  |  | REDSHAW 400kV
REJO2A | SHET | B-2-2a | 275 | RED JOHN PSH STORAGE |  |  | RED JOHN PSH STORAGE 275kV
REJO2B | SHET | B-2-2a | 275 | RED JOHN PSH STORAGE |  |  | RED JOHN PSH STORAGE 275kV
RHIG41 | NGET | B-2-1c | 400 | RHIGOS | 51.7466 | -3.545 | RHIGOS 400kV
RICH11 | NGET | B-3-1c | 132 | RICHBOROUGH | 51.3115 | 1.3441 | RICHBOROUGH 132kV
RICH41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | RICHBOROUGH | 51.3115 | 1.3441 | RICHBOROUGH 400kV
ROCH11 | NGET | B-3-1c, B-4-1c | 132 | ROCHDALE | 53.6219 | -2.2168 | ROCHDALE 132kV
ROCH12 | NGET | B-3-1c | 132 | ROCHDALE | 53.6219 | -2.2168 | ROCHDALE 132kV
ROCH21 | NGET | B-2-1c, B-3-1c | 275 | ROCHDALE | 53.6219 | -2.2168 | ROCHDALE 275kV
ROCH4A | NGET | B-2-1c, B-3-1c | 400 | ROCHDALE | 53.6219 | -2.2168 | ROCHDALE 400kV
ROCK1A | NGET | B-3-1c | 132 | ROCKSAVAGE | 53.315 | -2.725 | ROCKSAVAGE 132kV
ROCK41 | NGET | B-2-1c, B-3-1c | 400 | ROCKSAVAGE | 53.315 | -2.725 | ROCKSAVAGE 400kV
ROTI3- | SHET | B-3-1a | 33 | ROTHIENORMAN | 57.4082 | -2.5159 | ROTHIENORMAN 33kV
ROTI4J | SHET | B-2-1a, B-2-2a, B-3-1a | 400 | ROTHIENORMAN | 57.4082 | -2.5159 | ROTHIENORMAN 400kV
ROTI4K | SHET | B-2-1a, B-2-2a, B-3-1a | 400 | ROTHIENORMAN | 57.4082 | -2.5159 | ROTHIENORMAN 400kV
ROWD41 | NGET | B-2-1c, B-4-2c | 400 | ROWDOWN | 51.3519 | -0.0035626 | ROWDOWN 400kV
ROWD42 | NGET | B-2-1c | 400 | ROWDOWN | 51.3519 | -0.0035626 | ROWDOWN 400kV
ROWD4A | NGET | B-2-1c | 400 | ROWDOWN | 51.3519 | -0.0035626 | ROWDOWN 400kV
ROWD4B | NGET | B-2-1c | 400 | ROWDOWN | 51.3519 | -0.0035626 | ROWDOWN 400kV
RUGE11 | NGET | B-3-1c | 132 | RUGELEY | 52.7567 | -1.915 | RUGELEY 132kV
RUGE41 | NGET | B-2-1c, B-3-1c | 400 | RUGELEY | 52.7567 | -1.915 | RUGELEY 400kV
RYEH11 | NGET | B-3-1c | 132 | RYE HOUSE | 51.759 | 0.0085411 | RYE HOUSE 132kV
RYEH12 | NGET | B-3-1c | 132 | RYE HOUSE | 51.759 | 0.0085411 | RYE HOUSE 132kV
RYEH13 | NGET | B-3-1c | 132 | RYE HOUSE | 51.759 | 0.0085411 | RYE HOUSE 132kV
RYEH41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | RYE HOUSE | 51.759 | 0.0085411 | RYE HOUSE 400kV
RYEH42 | NGET | B-2-1c, B-3-1c | 400 | RYE HOUSE | 51.759 | 0.0085411 | RYE HOUSE 400kV
RYEH43 | NGET | B-2-1c, B-3-1c | 400 | RYE HOUSE | 51.759 | 0.0085411 | RYE HOUSE 400kV
RYEH4A | NGET | B-2-1c, B-2-2c | 400 | RYE HOUSE | 51.759 | 0.0085411 | RYE HOUSE 400kV
RYEH4B | NGET | B-2-1c, B-2-2c | 400 | RYE HOUSE | 51.759 | 0.0085411 | RYE HOUSE 400kV
RYHA4A | NGET | B-2-1c | 400 | RYHALL | 52.6866 | -0.45843 | RYHALL 400kV
RYHA4B | NGET | B-2-1c | 400 | RYHALL | 52.6866 | -0.45843 | RYHALL 400kV
SACO1Q | SPT | B-2-1b, B-3-1b | 132 | SALTCOATS | 55.6467 | -4.7966 | SALTCOATS 132kV
SACO1R | SPT | B-2-1b, B-3-1b | 132 | SALTCOATS | 55.6467 | -4.7966 | SALTCOATS 132kV
SACO3J | SPT | B-3-1b | 33 | SALTCOATS | 55.6467 | -4.7966 | SALTCOATS 33kV
SACO3K | SPT | B-3-1b | 33 | SALTCOATS | 55.6467 | -4.7966 | SALTCOATS 33kV
SAEN11 | NGET | B-3-1c | 132 | SALTEND NORTH | 53.742 | -0.2385 | SALTEND NORTH 132kV
SAEN21 | NGET | B-2-1c, B-3-1c | 275 | SALTEND NORTH | 53.742 | -0.2385 | SALTEND NORTH 275kV
SAES21 | NGET | B-2-1c | 275 | SALTEND SOUTH | 53.7372 | -0.2429 | SALTEND SOUTH 275kV
SAFO11 | NGET | B-3-1c | 132 | SANDFORD | 51.3393 | -2.8413 | SANDFORD 132kV
SAFO41 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | SANDFORD | 51.3393 | -2.8413 | SANDFORD 400kV
SAKN1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | SANDY KNOWE |  |  | SANDY KNOWE 132kV
SAKN3- | SPT | B-3-1b | 33 | SANDY KNOWE |  |  | SANDY KNOWE 33kV
SALH11 | NGET | B-3-1c | 132 | SALTHOLME | 54.6055 | -1.2378 | SALTHOLME 132kV
SALH21 | NGET | B-2-1c, B-3-1c | 275 | SALTHOLME | 54.6055 | -1.2378 | SALTHOLME 275kV
SALH41 | NGET | B-2-1c, B-2-2c | 400 | SALTHOLME | 54.6055 | -1.2378 | SALTHOLME 400kV
SALH42 | NGET | B-2-1c, B-2-2c | 400 | SALTHOLME | 54.6055 | -1.2378 | SALTHOLME 400kV
SALM1A | SHET | B-2-2a | 132 | SALAMANDER OFFSHORE WIND FARM |  |  | SALAMANDER OFFSHORE WIND FARM 132kV
SALM1B | SHET | B-2-2a | 132 | SALAMANDER OFFSHORE WIND FARM |  |  | SALAMANDER OFFSHORE WIND FARM 132kV
SALM1C | SHET | B-2-2a | 132 | SALAMANDER OFFSHORE WIND FARM |  |  | SALAMANDER OFFSHORE WIND FARM 132kV
SANQ1- | SPT | B-2-2b | 132 | SANQUHAR II WIND FARM |  |  | SANQUHAR II WIND FARM 132kV
SANX1Q | SPT | B-2-1b, B-3-1b | 132 | ST ANDREWS CROSS | 51.9219 | -2.5903 | ST ANDREWS CROSS 132kV
SANX1R | SPT | B-2-1b, B-3-1b | 132 | ST ANDREWS CROSS | 51.9219 | -2.5903 | ST ANDREWS CROSS 132kV
SANX3- | SPT | B-3-1b | 33 | ST ANDREWS CROSS | 51.9219 | -2.5903 | ST ANDREWS CROSS 33kV
SASA11 | NGET | B-3-1c | 132 | ST ASAPHS | 53.2516 | -3.4773 | ST ASAPHS 132kV
SCOP1- | SPT | B-2-2b | 132 | SCOOP HILL WIND FARM |  |  | SCOOP HILL WIND FARM 132kV
SCOP1A | SPT | B-2-2b | 132 | SCOOP HILL WIND FARM |  |  | SCOOP HILL WIND FARM 132kV
SEAB11 | NGET | B-3-1c | 132 | SEABANK | 51.5371 | -2.67 | SEABANK 132kV
SEAB41 | NGET | B-2-1c, B-3-1c | 400 | SEABANK | 51.5371 | -2.67 | SEABANK 400kV
SELL11 | NGET | B-3-1c | 132 | SELLINDGE | 51.1065 | 0.9761 | SELLINDGE 132kV
SELL12 | NGET | B-3-1c | 132 | SELLINDGE | 51.1065 | 0.9761 | SELLINDGE 132kV
SELL13 | NGET | B-3-1c | 132 | SELLINDGE | 51.1065 | 0.9761 | SELLINDGE 132kV
SELL4A | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | SELLINDGE | 51.1065 | 0.9761 | SELLINDGE 400kV
SELL4B | NGET | B-2-1c | 400 | SELLINDGE | 51.1065 | 0.9761 | SELLINDGE 400kV
SELL4C | NGET | B-2-1c | 400 | SELLINDGE | 51.1065 | 0.9761 | SELLINDGE 400kV
SELL4D | NGET | B-2-1c | 400 | SELLINDGE | 51.1065 | 0.9761 | SELLINDGE 400kV
SELL4E | NGET | B-2-1c | 400 | SELLINDGE | 51.1065 | 0.9761 | SELLINDGE 400kV
SELL4F | NGET | B-2-1c | 400 | SELLINDGE | 51.1065 | 0.9761 | SELLINDGE 400kV
SFEE1A | SHET | B-2-1a | 132 | ST FERGUS EAST | 57.5754 | -1.8555 | ST FERGUS EAST 132kV
SFEE1B | SHET | B-2-1a | 132 | ST FERGUS EAST | 57.5754 | -1.8555 | ST FERGUS EAST 132kV
SFEE1C | SHET | B-2-1a, B-3-1a | 132 | ST FERGUS EAST | 57.5754 | -1.8555 | ST FERGUS EAST 132kV
SFEE1D | SHET | B-2-1a, B-3-1a | 132 | ST FERGUS EAST | 57.5754 | -1.8555 | ST FERGUS EAST 132kV
SFEE5- | SHET | B-3-1a | 11 | ST FERGUS EAST | 57.5754 | -1.8555 | ST FERGUS EAST 11kV
SFEG1Q | SHET | B-2-1a | 132 | ST FERGUS GAS TERMINAL | 57.5741 | -1.8491 | ST FERGUS GAS TERMINAL 132kV
SFEG1R | SHET | B-2-1a | 132 | ST FERGUS GAS TERMINAL | 57.5741 | -1.8491 | ST FERGUS GAS TERMINAL 132kV
SFEM1Q | SHET | B-2-1a | 132 | ST FERGUS MOBIL | 57.5657 | -1.8805 | ST FERGUS MOBIL 132kV
SFEM1R | SHET | B-2-1a | 132 | ST FERGUS MOBIL | 57.5657 | -1.8805 | ST FERGUS MOBIL 132kV
SFER1J | SHET | B-2-1a | 132 | ST FERGUS | 57.5741 | -1.8491 | ST FERGUS 132kV
SFER1K | SHET | B-2-1a | 132 | ST FERGUS | 57.5741 | -1.8491 | ST FERGUS 132kV
SFER1L | SHET | B-2-1a, B-2-2a | 132 | ST FERGUS | 57.5741 | -1.8491 | ST FERGUS 132kV
SFER1M | SHET | B-2-1a, B-2-2a | 132 | ST FERGUS | 57.5741 | -1.8491 | ST FERGUS 132kV
SFEV1S | SHET | B-2-1a | 132 | ST FERGUS VSD | 57.5657 | -1.8805 | ST FERGUS VSD 132kV
SFEV1T | SHET | B-2-1a | 132 | ST FERGUS VSD | 57.5657 | -1.8805 | ST FERGUS VSD 132kV
SFIL1Q | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | ST FILLANS | 56.3959 | -4.1171 | ST FILLANS 132kV
SFIL5- | SHET | B-3-1a, B-3-2a | 11 | ST FILLANS | 56.3959 | -4.1171 | ST FILLANS 11kV
SGRX2- | SHET | B-2-1a | 275 | SEAGREEN ONE 275KV ONSHORE |  |  | SEAGREEN ONE 275KV ONSHORE 275kV
SGRX2- | SHET | B-2-1a | 275 | SEAGREEN ONE 275KV ONSHORE |  |  | SEAGREEN ONE 275KV ONSHORE 275kV
SHBA41 | NGET | B-2-1c | 400 | SOUTH HUMBER BANK | 53.6014 | -0.14626 | SOUTH HUMBER BANK 400kV
SHEC21 | NGET | B-2-1c, B-3-1c | 275 | SHEFFIELD CITY | 53.3747 | -1.4786 | SHEFFIELD CITY 275kV
SHEC31 | NGET | B-3-1c | 33 | SHEFFIELD CITY | 53.3747 | -1.4786 | SHEFFIELD CITY 33kV
SHEE11 | NGET | B-3-1c | 132 | SHEERNESS | 51.4346 | 0.76713 | SHEERNESS 132kV
SHIN1- | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | SHIN | 57.9436 | -4.4143 | SHIN 132kV
SHIN1A | SHET | B-2-2a | 132 | SHIN | 57.9436 | -4.4143 | SHIN 132kV
SHIN1B | SHET | B-2-2a | 132 | SHIN | 57.9436 | -4.4143 | SHIN 132kV
SHIN3- | SHET | B-3-1a | 33 | SHIN | 57.9436 | -4.4143 | SHIN 33kV
SHIN5- | SHET | B-3-1a | 11 | SHIN | 57.9436 | -4.4143 | SHIN 11kV
SHRE11 | NGET | B-3-1c | 132 | SHREWSBURY | 52.709 | -2.6928 | SHREWSBURY 132kV
SHRE4A | NGET | B-2-1c | 400 | SHREWSBURY | 52.709 | -2.6928 | SHREWSBURY 400kV
SHRE4B | NGET | B-2-1c, B-3-1c | 400 | SHREWSBURY | 52.709 | -2.6928 | SHREWSBURY 400kV
SHRG1T | SPT | B-2-2b | 132 | SHEPHERDS RIG |  |  | SHEPHERDS RIG 132kV
SHRU2Q | SPT | B-2-1b, B-3-1b | 275 | SHRUBHILL | 55.9655 | -3.1856 | SHRUBHILL 275kV
SHRU2R | SPT | B-2-1b, B-3-1b | 275 | SHRUBHILL | 55.9655 | -3.1856 | SHRUBHILL 275kV
SHRU3A | SPT | B-3-1b | 33 | SHRUBHILL | 55.9655 | -3.1856 | SHRUBHILL 33kV
SHRU3B | SPT | B-3-1b | 33 | SHRUBHILL | 55.9655 | -3.1856 | SHRUBHILL 33kV
SHUR41 | NGET | B-2-1c | 400 | SHURTON | 51.2039 | -3.1368 | SHURTON 400kV
SIGH2Q | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | SIGHTHILL | 55.929 | -3.305 | SIGHTHILL 275kV
SIGH2R | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | SIGHTHILL | 55.929 | -3.305 | SIGHTHILL 275kV
SIGH3A | SPT | B-3-1b | 33 | SIGHTHILL | 55.929 | -3.305 | SIGHTHILL 33kV
SING41 | NGET | B-2-1c | 400 | SINGLEWELL | 51.405 | 0.39236 | SINGLEWELL 400kV
SIZE11 | NGET | B-2-1c, B-3-1c | 132 | SIZEWELL | 52.215 | 1.6165 | SIZEWELL 132kV
SIZE12 | NGET | B-3-1c | 132 | SIZEWELL | 52.215 | 1.6165 | SIZEWELL 132kV
SIZE1A | NGET | B-2-1c, B-3-1c | 132 | SIZEWELL | 52.215 | 1.6165 | SIZEWELL 132kV
SIZE1B | NGET | B-2-1c, B-3-1c | 132 | SIZEWELL | 52.215 | 1.6165 | SIZEWELL 132kV
SIZE41 | NGET | B-2-1c, B-3-1c | 400 | SIZEWELL | 52.215 | 1.6165 | SIZEWELL 400kV
SJOW11 | NGET | B-3-1c, B-3-2c, B-4-1c | 132 | ST JOHNS WOOD | 51.5275 | -0.16956 | ST JOHNS WOOD 132kV
SJOW12 | NGET | B-3-1c | 132 | ST JOHNS WOOD | 51.5275 | -0.16956 | ST JOHNS WOOD 132kV
SJOW13 | NGET | B-3-1c, B-3-2c | 132 | ST JOHNS WOOD | 51.5275 | -0.16956 | ST JOHNS WOOD 132kV
SJOW21 | NGET | B-3-1c, B-3-2c, B-4-1c, B-4-2c | 275 | ST JOHNS WOOD | 51.5275 | -0.16956 | ST JOHNS WOOD 275kV
SJOW41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c, B-4-1c | 400 | ST JOHNS WOOD | 51.5275 | -0.16956 | ST JOHNS WOOD 400kV
SKLG11 | NGET | B-3-1c, B-4-1c | 132 | SKELTON GRANGE | 53.7769 | -1.4969 | SKELTON GRANGE 132kV
SKLG21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | SKELTON GRANGE | 53.7769 | -1.4969 | SKELTON GRANGE 275kV
SLCK1- | SHET | B-2-2a | 132 | SLICKLY WIND FARM |  |  | SLICKLY WIND FARM 132kV
SLKB1J | SHET | B-2-1a | 132 | SLACKBUIE |  |  | SLACKBUIE 132kV
SLKB1K | SHET | B-2-1a | 132 | SLACKBUIE |  |  | SLACKBUIE 132kV
SLKB1L | SHET | B-2-1a | 132 | SLACKBUIE |  |  | SLACKBUIE 132kV
SLKB1M | SHET | B-2-1a | 132 | SLACKBUIE |  |  | SLACKBUIE 132kV
SLOY1A | SHET | B-2-1a | 132 | SLOY | 56.2455 | -4.729 | SLOY 132kV
SLOY1B | SHET | B-2-1a | 132 | SLOY | 56.2455 | -4.729 | SLOY 132kV
SLOY1C | SHET | B-2-1a | 132 | SLOY | 56.2455 | -4.729 | SLOY 132kV
SLOY1D | SHET | B-2-1a | 132 | SLOY | 56.2455 | -4.729 | SLOY 132kV
SLOY1E | SHET | B-2-1a | 132 | SLOY | 56.2455 | -4.729 | SLOY 132kV
SLOY1F | SHET | B-2-1a | 132 | SLOY | 56.2455 | -4.729 | SLOY 132kV
SLOY1J | SHET | B-2-1a, B-2-2a | 132 | SLOY | 56.2455 | -4.729 | SLOY 132kV
SLOY1K | SHET | B-2-1a, B-2-2a | 132 | SLOY | 56.2455 | -4.729 | SLOY 132kV
SLOY1L | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | SLOY | 56.2455 | -4.729 | SLOY 132kV
SLOY1M | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | SLOY | 56.2455 | -4.729 | SLOY 132kV
SLOY1N | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | SLOY | 56.2455 | -4.729 | SLOY 132kV
SLOY1P | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | SLOY | 56.2455 | -4.729 | SLOY 132kV
SLOY1T | SHET | B-2-1a | 132 | SLOY | 56.2455 | -4.729 | SLOY 132kV
SLOY5L | SHET | B-3-1a, B-3-2a | 11 | SLOY | 56.2455 | -4.729 | SLOY 11kV
SLOY5M | SHET | B-3-1a, B-3-2a | 11 | SLOY | 56.2455 | -4.729 | SLOY 11kV
SLOY5N | SHET | B-3-1a, B-3-2a | 11 | SLOY | 56.2455 | -4.729 | SLOY 11kV
SLOY5P | SHET | B-3-1a, B-3-2a | 11 | SLOY | 56.2455 | -4.729 | SLOY 11kV
SMAN11 | NGET | B-3-1c | 132 | SOUTH MANCHESTER | 53.4203 | -2.2763 | SOUTH MANCHESTER 132kV
SMAN12 | NGET | B-3-1c | 132 | SOUTH MANCHESTER | 53.4203 | -2.2763 | SOUTH MANCHESTER 132kV
SMAN21 | NGET | B-2-1c, B-3-1c | 275 | SOUTH MANCHESTER | 53.4203 | -2.2763 | SOUTH MANCHESTER 275kV
SMEA1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | SMEATON | 55.9085 | -3.0376 | SMEATON 132kV
SMEA2- | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | SMEATON | 55.9085 | -3.0376 | SMEATON 275kV
SMEA3U | SPT | B-4-1b | 33 | SMEATON | 55.9085 | -3.0376 | SMEATON 33kV
SMEA3V | SPT | B-4-1b | 33 | SMEATON | 55.9085 | -3.0376 | SMEATON 33kV
SMEA4Q | SPT | B-2-1b, B-2-2b | 400 | SMEATON | 55.9085 | -3.0376 | SMEATON 400kV
SMEA4R | SPT | B-2-1b, B-2-2b, B-3-1b | 400 | SMEATON | 55.9085 | -3.0376 | SMEATON 400kV
SNQR3- | SPT | B-2-1b | 33 | SANQUHAR |  |  | SANQUHAR 33kV
SOKY1- | SPT | B-2-1b, B-2-2b | 132 | SOUTH KYLE | 57.281 | -5.7097 | SOUTH KYLE 132kV
SPAV1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | SPANGO VALLEY | 55.9372 | -4.8133 | SPANGO VALLEY 132kV
SPAV1R | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | SPANGO VALLEY | 55.9372 | -4.8133 | SPANGO VALLEY 132kV
SPAV3- | SPT | B-3-1b | 33 | SPANGO VALLEY | 55.9372 | -4.8133 | SPANGO VALLEY 33kV
SPEN11 | NGET | B-3-1c | 132 | SPENNYMOOR | 54.7055 | -1.5548 | SPENNYMOOR 132kV
SPEN41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c, B-4-2c | 400 | SPENNYMOOR | 54.7055 | -1.5548 | SPENNYMOOR 400kV
SPEN42 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | SPENNYMOOR | 54.7055 | -1.5548 | SPENNYMOOR 400kV
SPIT1J | SHET | B-2-1a, B-3-1a | 132 | SPITTAL | 58.4801 | -3.4539 | SPITTAL 132kV
SPIT1K | SHET | B-2-1a, B-3-1a | 132 | SPITTAL | 58.4801 | -3.4539 | SPITTAL 132kV
SPIT1M | SHET | B-2-1a, B-3-1a | 132 | SPITTAL | 58.4801 | -3.4539 | SPITTAL 132kV
SPIT2J | SHET | B-2-1a, B-3-1a, B-3-2a | 275 | SPITTAL | 58.4801 | -3.4539 | SPITTAL 275kV
SPIT2K | SHET | B-2-1a, B-3-1a, B-3-2a | 275 | SPITTAL | 58.4801 | -3.4539 | SPITTAL 275kV
SPIT2R | SHET | B-2-1a | 275 | SPITTAL | 58.4801 | -3.4539 | SPITTAL 275kV
SPLN41 | NGET | B-2-1c | 400 | SPALDING NORTH | 52.8058 | -0.13332 | SPALDING NORTH 400kV
SPRB1- | SPT | B-2-2b, B-3-2b | 132 | SPIREBUSH |  |  | SPIREBUSH 132kV
SPRB3- | SPT | B-3-2b | 33 | SPIREBUSH |  |  | SPIREBUSH 33kV
SSHI22 | NGET | B-2-1c, B-3-1c | 275 | SOUTH SHIELDS | 54.9734 | -1.4495 | SOUTH SHIELDS 275kV
SSHI31 | NGET | B-3-1c | 33 | SOUTH SHIELDS | 54.9734 | -1.4495 | SOUTH SHIELDS 33kV
STAH11 | NGET | B-3-1c | 132 | STANAH | 53.8788 | -2.9878 | STANAH 132kV
STAH4A | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | STANAH | 53.8788 | -2.9878 | STANAH 400kV
STAH4B | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | STANAH | 53.8788 | -2.9878 | STANAH 400kV
STAL11 | NGET | B-3-1c | 132 | STALYBRIDGE | 53.4937 | -2.0413 | STALYBRIDGE 132kV
STAL21 | NGET | B-2-1c, B-3-1c | 275 | STALYBRIDGE | 53.4937 | -2.0413 | STALYBRIDGE 275kV
STAL41 | NGET | B-4-1c | 400 | STALYBRIDGE | 53.4937 | -2.0413 | STALYBRIDGE 400kV
STAL4A | NGET | B-2-1c, B-3-1c | 400 | STALYBRIDGE | 53.4937 | -2.0413 | STALYBRIDGE 400kV
STAL4B | NGET | B-2-1c | 400 | STALYBRIDGE | 53.4937 | -2.0413 | STALYBRIDGE 400kV
STAY41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | STAYTHORPE | 53.0775 | -0.86898 | STAYTHORPE 400kV
STAY4A | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | STAYTHORPE | 53.0775 | -0.86898 | STAYTHORPE 400kV
STCS1A | SHET | B-2-2a | 132 | STRATHY COLLECTOR STATION | 58.2775 | -6.3083 | STRATHY COLLECTOR STATION 132kV
STCS1B | SHET | B-2-2a | 132 | STRATHY COLLECTOR STATION | 58.2775 | -6.3083 | STRATHY COLLECTOR STATION 132kV
STEN11 | NGET | B-2-1c, B-3-1c | 132 | STELLA NORTH | 54.9781 | -1.7245 | STELLA NORTH 132kV
STES11 | NGET | B-2-1c, B-3-1c | 132 | STELLA SOUTH | 54.9744 | -1.7325 | STELLA SOUTH 132kV
STEW21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | STELLA WEST | 54.9777 | -1.7422 | STELLA WEST 275kV
STEW41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | STELLA WEST | 54.9777 | -1.7422 | STELLA WEST 400kV
STHA2A | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | STRATHAVEN | 55.7522 | -4.0818 | STRATHAVEN 275kV
STHA2B | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | STRATHAVEN | 55.7522 | -4.0818 | STRATHAVEN 275kV
STHA3- | SPT | B-3-1b | 33 | STRATHAVEN | 55.7522 | -4.0818 | STRATHAVEN 33kV
STHA3V | SPT | B-4-1b | 33 | STRATHAVEN | 55.7522 | -4.0818 | STRATHAVEN 33kV
STHA4A | SPT | B-2-1b, B-2-2b, B-3-1b | 400 | STRATHAVEN | 55.7522 | -4.0818 | STRATHAVEN 400kV
STHA4B | SPT | B-2-1b, B-2-2b, B-3-1b | 400 | STRATHAVEN | 55.7522 | -4.0818 | STRATHAVEN 400kV
STIR1S | SPT | B-2-1b, B-3-1b | 132 | STIRLING | 56.1169 | -3.92 | STIRLING 132kV
STIR1T | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | STIRLING | 56.1169 | -3.92 | STIRLING 132kV
STIR3- | SPT | B-3-1b | 33 | STIRLING | 56.1169 | -3.92 | STIRLING 33kV
STLE1Q | SPT | B-2-1b, B-3-1b | 132 | STRATHLEVEN | 55.9617 | -4.5628 | STRATHLEVEN 132kV
STLE1R | SPT | B-2-1b, B-3-1b | 132 | STRATHLEVEN | 55.9617 | -4.5628 | STRATHLEVEN 132kV
STLE3S | SPT | B-3-1b | 33 | STRATHLEVEN | 55.9617 | -4.5628 | STRATHLEVEN 33kV
STNG1A | SHET | B-2-2a | 132 | STANNERGATE |  |  | STANNERGATE 132kV
STNG1B | SHET | B-2-2a | 132 | STANNERGATE |  |  | STANNERGATE 132kV
STNG1C | SHET | B-2-2a | 132 | STANNERGATE |  |  | STANNERGATE 132kV
STNG1D | SHET | B-2-2a | 132 | STANNERGATE |  |  | STANNERGATE 132kV
STNG1E | SHET | B-2-2a, B-3-2a | 132 | STANNERGATE |  |  | STANNERGATE 132kV
STNG3- | SHET | B-3-2a | 33 | STANNERGATE |  |  | STANNERGATE 33kV
STOB11 | NGET | B-3-1c | 132 | STOKE BARDOLPH | 52.9598 | -1.0506 | STOKE BARDOLPH 132kV
STOB41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | STOKE BARDOLPH | 52.9598 | -1.0506 | STOKE BARDOLPH 400kV
STOC1- | SPT | B-2-2b, B-3-2b | 132 | STRANOCH WIND FARM |  |  | STRANOCH WIND FARM 132kV
STOC3- | SPT | B-3-2b | 33 | STRANOCH WIND FARM |  |  | STRANOCH WIND FARM 33kV
STOR1- | SHET | B-2-2a, B-3-2a | 132 | STORNOWAY | 58.2033 | -6.3737 | STORNOWAY 132kV
STOR3- | SHET | B-3-2a | 33 | STORNOWAY | 58.2033 | -6.3737 | STORNOWAY 33kV
STRB2- | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | STRATH BRORA WIND | 58.0202 | -3.8755 | STRATH BRORA WIND 275kV
STRB3W | SHET | B-3-1a | 33 | STRATH BRORA WIND | 58.0202 | -3.8755 | STRATH BRORA WIND 33kV
STRI1Q | SHET | B-2-1a, B-3-1a | 132 | STRICHEN | 57.5864 | -2.0694 | STRICHEN 132kV
STRI1R | SHET | B-2-1a, B-3-1a | 132 | STRICHEN | 57.5864 | -2.0694 | STRICHEN 132kV
STRI3- | SHET | B-3-1a | 33 | STRICHEN | 57.5864 | -2.0694 | STRICHEN 33kV
STRL1- | SHET | B-2-1a, B-3-1a | 132 | STRONELAIRG WIND FARM (SSE) | 57.0947 | -4.4339 | STRONELAIRG WIND FARM (SSE) 132kV
STRL3P | SHET | B-3-1a | 33 | STRONELAIRG WIND FARM (SSE) | 57.0947 | -4.4339 | STRONELAIRG WIND FARM (SSE) 33kV
STRL3Q | SHET | B-3-1a | 33 | STRONELAIRG WIND FARM (SSE) | 57.0947 | -4.4339 | STRONELAIRG WIND FARM (SSE) 33kV
STRL3R | SHET | B-3-1a | 33 | STRONELAIRG WIND FARM (SSE) | 57.0947 | -4.4339 | STRONELAIRG WIND FARM (SSE) 33kV
STRW1- | SHET | B-2-1a, B-3-1a | 132 | STRATHY WIND |  |  | STRATHY WIND 132kV
STRW1A | SHET | B-2-1a, B-2-2a | 132 | STRATHY WIND |  |  | STRATHY WIND 132kV
STRW3- | SHET | B-3-1a | 33 | STRATHY WIND |  |  | STRATHY WIND 33kV
STSB41 | NGET | B-4-1c | 400 | STOCKSBRIDGE | 53.4877 | -1.602 | STOCKSBRIDGE 400kV
STSB4A | NGET | B-2-1c, B-3-1c | 400 | STOCKSBRIDGE | 53.4877 | -1.602 | STOCKSBRIDGE 400kV
STSB4B | NGET | B-2-1c, B-3-1c | 400 | STOCKSBRIDGE | 53.4877 | -1.602 | STOCKSBRIDGE 400kV
STSO1A | SHET | B-2-2a | 132 | STRATHY SOUTH |  |  | STRATHY SOUTH 132kV
STSO1B | SHET | B-2-2a, B-3-2a | 132 | STRATHY SOUTH |  |  | STRATHY SOUTH 132kV
STSO3A | SHET | B-3-2a | 33 | STRATHY SOUTH |  |  | STRATHY SOUTH 33kV
STSO3B | SHET | B-3-2a | 33 | STRATHY SOUTH |  |  | STRATHY SOUTH 33kV
STWB4Q | NGET, SPT | B-2-1b, B-2-1c | 400 | STELLA WEST BORDER NODE | 55.6524 | -2.2476 | STELLA WEST BORDER NODE 400kV
STWB4Q | NGET, SPT | B-2-1b, B-2-1c | 400 | STELLA WEST BORDER 400KV | 55.6524 | -2.2476 | STELLA WEST BORDER 400KV 400kV
STWB4R | NGET, SPT | B-2-1b, B-2-1c | 400 | STELLA WEST BORDER NODE | 55.6524 | -2.2476 | STELLA WEST BORDER NODE 400kV
STWB4R | NGET, SPT | B-2-1b, B-2-1c | 400 | STELLA WEST BORDER 400KV | 55.6524 | -2.2476 | STELLA WEST BORDER 400KV 400kV
STWO1- | SHET | B-2-2a, B-3-2a | 132 | STRATHY WOOD |  |  | STRATHY WOOD 132kV
STWO3- | SHET | B-3-2a | 33 | STRATHY WOOD |  |  | STRATHY WOOD 33kV
STYC11 | NGET | B-3-1c | 132 | STAYTHORPE C | 53.0775 | -0.86898 | STAYTHORPE C 132kV
STYC12 | NGET | B-3-1c | 132 | STAYTHORPE C | 53.0775 | -0.86898 | STAYTHORPE C 132kV
SUND11 | NGET | B-3-1c | 132 | SUNDON | 51.9363 | -0.50301 | SUNDON 132kV
SUND31 | NGET | B-3-1c | 33 | SUNDON | 51.9363 | -0.50301 | SUNDON 33kV
SUND41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | SUNDON | 51.9363 | -0.50301 | SUNDON 400kV
SUND42 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | SUNDON | 51.9363 | -0.50301 | SUNDON 400kV
SWAN11 | NGET | B-3-1c | 132 | SWANSEA NORTH | 51.6894 | -3.9568 | SWANSEA NORTH 132kV
SWAN12 | NGET | B-3-1c | 132 | SWANSEA NORTH | 51.6894 | -3.9568 | SWANSEA NORTH 132kV
SWAN21 | NGET | B-2-1c, B-3-1c | 275 | SWANSEA NORTH | 51.6894 | -3.9568 | SWANSEA NORTH 275kV
SWAN22 | NGET | B-3-1c | 275 | SWANSEA NORTH | 51.6894 | -3.9568 | SWANSEA NORTH 275kV
SWAN41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | SWANSEA NORTH | 51.6894 | -3.9568 | SWANSEA NORTH 400kV
SWAN42 | NGET | B-2-1c | 400 | SWANSEA NORTH | 51.6894 | -3.9568 | SWANSEA NORTH 400kV
SWAN4A | NGET | B-2-1c, B-3-1c | 400 | SWANSEA NORTH | 51.6894 | -3.9568 | SWANSEA NORTH 400kV
SWAN4B | NGET | B-2-1c, B-3-1c | 400 | SWANSEA NORTH | 51.6894 | -3.9568 | SWANSEA NORTH 400kV
SYEL1- | SHET | B-2-2a | 132 | SOUTH YELL |  |  | SOUTH YELL 132kV
SYEL1A | SHET | B-2-2a | 132 | SOUTH YELL |  |  | SOUTH YELL 132kV
SYEL1B | SHET | B-2-2a | 132 | SOUTH YELL |  |  | SOUTH YELL 132kV
SYEL1M | SHET | B-2-2a | 132 | SOUTH YELL |  |  | SOUTH YELL 132kV
SYEL1N | SHET | B-2-2a | 132 | SOUTH YELL |  |  | SOUTH YELL 132kV
TADT2A | NGET | B-2-2c | 275 | TADCASTER TEE | 53.881 | -1.2655 | TADCASTER TEE 275kV
TADT2B | NGET | B-2-2c | 275 | TADCASTER TEE | 53.881 | -1.2655 | TADCASTER TEE 275kV
TARL1Q | SHET | B-2-1a, B-3-1a | 132 | TARLAND | 57.1522 | -2.7877 | TARLAND 132kV
TARL1R | SHET | B-2-1a, B-3-1a | 132 | TARLAND | 57.1522 | -2.7877 | TARLAND 132kV
TARL3- | SHET | B-3-1a | 33 | TARLAND | 57.1522 | -2.7877 | TARLAND 33kV
TAUN11 | NGET | B-3-1c | 132 | TAUNTON | 51.017 | -3.1551 | TAUNTON 132kV
TAUN41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | TAUNTON | 51.017 | -3.1551 | TAUNTON 400kV
TAUN42 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-2c | 400 | TAUNTON | 51.017 | -3.1551 | TAUNTON 400kV
TAYN1Q | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | TAYNUILT | 56.4302 | -5.2145 | TAYNUILT 132kV
TAYN1R | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | TAYNUILT | 56.4302 | -5.2145 | TAYNUILT 132kV
TAYN3- | SHET | B-3-1a | 33 | TAYNUILT | 56.4302 | -5.2145 | TAYNUILT 33kV
TEAL1- | SHET | B-2-1a, B-3-1a, B-4-1a | 132 | TEALING | 51.5019 | -0.29717 | TEALING 132kV
TEAL2A | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | TEALING | 51.5019 | -0.29717 | TEALING 275kV
TEAL2B | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | TEALING | 51.5019 | -0.29717 | TEALING 275kV
TEAL2J | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a, B-4-1a | 275 | TEALING | 51.5019 | -0.29717 | TEALING 275kV
TEAL2K | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 275 | TEALING | 51.5019 | -0.29717 | TEALING 275kV
TEAL3W | SHET | B-4-1a | 33 | TEALING | 51.5019 | -0.29717 | TEALING 33kV
TEAL3Y | SHET | B-4-1a | 33 | TEALING | 51.5019 | -0.29717 | TEALING 33kV
TELR1Q | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | TELFORD ROAD | 55.9618 | -3.2431 | TELFORD ROAD 132kV
TELR1R | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | TELFORD ROAD | 55.9618 | -3.2431 | TELFORD ROAD 132kV
TELR3- | SPT | B-3-1b | 33 | TELFORD ROAD | 55.9618 | -3.2431 | TELFORD ROAD 33kV
TEMP21 | NGET | B-2-1c, B-3-1c | 275 | TEMPLEBOROUGH | 53.4121 | -1.3858 | TEMPLEBOROUGH 275kV
TEMP22 | NGET | B-2-1c, B-2-2c, B-3-1c | 275 | TEMPLEBOROUGH | 53.4121 | -1.3858 | TEMPLEBOROUGH 275kV
TEMP31 | NGET | B-3-1c | 33 | TEMPLEBOROUGH | 53.4121 | -1.3858 | TEMPLEBOROUGH 33kV
THOM21 | NGET | B-2-1c, B-3-1c | 275 | THORPE MARSH | 53.5756 | -1.0891 | THORPE MARSH 275kV
THOM2A | NGET | B-2-1c, B-3-1c | 275 | THORPE MARSH | 53.5756 | -1.0891 | THORPE MARSH 275kV
THOM41 | NGET | B-2-1c, B-3-1c | 400 | THORPE MARSH | 53.5756 | -1.0891 | THORPE MARSH 400kV
THOM42 | NGET | B-2-1c, B-3-1c, B-4-1c | 400 | THORPE MARSH | 53.5756 | -1.0891 | THORPE MARSH 400kV
THOM61 | NGET | B-3-1c | 66 | THORPE MARSH | 53.5756 | -1.0891 | THORPE MARSH 66kV
THTO41 | NGET | B-2-1c, B-2-2c | 400 | THORNTON | 53.9003 | -0.82212 | THORNTON 400kV
THTO42 | NGET | B-2-1c, B-2-2c | 400 | THORNTON | 53.9003 | -0.82212 | THORNTON 400kV
THTO43 | NGET | B-2-1c, B-2-2c | 400 | THORNTON | 53.9003 | -0.82212 | THORNTON 400kV
THUR21 | NGET | B-2-1c, B-3-1c | 275 | THURCROFT | 53.4049 | -1.2685 | THURCROFT 275kV
THUR2A | NGET | B-2-1c, B-2-2c | 275 | THURCROFT | 53.4049 | -1.2685 | THURCROFT 275kV
THUR61 | NGET | B-3-1c | 66 | THURCROFT | 53.4049 | -1.2685 | THURCROFT 66kV
THUS1J | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | THURSO SOUTH | 58.5637 | -3.5102 | THURSO SOUTH 132kV
THUS1K | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | THURSO SOUTH | 58.5637 | -3.5102 | THURSO SOUTH 132kV
THUS1L | SHET | B-2-2a | 132 | THURSO SOUTH | 58.5637 | -3.5102 | THURSO SOUTH 132kV
THUS1M | SHET | B-2-2a | 132 | THURSO SOUTH | 58.5637 | -3.5102 | THURSO SOUTH 132kV
THUS2J | SHET | B-2-1a, B-2-2a, B-3-1a | 275 | THURSO SOUTH | 58.5637 | -3.5102 | THURSO SOUTH 275kV
THUS2K | SHET | B-2-1a, B-3-1a | 275 | THURSO SOUTH | 58.5637 | -3.5102 | THURSO SOUTH 275kV
THUS3- | SHET | B-3-1a | 33 | THURSO SOUTH | 58.5637 | -3.5102 | THURSO SOUTH 33kV
TILB11 | NGET | B-3-1c | 132 | TILBURY | 51.4603 | 0.39372 | TILBURY 132kV
TILB12 | NGET | B-3-1c | 132 | TILBURY | 51.4603 | 0.39372 | TILBURY 132kV
TILB13 | NGET | B-3-1c | 132 | TILBURY | 51.4603 | 0.39372 | TILBURY 132kV
TILB14 | NGET | B-3-1c | 132 | TILBURY | 51.4603 | 0.39372 | TILBURY 132kV
TILB21 | NGET | B-2-1c, B-3-1c | 275 | TILBURY | 51.4603 | 0.39372 | TILBURY 275kV
TILB41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | TILBURY | 51.4603 | 0.39372 | TILBURY 400kV
TILB4A | NGET | B-2-1c, B-3-1c | 400 | TILBURY | 51.4603 | 0.39372 | TILBURY 400kV
TILB4B | NGET | B-2-1c, B-3-1c | 400 | TILBURY | 51.4603 | 0.39372 | TILBURY 400kV
TINP21 | NGET | B-2-1c, B-3-1c | 275 | TINSLEY PARK | 53.4011 | -1.3946 | TINSLEY PARK 275kV
TINP22 | NGET | B-2-1c, B-3-1c | 275 | TINSLEY PARK | 53.4011 | -1.3946 | TINSLEY PARK 275kV
TINP31 | NGET | B-3-1c | 33 | TINSLEY PARK | 53.4011 | -1.3946 | TINSLEY PARK 33kV
TINP32 | NGET | B-3-1c | 33 | TINSLEY PARK | 53.4011 | -1.3946 | TINSLEY PARK 33kV
TLSK4- | SHET | B-2-2a | 400 | TALISK OFFSHORE WIND FARM |  |  | TALISK OFFSHORE WIND FARM 400kV
TNGF1- | SHET | B-2-2a | 132 | TANGY IV |  |  | TANGY IV 132kV
TNGF1A | SHET | B-2-2a, B-3-2a | 132 | TANGY IV |  |  | TANGY IV 132kV
TNGF3- | SHET | B-3-2a | 33 | TANGY IV |  |  | TANGY IV 33kV
TODD3- | SPT | B-2-1b | 33 | TODDLEBURN |  |  | TODDLEBURN 33kV
TODP21 | NGET | B-2-1c, B-3-1c | 275 | TOD POINT | 54.6065 | -1.1167 | TOD POINT 275kV
TODP61 | NGET | B-3-1c | 66 | TOD POINT | 54.6065 | -1.1167 | TOD POINT 66kV
TOMT1J | SHET | B-2-1a, B-3-1a | 132 | TOMATIN | 57.3014 | -4.0681 | TOMATIN 132kV
TOMT1K | SHET | B-2-1a, B-3-1a | 132 | TOMATIN | 57.3014 | -4.0681 | TOMATIN 132kV
TOMT1L | SHET | B-2-1a | 132 | TOMATIN | 57.3014 | -4.0681 | TOMATIN 132kV
TOMT1M | SHET | B-2-1a | 132 | TOMATIN | 57.3014 | -4.0681 | TOMATIN 132kV
TOMT2J | SHET | B-2-1a, B-3-1a | 275 | TOMATIN | 57.3014 | -4.0681 | TOMATIN 275kV
TOMT2K | SHET | B-2-1a, B-3-1a | 275 | TOMATIN | 57.3014 | -4.0681 | TOMATIN 275kV
TONG1- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 132 | TONGLAND | 54.8616 | -4.0344 | TONGLAND 132kV
TONG1Q | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 132 | TONGLAND | 54.8616 | -4.0344 | TONGLAND 132kV
TONG1R | SPT | B-3-1b, B-3-2b | 132 | TONGLAND | 54.8616 | -4.0344 | TONGLAND 132kV
TONG3- | SPT | B-3-1b | 33 | TONGLAND | 54.8616 | -4.0344 | TONGLAND 33kV
TONG5- | SPT | B-3-1b | 11 | TONGLAND | 54.8616 | -4.0344 | TONGLAND 11kV
TORN1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | TORNESS | 55.9663 | -2.411 | TORNESS 132kV
TORN4- | SPT | B-2-1b, B-2-2b, B-3-1b, B-4-1b | 400 | TORNESS | 55.9663 | -2.411 | TORNESS 400kV
TOTT11 | NGET | B-3-1c | 132 | TOTTENHAM | 51.6045 | -0.047649 | TOTTENHAM 132kV
TOTT12 | NGET | B-3-1c | 132 | TOTTENHAM | 51.6045 | -0.047649 | TOTTENHAM 132kV
TOTT21 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 275 | TOTTENHAM | 51.6045 | -0.047649 | TOTTENHAM 275kV
TOTT22 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 275 | TOTTENHAM | 51.6045 | -0.047649 | TOTTENHAM 275kV
TOTT23 | NGET | B-2-1c, B-3-1c | 275 | TOTTENHAM | 51.6045 | -0.047649 | TOTTENHAM 275kV
TOTT24 | NGET | B-2-1c, B-3-1c | 275 | TOTTENHAM | 51.6045 | -0.047649 | TOTTENHAM 275kV
TOTT2A | NGET | B-2-1c | 275 | TOTTENHAM | 51.6045 | -0.047649 | TOTTENHAM 275kV
TOTT2B | NGET | B-2-1c | 275 | TOTTENHAM | 51.6045 | -0.047649 | TOTTENHAM 275kV
TRAW11 | NGET | B-3-1c | 132 | TRAWSFYNYDD | 52.9264 | -3.9455 | TRAWSFYNYDD 132kV
TRAW21 | NGET | B-2-1c, B-3-1c | 275 | TRAWSFYNYDD | 52.9264 | -3.9455 | TRAWSFYNYDD 275kV
TRAW41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | TRAWSFYNYDD | 52.9264 | -3.9455 | TRAWSFYNYDD 400kV
TREM21 | NGET | B-2-1c, B-3-1c | 275 | TREMORFA | 51.4817 | -3.1307 | TREMORFA 275kV
TREM31 | NGET | B-3-1c | 33 | TREMORFA | 51.4817 | -3.1307 | TREMORFA 33kV
TREU4A | NGET | B-2-1c, B-2-2c | 400 | TREUDDYN | 53.111 | -3.1206 | TREUDDYN 400kV
TREU4B | NGET | B-2-1c, B-2-2c | 400 | TREUDDYN | 53.111 | -3.1206 | TREUDDYN 400kV
TRLO3- | SPT | B-2-1b, B-2-2b | 33 | TRALORG | 55.2345 | -4.789 | TRALORG 33kV
TRSN1- | SPT | B-2-2b, B-3-2b | 132 | TROSTON |  |  | TROSTON 132kV
TRSN3- | SPT | B-3-2b | 33 | TROSTON |  |  | TROSTON 33kV
TUMB1Q | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | TUMMEL BRIDGE | 56.7068 | -4.0295 | TUMMEL BRIDGE 132kV
TUMB1R | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | TUMMEL BRIDGE | 56.7068 | -4.0295 | TUMMEL BRIDGE 132kV
TUMB5- | SHET | B-3-1a, B-3-2a | 11 | TUMMEL BRIDGE | 56.7068 | -4.0295 | TUMMEL BRIDGE 11kV
TUMM1J | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | TUMMEL | 56.7068 | -4.0295 | TUMMEL 132kV
TUMM1K | SHET | B-2-1a, B-3-1a, B-3-2a | 132 | TUMMEL | 56.7068 | -4.0295 | TUMMEL 132kV
TUMM2J | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 275 | TUMMEL | 56.7068 | -4.0295 | TUMMEL 275kV
TUMM2K | SHET | B-2-1a, B-2-2a, B-3-1a, B-3-2a | 275 | TUMMEL | 56.7068 | -4.0295 | TUMMEL 275kV
TUMM4- | SHET | B-2-1a | 400 | TUMMEL | 56.7068 | -4.0295 | TUMMEL 400kV
TWIN11 | NGET | B-3-2c | 132 | TWINSTEAD | 52.0018 | 0.68625 | TWINSTEAD 132kV
TWIN4A | NGET | B-2-2c, B-3-2c | 400 | TWINSTEAD | 52.0018 | 0.68625 | TWINSTEAD 400kV
TWIN4B | NGET | B-2-2c, B-3-2c | 400 | TWINSTEAD | 52.0018 | 0.68625 | TWINSTEAD 400kV
TYNE11 | NGET | B-3-1c | 132 | TYNEMOUTH | 55.0237 | -1.5006 | TYNEMOUTH 132kV
TYNE21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | TYNEMOUTH | 55.0237 | -1.5006 | TYNEMOUTH 275kV
TYNE2A | NGET | B-2-1c, B-3-1c | 275 | TYNEMOUTH | 55.0237 | -1.5006 | TYNEMOUTH 275kV
TYNE51 | NGET | B-3-1c | 11 | TYNEMOUTH | 55.0237 | -1.5006 | TYNEMOUTH 11kV
TYNE51 | NGET | B-3-1c | 11 | TYNEMOUTH | 55.0237 | -1.5006 | TYNEMOUTH 11kV
UPPB11 | NGET | B-3-1c | 132 | UPPER BOAT | 51.5741 | -3.3004 | UPPER BOAT 132kV
UPPB21 | NGET | B-2-1c, B-3-1c | 275 | UPPER BOAT | 51.5741 | -3.3004 | UPPER BOAT 275kV
UPPB22 | NGET | B-2-1c, B-3-1c | 275 | UPPER BOAT | 51.5741 | -3.3004 | UPPER BOAT 275kV
UPPB31 | NGET | B-3-1c | 33 | UPPER BOAT | 51.5741 | -3.3004 | UPPER BOAT 33kV
USKM11 | NGET | B-3-1c | 132 | USKMOUTH | 51.5471 | -2.9786 | USKMOUTH 132kV
USKM12 | NGET | B-3-1c, B-4-1c | 132 | USKMOUTH | 51.5471 | -2.9786 | USKMOUTH 132kV
USKM21 | NGET | B-2-1c, B-3-1c | 275 | USKMOUTH | 51.5471 | -2.9786 | USKMOUTH 275kV
USKM2A | NGET | B-2-1c | 275 | USKMOUTH | 51.5471 | -2.9786 | USKMOUTH 275kV
USKM2B | NGET | B-2-1c | 275 | USKMOUTH | 51.5471 | -2.9786 | USKMOUTH 275kV
WALE41 | NGET | B-2-2c | 400 | GRAIN WEST |  |  | GRAIN WEST 400kV
WALH41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | WALHAM | 51.8792 | -2.2539 | WALHAM 400kV
WALP11 | NGET | B-3-1c, B-4-1c | 132 | WALPOLE | 52.7266 | 0.19804 | WALPOLE 132kV
WALP41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | WALPOLE | 52.7266 | 0.19804 | WALPOLE 400kV
WALX21 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 275 | WALTHAM CROSS | 51.7148 | -0.011174 | WALTHAM CROSS 275kV
WALX22 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 275 | WALTHAM CROSS | 51.7148 | -0.011174 | WALTHAM CROSS 275kV
WALX2A | NGET | B-3-2c | 275 | WALTHAM CROSS | 51.7148 | -0.011174 | WALTHAM CROSS 275kV
WALX41 | NGET | B-2-2c, B-3-2c | 400 | WALTHAM CROSS | 51.7148 | -0.011174 | WALTHAM CROSS 400kV
WALX4A | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 400 | WALTHAM CROSS | 51.7148 | -0.011174 | WALTHAM CROSS 400kV
WALX4B | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c | 400 | WALTHAM CROSS | 51.7148 | -0.011174 | WALTHAM CROSS 400kV
WARL11 | NGET | B-3-1c, B-4-1c | 132 | WARLEY | 51.5528 | 0.30137 | WARLEY 132kV
WARL21 | NGET | B-2-1c, B-3-1c | 275 | WARLEY | 51.5528 | 0.30137 | WARLEY 275kV
WASF1A | NGET | B-3-1c | 132 | WASHWAY FARM | 53.5626 | -2.8196 | WASHWAY FARM 132kV
WASF1B | NGET | B-3-1c | 132 | WASHWAY FARM | 53.5626 | -2.8196 | WASHWAY FARM 132kV
WASF2A | NGET | B-2-1c, B-3-1c | 275 | WASHWAY FARM | 53.5626 | -2.8196 | WASHWAY FARM 275kV
WASF2B | NGET | B-2-1c, B-3-1c | 275 | WASHWAY FARM | 53.5626 | -2.8196 | WASHWAY FARM 275kV
WATS11 | NGET | B-3-1c | 132 | WATFORD SOUTH | 51.643 | -0.40411 | WATFORD SOUTH 132kV
WATS12 | NGET | B-3-1c | 132 | WATFORD SOUTH | 51.643 | -0.40411 | WATFORD SOUTH 132kV
WATS21 | NGET | B-2-1c, B-3-1c | 275 | WATFORD SOUTH | 51.643 | -0.40411 | WATFORD SOUTH 275kV
WATS22 | NGET | B-2-1c, B-3-1c | 275 | WATFORD SOUTH | 51.643 | -0.40411 | WATFORD SOUTH 275kV
WBOL21 | NGET | B-2-1c, B-3-1c | 275 | WEST BOLDON | 54.9401 | -1.4704 | WEST BOLDON 275kV
WBOL61 | NGET | B-3-1c | 66 | WEST BOLDON | 54.9401 | -1.4704 | WEST BOLDON 66kV
WBUR11 | NGET | B-3-1c | 132 | WEST BURTON | 53.3592 | -0.80943 | WEST BURTON 132kV
WBUR12 | NGET | B-3-1c | 132 | WEST BURTON | 53.3592 | -0.80943 | WEST BURTON 132kV
WBUR41 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | WEST BURTON | 53.3592 | -0.80943 | WEST BURTON 400kV
WBUR42 | NGET | B-2-1c, B-2-2c, B-3-1c | 400 | WEST BURTON | 53.3592 | -0.80943 | WEST BURTON 400kV
WEAV71 | NGET | B-3-1c | 25 | WEAVER JUNCTION | 53.2417 | -2.5539 | WEAVER JUNCTION 25kV
WESE1- | SPT | B-2-1b, B-3-1b | 132 | WESTERDOD |  |  | WESTERDOD 132kV
WFIB2- | SHET, SPT | B-2-1a, B-2-1b, B-2-2b | 275 | WESTFIELD BOUNDARY | 56.1636 | -3.3026 | WESTFIELD BOUNDARY 275kV
WFIB2- | SHET, SPT | B-2-1a, B-2-1b, B-2-2b | 275 | WESTFIELD BOUNDARY | 56.1636 | -3.3026 | WESTFIELD BOUNDARY 275kV
WFIB4- | SHET, SPT | B-2-2a, B-2-2b | 400 | WESTFIELD BOUNDARY | 56.1636 | -3.3026 | WESTFIELD BOUNDARY 400kV
WFIB4- | SHET, SPT | B-2-2a, B-2-2b | 400 | WESTFIELD BOUNDARY | 56.1636 | -3.3026 | WESTFIELD BOUNDARY 400kV
WFIE1A | SPT | B-2-1b, B-3-1b | 132 | WESTFIELD | 56.1636 | -3.3026 | WESTFIELD 132kV
WFIE1B | SPT | B-2-1b, B-3-1b | 132 | WESTFIELD | 56.1636 | -3.3026 | WESTFIELD 132kV
WFIE2- | SPT | B-2-1b, B-2-2b, B-3-1b | 275 | WESTFIELD | 56.1636 | -3.3026 | WESTFIELD 275kV
WFIE3- | SPT | B-3-1b | 33 | WESTFIELD | 56.1636 | -3.3026 | WESTFIELD 33kV
WFIE4- | SPT | B-2-2b | 400 | WESTFIELD | 56.1636 | -3.3026 | WESTFIELD 400kV
WFIE4A | SPT | B-2-2b | 400 | WESTFIELD | 56.1636 | -3.3026 | WESTFIELD 400kV
WGEO2Q | SPT | B-2-1b, B-3-1b | 275 | WEST GEORGE STREET | 55.8631 | -4.2665 | WEST GEORGE STREET 275kV
WGEO2R | SPT | B-2-1b, B-3-1b, B-3-2b | 275 | WEST GEORGE STREET | 55.8631 | -4.2665 | WEST GEORGE STREET 275kV
WGEO3- | SPT | B-3-1b, B-3-2b | 33 | WEST GEORGE STREET | 55.8631 | -4.2665 | WEST GEORGE STREET 33kV
WHAM11 | NGET | B-3-1c | 132 | WEST HAM | 51.5196 | 0.0007427 | WEST HAM 132kV
WHAM12 | NGET | B-3-1c | 132 | WEST HAM | 51.5196 | 0.0007427 | WEST HAM 132kV
WHAM41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | WEST HAM | 51.5196 | 0.0007427 | WEST HAM 400kV
WHAM4A | NGET | B-2-1c, B-3-1c | 400 | WEST HAM | 51.5196 | 0.0007427 | WEST HAM 400kV
WHAM4B | NGET | B-2-1c, B-3-1c | 400 | WEST HAM | 51.5196 | 0.0007427 | WEST HAM 400kV
WHBR3A | SPT | B-2-2b | 33 | WHITELAW BRAE | 60.4016 | -1.3479 | WHITELAW BRAE 33kV
WHBR3B | SPT | B-2-2b | 33 | WHITELAW BRAE | 60.4016 | -1.3479 | WHITELAW BRAE 33kV
WHGA11 | NGET | B-3-1c | 132 | WHITEGATE | 53.5288 | -2.1672 | WHITEGATE 132kV
WHGA21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | WHITEGATE | 53.5288 | -2.1672 | WHITEGATE 275kV
WHHO2Q | SPT | B-2-1b, B-3-1b | 275 | WHITEHOUSE | 55.9311 | -3.2014 | WHITEHOUSE 275kV
WHHO2R | SPT | B-2-1b, B-3-1b | 275 | WHITEHOUSE | 55.9311 | -3.2014 | WHITEHOUSE 275kV
WHHO3- | SPT | B-3-1b | 33 | WHITEHOUSE | 55.9311 | -3.2014 | WHITEHOUSE 33kV
WHIB1A | SHET | B-2-1a | 132 | WHITE BRIDGE |  |  | WHITE BRIDGE 132kV
WHIB1B | SHET | B-2-1a | 132 | WHITE BRIDGE |  |  | WHITE BRIDGE 132kV
WHIB1C | SHET | B-2-1a | 132 | WHITE BRIDGE |  |  | WHITE BRIDGE 132kV
WHIB1D | SHET | B-2-1a | 132 | WHITE BRIDGE |  |  | WHITE BRIDGE 132kV
WHIB1E | SHET | B-2-1a | 132 | WHITE BRIDGE |  |  | WHITE BRIDGE 132kV
WHIB1F | SHET | B-2-1a | 132 | WHITE BRIDGE |  |  | WHITE BRIDGE 132kV
WHIB1G | SHET | B-2-1a | 132 | WHITE BRIDGE |  |  | WHITE BRIDGE 132kV
WHIB1H | SHET | B-2-1a | 132 | WHITE BRIDGE |  |  | WHITE BRIDGE 132kV
WHLL3- | SPT | B-2-1b | 33 | WHITESIDE HILL |  |  | WHITESIDE HILL 33kV
WHSO21 | NGET | B-2-1c, B-3-1c | 275 | WHITSON | 51.5648 | -2.9087 | WHITSON 275kV
WHSO22 | NGET | B-2-1c, B-3-1c | 275 | WHITSON | 51.5648 | -2.9087 | WHITSON 275kV
WHSO2A | NGET | B-2-1c, B-3-1c | 275 | WHITSON | 51.5648 | -2.9087 | WHITSON 275kV
WHSO2B | NGET | B-2-1c, B-3-1c | 275 | WHITSON | 51.5648 | -2.9087 | WHITSON 275kV
WHSO31 | NGET | B-3-1c | 33 | WHITSON | 51.5648 | -2.9087 | WHITSON 33kV
WHSO32 | NGET | B-3-1c | 33 | WHITSON | 51.5648 | -2.9087 | WHITSON 33kV
WHSO41 | NGET | B-2-1c, B-3-1c | 400 | WHITSON | 51.5648 | -2.9087 | WHITSON 400kV
WHSO4A | NGET | B-2-1c | 400 | WHITSON | 51.5648 | -2.9087 | WHITSON 400kV
WHTB1S | SHET, SPT | B-2-1a, B-2-1b, B-2-2a | 132 | WHISTLEFIELD BORDER | 56.0896 | -4.8401 | WHISTLEFIELD BORDER 132kV
WHTB1S | SHET, SPT | B-2-1a, B-2-1b, B-2-2a | 132 | WHISTLEFIELD BOUNDARY | 56.0896 | -4.8401 | WHISTLEFIELD BOUNDARY 132kV
WHTB1T | SHET, SPT | B-2-1a, B-2-1b, B-2-2a | 132 | WHISTLEFIELD BORDER | 56.0896 | -4.8401 | WHISTLEFIELD BORDER 132kV
WHTB1T | SHET, SPT | B-2-1a, B-2-1b, B-2-2a | 132 | WHISTLEFIELD BOUNDARY | 56.0896 | -4.8401 | WHISTLEFIELD BOUNDARY 132kV
WHTL1S | SPT | B-2-1b, B-3-1b | 132 | WHISTLEFIELD | 56.0896 | -4.8401 | WHISTLEFIELD 132kV
WHTL1T | SPT | B-2-1b, B-3-1b | 132 | WHISTLEFIELD | 56.0896 | -4.8401 | WHISTLEFIELD 132kV
WHTL3- | SPT | B-3-1b | 33 | WHISTLEFIELD | 56.0896 | -4.8401 | WHISTLEFIELD 33kV
WIBA21 | NGET | B-2-1c, B-2-2c, B-3-1c | 275 | WINCOBANK | 53.4159 | -1.4139 | WINCOBANK 275kV
WIBA31 | NGET | B-3-1c | 33 | WINCOBANK | 53.4159 | -1.4139 | WINCOBANK 33kV
WIEN11 | NGET | B-3-1c | 132 | WILLENHALL | 52.5778 | -2.0495 | WILLENHALL 132kV
WIEN2A | NGET | B-2-1c, B-3-1c | 275 | WILLENHALL | 52.5778 | -2.0495 | WILLENHALL 275kV
WIEN2B | NGET | B-2-1c, B-3-1c | 275 | WILLENHALL | 52.5778 | -2.0495 | WILLENHALL 275kV
WILE41 | NGET | B-2-1c, B-3-1c, B-4-2c | 400 | WILLINGTON EAST | 52.8556 | -1.5527 | WILLINGTON EAST 400kV
WILL11 | NGET | B-3-1c | 132 | WILLINGTON | 52.8554 | -1.5467 | WILLINGTON 132kV
WILL12 | NGET | B-3-1c | 132 | WILLINGTON | 52.8554 | -1.5467 | WILLINGTON 132kV
WILT2A | NGET | B-2-1c, B-3-1c | 275 | WILTON | 54.5758 | -1.1318 | WILTON 275kV
WILT2B | NGET | B-2-1c, B-3-1c | 275 | WILTON | 54.5758 | -1.1318 | WILTON 275kV
WILT2C | NGET | B-2-1c, B-3-1c | 275 | WILTON | 54.5758 | -1.1318 | WILTON 275kV
WILT2D | NGET | B-2-1c, B-3-1c | 275 | WILTON | 54.5758 | -1.1318 | WILTON 275kV
WIMB11 | NGET | B-3-1c | 132 | WIMBLEDON | 51.4311 | -0.18917 | WIMBLEDON 132kV
WIMB12 | NGET | B-3-1c, B-3-2c | 132 | WIMBLEDON | 51.4311 | -0.18917 | WIMBLEDON 132kV
WIMB21 | NGET | B-2-1c, B-2-2c, B-3-1c, B-3-2c, B-4-1c, B-4-2c | 275 | WIMBLEDON | 51.4311 | -0.18917 | WIMBLEDON 275kV
WIMB2A | NGET | B-2-1c, B-2-2c | 275 | WIMBLEDON | 51.4311 | -0.18917 | WIMBLEDON 275kV
WIMB41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | WIMBLEDON | 51.4311 | -0.18917 | WIMBLEDON 400kV
WIOW1- | SHET | B-2-2a | 132 | WILLOWDALE | 57.1539 | -2.0964 | WILLOWDALE 132kV
WIOW1Q | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | WILLOWDALE | 57.1539 | -2.0964 | WILLOWDALE 132kV
WIOW1R | SHET | B-2-1a, B-2-2a, B-3-1a | 132 | WILLOWDALE | 57.1539 | -2.0964 | WILLOWDALE 132kV
WIOW3- | SHET | B-3-1a | 33 | WILLOWDALE | 57.1539 | -2.0964 | WILLOWDALE 33kV
WISD11 | NGET | B-3-1c | 132 | WILLESDEN | 51.5346 | -0.25716 | WILLESDEN 132kV
WISD21 | NGET | B-3-1c, B-4-1c | 275 | WILLESDEN | 51.5346 | -0.25716 | WILLESDEN 275kV
WISD2A | NGET | B-2-1c, B-3-1c | 275 | WILLESDEN | 51.5346 | -0.25716 | WILLESDEN 275kV
WISD41 | NGET | B-2-1c, B-3-1c | 400 | WILLESDEN | 51.5346 | -0.25716 | WILLESDEN 400kV
WISD42 | NGET | B-2-1c, B-3-1c | 400 | WILLESDEN | 51.5346 | -0.25716 | WILLESDEN 400kV
WISD61 | NGET | B-3-1c | 66 | WILLESDEN | 51.5346 | -0.25716 | WILLESDEN 66kV
WISH1- | SPT | B-2-1b, B-2-2b, B-3-1b | 132 | WISHAW | 55.765 | -3.93 | WISHAW 132kV
WISH2- | SPT | B-2-1b, B-3-1b | 275 | WISHAW | 55.765 | -3.93 | WISHAW 275kV
WISH3- | SPT | B-3-1b | 33 | WISHAW | 55.765 | -3.93 | WISHAW 33kV
WISH3S | SPT | B-2-1b, B-3-1b | 33 | WISHAW | 55.765 | -3.93 | WISHAW 33kV
WISH3T | SPT | B-2-1b, B-2-2b, B-3-1b | 33 | WISHAW | 55.765 | -3.93 | WISHAW 33kV
WISH3W | SPT | B-4-1b | 33 | WISHAW | 55.765 | -3.93 | WISHAW 33kV
WISH4- | SPT | B-2-1b, B-2-2b, B-3-1b | 400 | WISHAW | 55.765 | -3.93 | WISHAW 400kV
WIYH1- | SPT | B-2-1b, B-3-1b | 132 | WINDYHILL | 55.9315 | -4.3753 | WINDYHILL 132kV
WIYH2- | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b, B-4-1b | 275 | WINDYHILL | 55.9315 | -4.3753 | WINDYHILL 275kV
WIYH2R | SPT | B-2-1b, B-2-2b | 275 | WINDYHILL | 55.9315 | -4.3753 | WINDYHILL 275kV
WIYH3W | SPT | B-4-1b | 33 | WINDYHILL | 55.9315 | -4.3753 | WINDYHILL 33kV
WIYH4Q | SPT | B-2-1b, B-2-2b, B-3-1b, B-3-2b | 400 | WINDYHILL | 55.9315 | -4.3753 | WINDYHILL 400kV
WLEE2- | SPT | B-2-1b, B-3-1b | 275 | WHITELEE | 55.6955 | -4.1725 | WHITELEE 275kV
WLEE3A | SPT | B-3-1b | 33 | WHITELEE | 55.6955 | -4.1725 | WHITELEE 33kV
WLEE3B | SPT | B-3-1b | 33 | WHITELEE | 55.6955 | -4.1725 | WHITELEE 33kV
WLEE3C | SPT | B-3-1b | 33 | WHITELEE | 55.6955 | -4.1725 | WHITELEE 33kV
WLER2- | SPT | B-2-2b, B-3-2b | 275 | WHITELEE REPOWERING |  |  | WHITELEE REPOWERING 275kV
WLER3A | SPT | B-3-2b | 33 | WHITELEE REPOWERING |  |  | WHITELEE REPOWERING 33kV
WLER3C | SPT | B-3-2b | 33 | WHITELEE REPOWERING |  |  | WHITELEE REPOWERING 33kV
WLER3E | SPT | B-3-2b | 33 | WHITELEE REPOWERING |  |  | WHITELEE REPOWERING 33kV
WLEX2- | SPT | B-2-1b, B-3-1b | 275 | WHITELEE EXTENSION |  |  | WHITELEE EXTENSION 275kV
WLEX3A | SPT | B-3-1b | 33 | WHITELEE EXTENSION |  |  | WHITELEE EXTENSION 33kV
WLEX3B | SPT | B-3-1b | 33 | WHITELEE EXTENSION |  |  | WHITELEE EXTENSION 33kV
WLEX3C | SPT | B-3-1b | 33 | WHITELEE EXTENSION |  |  | WHITELEE EXTENSION 33kV
WMEL11 | NGET | B-3-1c | 132 | WEST MELTON | 53.5015 | -1.377 | WEST MELTON 132kV
WMEL12 | NGET | B-3-1c, B-4-1c | 132 | WEST MELTON | 53.5015 | -1.377 | WEST MELTON 132kV
WMEL21 | NGET | B-2-1c, B-3-1c | 275 | WEST MELTON | 53.5015 | -1.377 | WEST MELTON 275kV
WNUK1- | SPT | B-2-2b | 132 | WHITENEUK |  |  | WHITENEUK 132kV
WOHI1Q | SHET | B-2-1a, B-3-1a | 132 | WOODHILL | 57.1544 | -2.1469 | WOODHILL 132kV
WOHI1R | SHET | B-2-1a, B-3-1a | 132 | WOODHILL | 57.1544 | -2.1469 | WOODHILL 132kV
WOHI3- | SHET | B-3-1a | 33 | WOODHILL | 57.1544 | -2.1469 | WOODHILL 33kV
WTHU31 | NGET | B-3-1c | 33 | WEST THURROCK | 51.4709 | 0.288 | WEST THURROCK 33kV
WTHU4A | NGET | B-2-1c, B-3-1c | 400 | WEST THURROCK | 51.4709 | 0.288 | WEST THURROCK 400kV
WTHU4B | NGET | B-2-1c, B-3-1c | 400 | WEST THURROCK | 51.4709 | 0.288 | WEST THURROCK 400kV
WTHU4C | NGET | B-2-1c | 400 | WEST THURROCK | 51.4709 | 0.288 | WEST THURROCK 400kV
WTHU4D | NGET | B-2-1c | 400 | WEST THURROCK | 51.4709 | 0.288 | WEST THURROCK 400kV
WTHU4E | NGET | B-2-1c | 400 | WEST THURROCK | 51.4709 | 0.288 | WEST THURROCK 400kV
WTHU4F | NGET | B-2-1c | 400 | WEST THURROCK | 51.4709 | 0.288 | WEST THURROCK 400kV
WWEY11 | NGET | B-3-1c | 132 | WEST WEYBRIDGE | 51.3534 | -0.47958 | WEST WEYBRIDGE 132kV
WWEY12 | NGET | B-3-1c | 132 | WEST WEYBRIDGE | 51.3534 | -0.47958 | WEST WEYBRIDGE 132kV
WWEY21 | NGET | B-2-1c, B-3-1c, B-4-1c | 275 | WEST WEYBRIDGE | 51.3534 | -0.47958 | WEST WEYBRIDGE 275kV
WWEY22 | NGET | B-2-1c, B-3-1c | 275 | WEST WEYBRIDGE | 51.3534 | -0.47958 | WEST WEYBRIDGE 275kV
WWEY2A | NGET | B-2-1c, B-3-1c | 275 | WEST WEYBRIDGE | 51.3534 | -0.47958 | WEST WEYBRIDGE 275kV
WWEY4A | NGET | B-2-1c, B-3-1c | 400 | WEST WEYBRIDGE | 51.3534 | -0.47958 | WEST WEYBRIDGE 400kV
WWEY4B | NGET | B-2-1c, B-3-1c | 400 | WEST WEYBRIDGE | 51.3534 | -0.47958 | WEST WEYBRIDGE 400kV
WYLF11 | NGET | B-3-1c | 132 | WYLFA | 53.4152 | -4.4802 | WYLFA 132kV
WYLF41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | WYLFA | 53.4152 | -4.4802 | WYLFA 400kV
WYLS41 | NGET | B-2-2c | 400 | WYLFA SOUTH | 53.4162 | -4.4806 | WYLFA SOUTH 400kV
WYMO11 | NGET | B-3-1c | 132 | WYMONDLEY | 51.9272 | -0.25028 | WYMONDLEY 132kV
WYMO41 | NGET | B-2-1c, B-2-2c, B-3-1c, B-4-1c | 400 | WYMONDLEY | 51.9272 | -0.25028 | WYMONDLEY 400kV
YAXL41 | NGET | B-2-1c | 400 | YAXLEY | 52.333 | 1.1046 | YAXLEY 400kV
YORK4A | NGET | B-2-2c, B-3-2c | 400 | YORK NORTH | 53.9566 | -1.0226 | YORK NORTH 400kV
YORK4B | NGET | B-2-2c, B-3-2c | 400 | YORK NORTH | 53.9566 | -1.0226 | YORK NORTH 400kV

## Cable
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
ABBA1- | DYCE1J | 0 | 7.8 | Cable | 0.1092 | 1.2324 | 10.14 | 173 | 158 | 158 | 158 | B-2-1a
ABNE1Q | ABNE1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
ALNE1Q | FYRI1J | 0 | 2.1 | Cable | 0.06 | 0.202 | 2.547 | 156 | 142 | 142 | 142 | B-2-1a
ALNE1R | FYRI1K | 0 | 2.1 | Cable | 0.06 | 0.202 | 2.547 | 156 | 142 | 142 | 142 | B-2-1a
ALYT2A | ALYT2B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
AMUL1E | AMUL1F | 0 | 8.62 | Cable | 0.2518 | 0.8041 | 10.215 | 153 | 129 | 129 | 129 | B-2-1a
AMUL1G | AMUL1H | 0 | 8.62 | Cable | 0.2518 | 0.8041 | 10.215 | 153 | 129 | 129 | 129 | B-2-1a
ARDK1- | INVE1J | 0 | 9 | Cable | 0.92 | 2.1 | 0.44 | 132 | 123 | 106 | 123 | B-2-1a
BEAT4- | BLHI4- | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BEAU1J | BEAU1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BEAU1J | BEAU1R | 0 | 2.4 | Cable | 0.0315 | 0.197 | 3.941 | 265 | 263 | 263 | 263 | B-2-1a
BEAU1J | BEAU1T | 0 | 0.22 | Cable | 0.01 | 0.0147 | 0.268 | 141 | 136 | 136 | 136 | B-2-1a
BEAU1J | DUCC1J | 0 | 3.1 | Cable | 0.0219 | 0.1198 | 10.47 | 444 | 403 | 403 | 403 | B-2-1a
BEAU1K | BEAU1N | 0 | 0.25 | Cable | 0.01 | 0.0167 | 0.305 | 141 | 136 | 136 | 136 | B-2-1a
BEAU1K | BEAU1S | 0 | 2.4 | Cable | 0.0315 | 0.197 | 3.941 | 265 | 263 | 263 | 263 | B-2-1a
BEAU1K | DUCC1K | 0 | 3.1 | Cable | 0.0219 | 0.1198 | 10.47 | 444 | 403 | 403 | 403 | B-2-1a
BEAU1L | BEAU1P | 0 | 1.74 | Cable | 0.0634 | 0.1599 | 2.062 | 152 | 140 | 140 | 140 | B-2-1a
BEAU1M | BEAU1Q | 0 | 1.74 | Cable | 0.0634 | 0.1599 | 2.062 | 152 | 140 | 140 | 140 | B-2-1a
BEAU2J | BEAU2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BHLA11 | GLEN1Q | 0 | 7.8 | Cable | 0.1425 | 0.6104 | 28.363 | 208 | 187 | 187 | 187 | B-2-1a
BLHI1J | BLHI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BLHI1J | KEIT1K | 0 | 3.26 | Cable | 0.0429 | 0.2582 | 4.733 | 176 | 176 | 176 | 176 | B-2-1a
BLHI1K | KEIT1J | 0 | 3.26 | Cable | 0.0429 | 0.2582 | 4.733 | 176 | 176 | 176 | 176 | B-2-1a
BLHI2J | BLHI2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BLHI2J | KEIT2Q | 0 | 2.41 | Cable | 0.01 | 0.044 | 13.793 | 580 | 546 | 546 | 546 | B-2-1a
BLHI2K | KEIT2R | 0 | 2.49 | Cable | 0.01 | 0.0456 | 14.286 | 580 | 546 | 546 | 546 | B-2-1a
BLHI4- | BLHI4R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 1272 | 1272 | 1272 | 1272 | B-2-1a
BLHI4- | MOWO4- | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BOAG1L | BOAG1Q | 0 | 5.7 | Cable | 0.0362 | 0.8819 | 7.98 | 227 | 209 | 209 | 209 | B-2-1a
BOAG1M | BOAG1R | 0 | 5.7 | Cable | 0.0362 | 0.8819 | 7.98 | 227 | 209 | 209 | 209 | B-2-1a
BOAG1P | BOAG1Q | 0 | 8.4 | Cable | 0.0558 | 1.271 | 11.48 | 227 | 209 | 209 | 209 | B-2-1a
BOAG1P | GLFA1- | 0 | 24.82 | Cable | 2.5189 | 5.7753 | 1.228 | 126 | 117 | 101 | 117 | B-2-1a
BRCW2J | BRCW2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BREC1Q | BREC1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BUMU1Q | BUMU1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BUMU1Q | CHAR1- | 0 | 42.2 | Cable | 4.29 | 9.76 | 2.1 | 132 | 123 | 106 | 123 | B-2-1a
CHAR1- | CHAR1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 229 | 211 | 183 | 211 | B-2-1a
CHAR1- | CHAR1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117 | B-2-1a
CHAR1- | CHAR1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117 | B-2-1a
CLAY1Q | WIOW1Q | 0 | 2.1 | Cable | 0.0474 | 0.1253 | 2.897 | 155 | 129 | 129 | 129 | B-2-1a
CLAY1R | WIOW1R | 0 | 2.1 | Cable | 0.0474 | 0.1253 | 2.897 | 155 | 129 | 129 | 129 | B-2-1a
CLUN1Q | CLUN1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117 | B-2-1a
CLUN1R | CLUN1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117 | B-2-1a
COGA1C | FARI1J | 0 | 4.11 | Cable | 0.065 | 0.334 | 6.245 | 210 | 196 | 196 | 196 | B-2-1a
CONN1C | CONN1J | 0 | 0.76 | Cable | 0.0161 | 0.0631 | 1.035 | 200 | 178 | 178 | 178 | B-2-1a
CORI1J | CORI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
CORI1J | CORI1P | 0 | 0.71 | Cable | 0.0216 | 0.0662 | 0.84 | 126 | 116 | 116 | 116 | B-2-1a
CORI1K | CORI1Q | 0 | 0.63 | Cable | 0.0191 | 0.0586 | 0.742 | 126 | 116 | 116 | 116 | B-2-1a
CRAI1- | CRAI1P | 0 | 1.1 | Cable | 0.0309 | 0.0973 | 1.456 | 149 | 137 | 137 | 137 | B-2-1a
CRAI1- | CRAI1Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 145 | 131 | 116 | 131 | B-2-1a
CRAI1- | CRAI1R | 0 | 1.1 | Cable | 0.0309 | 0.0973 | 1.456 | 149 | 137 | 137 | 137 | B-2-1a
CRAI1- | WOHI1Q | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120 | B-2-1a
CRAI1- | WOHI1R | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120 | B-2-1a
CREA1A | CREA1B | 0 | 1.4 | Cable | 0.0149 | 0.0892 | 2.161 | 306 | 253 | 253 | 253 | B-2-1a
CRSS1J | CRSS1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
CRSS2A | CRSS2C | 0 | 1.61 | Cable | 0.0178 | 0.0531 | 4.45 | 240 | 240 | 240 | 240 | B-2-1a
CRSS2B | CRSS2D | 0 | 1.66 | Cable | 0.0178 | 0.056 | 4.57 | 240 | 240 | 240 | 240 | B-2-1a
CRSS2C | HUNN2C | 0 | 38.1 | Cable | 0.6045 | 1.1463 | 76.848 | 240 | 240 | 240 | 240 | B-2-1a
CRSS2D | HUNN2D | 0 | 38.5 | Cable | 0.6157 | 1.1674 | 78.263 | 240 | 240 | 240 | 240 | B-2-1a
DLCH1A | DLCH1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
DLCH1A | LAIR1- | 0 | 4.52 | Cable | 0.458 | 1.089 | 0.215 | 111 | 103 | 89 | 103 | B-2-1a
DLCH1A | LAIR1- | 0 | 4.52 | Cable | 0.458 | 1.089 | 0.215 | 111 | 103 | 89 | 103 | B-2-1a
DUDH1Q | GLAG1Q | 0 | 1.95 | Cable | 0.0585 | 0.1151 | 2.73 | 124 | 114 | 114 | 114 | B-2-1a
DUDH1Q | MILC1R | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113 | B-2-1a
DUDH1R | GLAG1R | 0 | 1.95 | Cable | 0.0585 | 0.1151 | 2.73 | 124 | 114 | 114 | 114 | B-2-1a
DUDH1R | MILC1V | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113 | B-2-1a
DUNM1C | FARI1K | 0 | 4.07 | Cable | 0.064 | 0.28 | 6.175 | 210 | 196 | 196 | 196 | B-2-1a
DYCE1Q | DYCE1T | 0 | 1.3 | Cable | 0.0455 | 0.0543 | 2.428 | 150 | 143 | 143 | 143 | B-2-1a
DYCE1R | DYCE1U | 0 | 1.3 | Cable | 0.0455 | 0.0543 | 2.428 | 150 | 143 | 143 | 143 | B-2-1a
ELGI1L | ELGI1Q | 0 | 1.8 | Cable | 0.0236 | 0.1477 | 2.956 | 251 | 252 | 252 | 252 | B-2-1a
ELGI1M | ELGI1R | 0 | 1.8 | Cable | 0.0236 | 0.1477 | 2.956 | 251 | 252 | 252 | 252 | B-2-1a
ERRO1A | ERRO1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 240 | 240 | 240 | 240 | B-2-1a
ERRO1A | TUMM1J | 0 | 1.33 | Cable | 0.014 | 0.098 | 2.572 | 300 | 280 | 280 | 280 | B-2-1a
ERRO1B | ERRO1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 240 | 240 | 240 | 240 | B-2-1a
ERRO1B | TUMM1K | 0 | 1.3 | Cable | 0.013 | 0.095 | 2.51 | 300 | 280 | 280 | 280 | B-2-1a
ERRO1J | ERRO1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
ERRO1J | ERRO1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
FAUG1- | FAUG1M | 0 | 0.25 | Cable | 0.0028 | 0.0145 | 0.45 | 319 | 295 | 295 | 295 | B-2-1a
FAUG1- | FAUG1N | 0 | 0.17 | Cable | 0.0018 | 0.0097 | 0.302 | 319 | 297 | 297 | 297 | B-2-1a
FAUG1- | FAUG1P | 0 | 0.54 | Cable | 0.0088 | 0.0486 | 0.8014 | 230 | 218 | 218 | 218 | B-2-1a
FAUG1- | FAUG1Q | 0 | 1 | Cable | 0.01 | 0.012 | 0.002 | 126 | 117 | 101 | 117 | B-2-1a
FAUG1- | GLDO1G | 0 | 6 | Cable | 0.21 | 0.47 | 5.91 | 127 | 127 | 127 | 127 | B-2-1a
FAUG1J | FAUG1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
FAUG2J | FAUG2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
FAUG4J | FAUG4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
FETT2P | FETT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
FETT2Q | FETT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
FIDD1A | FIDD1Q | 0 | 0.55 | Cable | 0.0192 | 0.02 | 1.03 | 180 | 180 | 171 | 180 | B-2-1a
FIDD1B | FIDD1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
FIDD1Q | FIDD1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
FYRI1J | FYRI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
GLKO1- | TOMT1K | 0 | 3 | Cable | 0.417 | 0.627 | 0.156 | 83 | 77 | 67 | 77 | B-2-1a
INNE1J | INNE1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
INNE1J | KNOC1J | 0 | 4.57 | Cable | 0.1051 | 0.3818 | 6.326 | 155 | 150 | 150 | 150 | B-2-1a
INNE1K | INNE1L | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
INNE1L | KNOC1J | 0 | 4.48 | Cable | 0.1042 | 0.3784 | 6.27 | 155 | 150 | 150 | 150 | B-2-1a
INRU1S | PEHE1- | 0 | 3 | Cable | 0.0687 | 0.2536 | 4.105 | 186 | 186 | 186 | 186 | B-2-1a
INVE1J | INVE1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
INVR1A | INVR1C | 0 | 4.4 | Cable | 0.1393 | 0.4267 | 5.615 | 130 | 126 | 126 | 126 | B-2-1a
INVR1B | INVR1D | 0 | 4.4 | Cable | 0.1396 | 0.4277 | 5.627 | 130 | 126 | 126 | 126 | B-2-1a
KEIT3- | KEIT3A | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
KERG1- | KERG1J | 0 | 0.17 | Cable | 0.0019 | 0.0098 | 0.298 | 370 | 370 | 370 | 370 | B-2-1a
KERG1- | KERG1J | 0 | 0.17 | Cable | 0.0019 | 0.0098 | 0.298 | 370 | 370 | 370 | 370 | B-2-1a
KERG1J | KERG1K | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
KERG1J | KERG1K | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
KERG1J | KERG1P | 0 | 0.09 | Cable | 0.0017 | 0.0085 | 0.149 | 234 | 234 | 234 | 234 | B-2-1a
KERG1J | KERG1Q | 0 | 0.15 | Cable | 0.0027 | 0.0137 | 0.241 | 234 | 234 | 234 | 234 | B-2-1a
KERG1J | KERG1T | 0 | 0.12 | Cable | 0.0013 | 0.0069 | 0.21 | 220 | 220 | 220 | 220 | B-2-1a
KERG1K | KERG1R | 0 | 0.08 | Cable | 0.0014 | 0.0072 | 0.127 | 234 | 234 | 234 | 234 | B-2-1a
KINA2J | KINA2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
KINT1- | KINT1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
KINT1- | KINT1P | 0 | 0.27 | Cable | 0.01 | 0.0154 | 0.354 | 148 | 140 | 140 | 140 | B-2-1a
KINT1- | KINT1R | 0 | 0.26 | Cable | 0.01 | 0.0148 | 0.341 | 148 | 140 | 140 | 140 | B-2-1a
KINT1- | KINT1T | 0 | 0.6 | Cable | 0.0135 | 0.0343 | 0.787 | 165 | 141 | 141 | 141 | B-2-1a
KINT1- | KINT1U | 0 | 0.6 | Cable | 0.0135 | 0.0343 | 0.787 | 165 | 141 | 141 | 141 | B-2-1a
KINT2J | KINT2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
KNOC2J | KNOC2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
KNOC2J | KNOC2L | 0 | 1.47 | Cable | 0.01 | 0.042 | 8.36 | 930 | 900 | 900 | 900 | B-2-1a
KNOC2J | KNOC2N | 0 | 0.51 | Cable | 0.01 | 0.0157 | 3.005 | 850 | 793 | 793 | 793 | B-2-1a
KNOC2K | KNOC2M | 0 | 1.29 | Cable | 0.01 | 0.037 | 7.336 | 930 | 900 | 900 | 900 | B-2-1a
KNOC2K | KNOC2P | 0 | 0.17 | Cable | 0.01 | 0.01 | 1.006 | 850 | 793 | 793 | 793 | B-2-1a
LOCB1J | LOCB1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
LOCB1J | LOCB1L | 0 | 0.83 | Cable | 0.01 | 0.0635 | 1.489 | 373 | 373 | 373 | 373 | B-2-1a
LOCB1J | LOCB1S | 0 | 0.79 | Cable | 0.022 | 0.0694 | 1.039 | 149 | 137 | 137 | 137 | B-2-1a
LOCB1J | LOCB1S | 0 | 0.785 | Cable | 0.022 | 0.0694 | 1.0394 | 149 | 137 | 137 | 137 | B-2-1a
LOCB1J | LOCB1U | 0 | 0.38 | Cable | 0.0105 | 0.0332 | 0.496 | 149 | 137 | 137 | 137 | B-2-1a
LOCB1K | LOCB1M | 0 | 0.92 | Cable | 0.01 | 0.0704 | 1.651 | 373 | 373 | 373 | 373 | B-2-1a
LOCB1K | LOCB1R | 0 | 0.73 | Cable | 0.0204 | 0.0641 | 0.96 | 149 | 137 | 137 | 137 | B-2-1a
LOCB1K | LOCB1T | 0 | 0.28 | Cable | 0.008 | 0.0252 | 0.377 | 149 | 137 | 137 | 137 | B-2-1a
LOCB2J | LOCB2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
MELG1J | MELG1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
MELG1J | STRL1- | 0 | 10 | Cable | 0.0752 | 0.806 | 18.176 | 317 | 277 | 277 | 277 | B-2-1a
MELG4J | MELG4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
MILC1R | MILC1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
MILC1R | MILC1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
MILC1S | MILC1V | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
MORF4- | NEDE4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
MYBS3M | MYBS3N | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
NEDE4J | NEDE4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
ORRI1Q | ORRI1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117 | B-2-1a
ORRI1R | ORRI1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117 | B-2-1a
PEHE2- | PEHE2Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PEHE2- | PEHE2S | 0 | 1 | Cable | 0.01 | 0.033 | 14.21 | 776 | 776 | 776 | 776 | B-2-1a
PEHE2- | PEHEMEC6 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PEHE2J | PEHE2Q | 0 | 0.47 | Cable | 0.01 | 0.01 | 5.009 | 1560 | 1560 | 1560 | 1560 | B-2-1a
PEHE2R | PEHERSV2 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PEHE2T | PEHERSV1 | 0 | 1 | Cable | 0.01 | 0.032 | 13.51 | 776 | 776 | 776 | 776 | B-2-1a
PEHE2U | PEHEMEC5 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313 | B-2-1a
PEHE2V | PEHEMEC3 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313 | B-2-1a
PEHE2W | PEHEMEC1 | 0 | 1 | Cable | 0.01 | 0.021 | 5.25 | 313 | 313 | 313 | 313 | B-2-1a
PEHE4J | PEHE4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PEHEMEC1 | PEHEMEC2 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PEHEMEC1 | PEHEMEC6 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PEHEMEC2 | PEHEMEC3 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PEHEMEC2 | PEHERSV2 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PEHEMEC3 | PEHEMEC4 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PEHEMEC4 | PEHEMEC5 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PEHEMEC4 | PEHERSV1 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PEHEMEC5 | PEHEMEC6 | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PEHERSV1 | PEHE2K | 0 | 0.47 | Cable | 0.01 | 0.01 | 5.0094 | 1560 | 1560 | 1560 | 1560 | B-2-1a
PERS1Q | PERS1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PERS1Q | WIOW1R | 0 | 3.7 | Cable | 0.084 | 0.221 | 5.104 | 155 | 129 | 129 | 129 | B-2-1a
PERS1R | WIOW1Q | 0 | 3.7 | Cable | 0.084 | 0.221 | 5.104 | 155 | 129 | 129 | 129 | B-2-1a
PERS2Q | PERS2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PORA1T | PORA1U | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
ROTI4J | ROTI4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
SFEE1A | SFEE1C | 0 | 0.27 | Cable | 0.0077 | 0.0304 | 0.351 | 47 | 47 | 47 | 47 | B-2-1a
SFEE1B | SFEE1D | 0 | 0.29 | Cable | 0.0084 | 0.0303 | 0.383 | 47 | 47 | 47 | 47 | B-2-1a
SFEG1Q | SFEV1S | 0 | 0.4 | Cable | 0.01 | 0.034 | 0.46 | 160 | 135 | 135 | 135 | B-2-1a
SFEG1R | SFEV1T | 0 | 0.4 | Cable | 0.01 | 0.034 | 0.46 | 160 | 135 | 135 | 135 | B-2-1a
SFER1J | SFER1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
SFER1J | SFER1M | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
SFER1K | SFER1L | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
SFER1L | SFER1M | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100 | B-2-1a
SFEV1S | SFEV1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100 | B-2-1a
SGRX2- | TEAL2K | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
SLKB1J | SLKB1L | 0 | 1.5 | Cable | 0.0159 | 0.0956 | 2.316 | 306 | 253 | 253 | 253 | B-2-1a
SLKB1K | SLKB1M | 0 | 1.5 | Cable | 0.0159 | 0.0956 | 2.316 | 306 | 253 | 253 | 253 | B-2-1a
SLOY1A | SLOY1K | 0 | 0.92 | Cable | 0.0279 | 0.0856 | 1.126 | 120 | 112 | 112 | 112 | B-2-1a
SLOY1B | SLOY1K | 0 | 0.91 | Cable | 0.0277 | 0.0848 | 1.1158 | 120 | 112 | 112 | 112 | B-2-1a
SLOY1C | SLOY1J | 0 | 0.835 | Cable | 0.0254 | 0.0778 | 1.0238 | 120 | 112 | 112 | 112 | B-2-1a
SLOY1D | SLOY1J | 0 | 0.867 | Cable | 0.0264 | 0.0808 | 1.0631 | 120 | 112 | 112 | 112 | B-2-1a
SLOY1E | SLOY1J | 0 | 1.28 | Cable | 0.0389 | 0.1193 | 1.5695 | 140 | 132 | 132 | 132 | B-2-1a
SLOY1F | SLOY1K | 0 | 1.37 | Cable | 0.0417 | 0.1277 | 1.6798 | 140 | 132 | 132 | 132 | B-2-1a
SLOY1J | SLOY1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
SPIT2J | SPIT2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
SPIT2K | SPIT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 960 | 960 | 960 | 960 | B-2-1a
STRW1- | STRW1A | 0 | 0.35 | Cable | 0.01 | 0.0631 | 0.48 | 200 | 178 | 178 | 178 | B-2-1a
TEAL2A | TEAL2J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
TEAL2B | TEAL2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
TEAL2J | TEAL2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
TEAL2J | WFIB2- | 0 | 38.8 | Cable | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030 | B-2-1a
THUS1J | THUS1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
TOMT1J | TOMT1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
TOMT1J | TOMT1M | 0 | 0.14 | Cable | 0.29 | 1.59 | 18.77 | 261 | 237 | 237 | 237 | B-2-1a
TOMT1K | TOMT1L | 0 | 0.13 | Cable | 0.27 | 1.5 | 17.6 | 261 | 237 | 237 | 237 | B-2-1a
TUMM2J | TUMM2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
WHIB1A | WHIB1C | 0 | 2.93 | Cable | 0.0896 | 0.2773 | 3.437 | 153 | 140 | 140 | 140 | B-2-1a
WHIB1B | WHIB1D | 0 | 2.93 | Cable | 0.0896 | 0.2773 | 3.437 | 153 | 140 | 140 | 140 | B-2-1a
WHIB1E | WHIB1G | 0 | 0.44 | Cable | 0.0134 | 0.0416 | 0.515 | 153 | 140 | 140 | 140 | B-2-1a
WHIB1F | WHIB1H | 0 | 0.44 | Cable | 0.0134 | 0.0416 | 0.515 | 153 | 140 | 140 | 140 | B-2-1a
WIOW1Q | WOHI1Q | 0 | 3.4 | Cable | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147 | B-2-1a
WIOW1R | WOHI1R | 0 | 3.4 | Cable | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147 | B-2-1a
AUCW1- | HADH1- | 0 | 18 | Cable | 1.83 | 3.88 | 0.96 | 140 | 140 | 140 | 140 | B-2-1b
AUCW1- | MAYB1- | 0 | 0.07 | Cable | 0 | 0.009 | 0.0682 | 140 | 140 | 140 | 140 | B-2-1b
BRAP1- | GOVA1R | 0 | 6.13 | Cable | 0.2168 | 0.45 | 11.0073 | 125 | 113 | 110 | 113 | B-2-1b
BROT1- | COAL1- | 0 | 3.2 | Cable | 0.0261 | 0.2614 | 5.959 | 293 | 293 | 293 | 293 | B-2-1b
BUSB2- | GIFF2Q | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240 | B-2-1b
BUSB2- | GIFF2R | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240 | B-2-1b
CATY1Q | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.3018 | 6.1089 | 122 | 107 | 107 | 107 | B-2-1b
CATY1R | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.3018 | 6.1089 | 122 | 107 | 107 | 107 | B-2-1b
CCSS1- | COAL1- | 0 | 6.97 | Cable | 0.10961 | 0.60003 | 11.4841 | 210 | 210 | 210 | 210 | B-2-1b
CHAS2Q | DALM2Q | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186 | B-2-1b
CHAS2R | DALM2R | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186 | B-2-1b
CLYN2Q | ELVA2Q | 0 | 6.2 | Cable | 0.032 | 0.174 | 26.956 | 476 | 415 | 415 | 415 | B-2-1b
CLYS2R | ELVA2R | 0 | 7.17 | Cable | 0.0445 | 0.1289 | 23.8486 | 291 | 245 | 245 | 245 | B-2-1b
CLYS3B | CLYS3X | 0 | 0.05 | Cable | 0.0084 | 0.0315 | 0.0106 | 52 | 52 | 52 | 52 | B-2-1b
COAL1A | MIDM1- | 0 | 13.88 | Cable | 0.3802 | 0.937 | 17.3258 | 153 | 134 | 134 | 134 | B-2-1b
COAL1B | CCSS1- | 0 | 6.97 | Cable | 0.10961 | 0.60003 | 11.4841 | 210 | 210 | 210 | 210 | B-2-1b
COAL1B | KYPE1- | 0 | 17.09 | Cable | 0.3286 | 1.5387 | 24.4568 | 194 | 180 | 180 | 180 | B-2-1b
CRYR1A | WESE1- | 0 | 3.989 | Cable | 0.0559 | 0.3473 | 5.1163 | 155 | 155 | 155 | 155 | B-2-1b
DALM1- | SANX1Q | 0 | 5.16 | Cable | 0.1457 | 0.1955 | 6.7791 | 181 | 164 | 164 | 164 | B-2-1b
DALM1- | SANX1R | 0 | 5.78 | Cable | 0.1632 | 0.2189 | 7.5936 | 181 | 164 | 164 | 164 | B-2-1b
DEWP2Q | WHHO2Q | 0 | 2.48 | Cable | 0.0159 | 0.0559 | 7.7539 | 276 | 240 | 240 | 240 | B-2-1b
DEWP2R | WHHO2R | 0 | 2.55 | Cable | 0.0164 | 0.0575 | 7.9728 | 276 | 240 | 240 | 240 | B-2-1b
DONO3A | HAGH3- | 0 | 7.5 | Cable | 1.0376 | 3.279 | 1.7603 | 40 | 38 | 38 | 38 | B-2-1b
DUNE3- | TODD3- | 0 | 6.07 | Cable | 2.245 | 5.682 | 0.73 | 42 | 42 | 42 | 42 | B-2-1b
DUNH1Q | DUNH1S | 0 | 0.336 | Cable | 0.0168 | 0.037 | 0.2759 | 159 | 147 | 147 | 147 | B-2-1b
DUNH1R | DUNH1T | 0 | 0.372 | Cable | 0.0186 | 0.0409 | 0.3054 | 159 | 147 | 147 | 147 | B-2-1b
EKIS2- | WLEE2- | 0 | 6 | Cable | 0.034 | 0.101 | 25.635 | 378 | 378 | 378 | 378 | B-2-1b
EKIS2- | WLEX2- | 0 | 16.68 | Cable | 0.088 | 0.346 | 70.948 | 340 | 340 | 340 | 340 | B-2-1b
ENHI1- | NECU1C | 0 | 4.4 | Cable | 0.1242 | 0.2856 | 5.7805 | 134 | 123 | 123 | 123 | B-2-1b
ESST1- | PART1Q | 0 | 6.9 | Cable | 0.137 | 0.641 | 9.143 | 210 | 200 | 190 | 200 | B-2-1b
ESST1- | WIYH1- | 0 | 3.59 | Cable | 0.0711 | 0.3255 | 5.0111 | 233 | 200 | 200 | 200 | B-2-1b
ESST1Q | PART1R | 0 | 6.84 | Cable | 0.136 | 0.635 | 9.062 | 203 | 190 | 190 | 190 | B-2-1b
ESST1Q | WIYH1- | 0 | 3.16 | Cable | 0.178 | 0.334 | 7.691 | 203 | 190 | 190 | 190 | B-2-1b
FINN1Q | PART1Q | 0 | 2.813 | Cable | 0.0563 | 0.1582 | 4.0035 | 171 | 152 | 152 | 152 | B-2-1b
FINN1R | PART1R | 0 | 2.845 | Cable | 0.057 | 0.16 | 4.0491 | 171 | 152 | 152 | 152 | B-2-1b
GAWH3- | HAHA3- | 0 | 5 | Cable | 1.6871 | 4.5198 | 0.5324 | 36 | 34 | 34 | 34 | B-2-1b
GLGL1Q | SAKN1- | 0 | 9 | Cable | 0.2541 | 0.5842 | 11.0847 | 166 | 166 | 166 | 166 | B-2-1b
GLGL3- | SNQR3- | 0 | 2.3 | Cable | 0.6364 | 2.0111 | 0.2699 | 30 | 30 | 30 | 30 | B-2-1b
GLGL3- | WHLL3- | 0 | 1.2 | Cable | 0.332 | 1.5811 | 0.1408 | 30 | 30 | 30 | 30 | B-2-1b
GOVA1Q | HAGR1Q | 0 | 4.04 | Cable | 0.2097 | 0.252 | 6.0812 | 70 | 64 | 64 | 64 | B-2-1b
GOVA1R | HAGR1R | 0 | 4.11 | Cable | 0.187 | 0.225 | 3.587 | 69 | 64 | 64 | 64 | B-2-1b
GRMO3A | GRMO3C | 0 | 1 | Cable | 0.017 | 0.047 | 0.066 | 1000 | 1000 | 1000 | 1000 | B-2-1b
GRMO3A | GRMO3C | 0 | 1 | Cable | 0.012 | 0.035 | 0.049 | 1000 | 1000 | 1000 | 1000 | B-2-1b
HARR3- | KYPE3A | 0 | 0.5 | Cable | 0.0692 | 0.2186 | 0.1174 | 40 | 38 | 38 | 38 | B-2-1b
HUER1- | HUNF1Q | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 146 | 146 | 146 | B-2-1b
HUER1- | HUNF1R | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 146 | 146 | 146 | B-2-1b
HUER1- | JUNA1T | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 175 | 175 | 175 | B-2-1b
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.0001 | 0.001 | 0.7263 | 2770 | 2770 | 2770 | 2770 | B-2-1b
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.0001 | 0.001 | 0.7263 | 2770 | 2770 | 2770 | 2770 | B-2-1b
HUNE4- | HUNN4A | 0 | 0.259 | Cable | 0.0008 | 0.0027 | 1.7445 | 607 | 607 | 607 | 607 | B-2-1b
HUNE4- | HUNN4B | 0 | 0.177 | Cable | 0.0005 | 0.0019 | 1.1922 | 607 | 607 | 607 | 607 | B-2-1b
HUNN2A | HUNN2C | 0 | 3.356 | Cable | 0.0212 | 0.1068 | 11.7957 | 240 | 240 | 240 | 240 | B-2-1b
HUNN2B | HUNN2D | 0 | 3.413 | Cable | 0.0216 | 0.1087 | 11.9781 | 240 | 240 | 240 | 240 | B-2-1b
INVB2A | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000 | B-2-1b
INVB2B | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000 | B-2-1b
KAIM2- | WHHO2Q | 0 | 6.455 | Cable | 0.0415 | 0.1456 | 20.1821 | 276 | 240 | 240 | 240 | B-2-1b
KAIM2- | WHHO2R | 0 | 6.297 | Cable | 0.0405 | 0.1421 | 19.6881 | 276 | 240 | 240 | 240 | B-2-1b
KILB1Q | WIYH1- | 0 | 3.38 | Cable | 0.098 | 0.209 | 4.333 | 139 | 126 | 113 | 126 | B-2-1b
KILB1R | WIYH1- | 0 | 3.29 | Cable | 0.115 | 0.199 | 8.02 | 139 | 126 | 113 | 126 | B-2-1b
KILG2- | MAHI2- | 0 | 14 | Cable | 0.0719 | 0.2998 | 53.9497 | 352 | 290 | 290 | 290 | B-2-1b
MEAD1- | MEAD1Q | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100 | B-2-1b
MEAD1- | MEAD1R | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100 | B-2-1b
MINN3- | MOFF3A | 0 | 12.34 | Cable | 4.1636 | 17.1281 | 1.314 | 31 | 29 | 29 | 29 | B-2-1b
MOSH1Q | MOSM1A | 0 | 1.03 | Cable | 0.048 | 0.063 | 2.012 | 132 | 123 | 106 | 123 | B-2-1b
MOSH1R | MOSM1B | 0 | 0.96 | Cable | 0.044 | 0.057 | 1.826 | 132 | 123 | 106 | 123 | B-2-1b
NECU1- | SOKY1- | 0 | 4.2 | Cable | 0.0458 | 0.2435 | 7.265 | 242 | 223 | 192 | 223 | B-2-1b
NEIL1- | NEIL1C | 0 | 0.32 | Cable | 0 | 0.0126 | 0 | 416 | 389 | 389 | 389 | B-2-1b
NEIL2- | NEIL2C | 0 | 0.2 | Cable | 0.0007 | 0.003 | 1.492 | 1140 | 945 | 945 | 945 | B-2-1b
NOKY1- | NECU1- | 0 | 1.3 | Cable | 0.0084 | 0.0773 | 2.2771 | 261 | 261 | 261 | 261 | B-2-1b
POOB2Q | SHRU2Q | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270 | B-2-1b
POOB2R | SHRU2R | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270 | B-2-1b
PORD2Q | WGEO2Q | 0 | 1.83 | Cable | 0.017 | 0.056 | 12.236 | 305 | 198 | 198 | 198 | B-2-1b
PORD2R | WGEO2R | 0 | 2.15 | Cable | 0.014 | 0.049 | 10.691 | 305 | 198 | 198 | 198 | B-2-1b
RAVE3S | WISH3S | 0 | 4.1 | Cable | 0.9601 | 1.9766 | 0.01 | 32 | 32 | 32 | 32 | B-2-1b
RAVE3T | WISH3T | 0 | 4.1 | Cable | 0.9601 | 1.9766 | 0.01 | 32 | 32 | 32 | 32 | B-2-1b
BEDD4A | ROWD42 | 0 | 10.1 | Cable | 0.0071 | 0.1292 | 121.8435 | 1309 | 1309 | 1309 | 1309 | B-2-1c
BEDD4B | ROWD41 | 0 | 10.1 | Cable | 0.0069 | 0.1275 | 124.3819 | 1417 | 1417 | 1220 | 1294 | B-2-1c
BIRK21 | LISD2A | 0 | 12.891 | Cable | 0.0271 | 0.2978 | 125.0427 | 817 | 817 | 739 | 739 | B-2-1c
BODE41 | GWYN4A | 0 | 0.8 | Cable | 0.0008 | 0.0094 | 7.6404 | 1056 | 1056 | 980 | 980 | B-2-1c
CAMA11 | IROA13 | 0 | 1 | Cable | 0.815 | 5.549 | 1.802 | 246 | 228 | 198 | 228 | B-2-1c
CAMA12 | IROA12 | 0 | 1 | Cable | 0.815 | 5.549 | 1.802 | 246 | 228 | 198 | 228 | B-2-1c
CANT41 | CANT41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 3102 | 3102 | 3102 | 3102 | B-2-1c
CANT41 | CANT41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 3102 | 3102 | 3102 | 3102 | B-2-1c
CANT41 | CANT41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 3102 | 3102 | 3102 | 3102 | B-2-1c
CAPE1A | INCE11 | 0 | 1 | Cable | 0.2226 | 2.0652 | 3.2486 | 258 | 258 | 240 | 240 | B-2-1c
CAPE1B | INCE11 | 0 | 1 | Cable | 0.2204 | 2.0451 | 3.2416 | 240 | 240 | 240 | 240 | B-2-1c
CHIL41 | FAWL41 | 0 | 3.73 | Cable | 0.0037 | 0.0235 | 56.9944 | 970 | 928 | 800 | 928 | B-2-1c
CHIL41 | FAWL41 | 0 | 3.69 | Cable | 0.0037 | 0.0232 | 56.3832 | 970 | 928 | 800 | 928 | B-2-1c
CITR41 | CITR41 | 0 | 0.1 | Cable | 0.0001 | 0.0008 | 1.8 | 1733 | 1492 | 1362 | 1492 | B-2-1c
CITR41 | CITR41 | 0 | 0.1 | Cable | 0.0001 | 0.0008 | 1.8 | 1566 | 1538 | 1351 | 1424 | B-2-1c
CITR41 | PUDM41 | 0 | 7.29 | Cable | 0.0066 | 0.0598 | 131.22 | 1282 | 1136 | 984 | 1136 | B-2-1c
CITR41 | SJOW41 | 0 | 7.243 | Cable | 0.0065 | 0.0594 | 130.374 | 1282 | 1136 | 984 | 1136 | B-2-1c
CITR41 | SJOW41 | 0 | 6.776 | Cable | 0.0061 | 0.0556 | 121.968 | 1282 | 1136 | 984 | 1136 | B-2-1c
CITR41 | WHAM4B | 0 | 9.39 | Cable | 0.0085 | 0.077 | 169.02 | 1282 | 1136 | 984 | 1136 | B-2-1c
CONQ41 | FLIB41 | 0 | 3.495 | Cable | 0.0022 | 0.05 | 43.9195 | 1438 | 1438 | 1389 | 1389 | B-2-1c
CONQ41 | FLIB41 | 0 | 3.388 | Cable | 0.0022 | 0.0485 | 42.5749 | 1438 | 1438 | 1389 | 1389 | B-2-1c
DAMC41 | KINO41 | 0 | 0.919 | Cable | 0.0001 | 0.0005 | 2.6467 | 1528 | 1528 | 1528 | 1528 | B-2-1c
DINO41 | PENT41 | 0 | 10.605 | Cable | 0.0056 | 0.153 | 133.2664 | 1604 | 1571 | 1571 | 1571 | B-2-1c
DINO41 | PENT41 | 0 | 10.762 | Cable | 0.0057 | 0.1552 | 135.2393 | 1604 | 1604 | 1557 | 1557 | B-2-1c
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 524 | 518 | 401 | 401 | B-2-1c
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 525 | 525 | 426 | 426 | B-2-1c
EALI21 | WISD2A | 0 | 6.075 | Cable | 0.0121 | 0.1391 | 61.5397 | 750 | 750 | 735 | 735 | B-2-1c
ELST12 | HEND11 | 0 | 1 | Cable | 0.081 | 0.634 | 16.01 | 299 | 275 | 218 | 275 | B-2-1c
ELST41 | SJOW41 | 0 | 20 | Cable | 0.014 | 0.176 | 244.29 | 1767 | 1732 | 1663 | 1732 | B-2-1c
FRIN4A | FRIS41 | 0 | 0.3 | Cable | 0.0002 | 0.0035 | 3.2746 | 2779 | 2779 | 2779 | 2779 | B-2-1c
FRIN4B | FRIS4C | 0 | 0.1 | Cable | 0 | 0 | 0 | 2780 | 2780 | 2780 | 2780 | B-2-1c
FRIS4A | FRIS41 | 0 | 0.2 | Cable | 0.0001 | 0.0024 | 2.183 | 2779 | 2779 | 2779 | 2779 | B-2-1c
FRIS4B | FRIS41 | 0 | 0.15 | Cable | 0.0001 | 0.0018 | 1.6373 | 2779 | 2779 | 2779 | 2779 | B-2-1c
FRIS4D | FRIS41 | 0 | 0.2 | Cable | 0 | 0 | 0 | 2779 | 2779 | 2779 | 2779 | B-2-1c
GRST2A | WILT2A | 0 | 1 | Cable | 0 | 0.011 | 0 | 207 | 196 | 183 | 196 | B-2-1c
GRST2A | WILT2B | 0 | 1 | Cable | 0 | 0.011 | 0 | 207 | 198 | 185 | 198 | B-2-1c
GRST2B | WILT2C | 0 | 1 | Cable | 0 | 0.011 | 0 | 198 | 198 | 180 | 180 | B-2-1c
GRST2B | WILT2D | 0 | 1 | Cable | 0 | 0.011 | 0 | 206 | 204 | 190 | 204 | B-2-1c
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1770 | 1730 | 1600 | 1730 | B-2-1c
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1770 | 1730 | 1600 | 1730 | B-2-1c
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729 | B-2-1c
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729 | B-2-1c
HAMH1A | LEMR11 | 0 | 1 | Cable | 0.016 | 0.098 | 1.942 | 226 | 209 | 209 | 209 | B-2-1c
HAMH1B | LEMR11 | 0 | 1 | Cable | 0.027 | 0.129 | 0.424 | 211 | 170 | 170 | 170 | B-2-1c
HARK21 | HARK21 | 0 | 0.05 | Cable | 0.0001 | 0.0013 | 0.258 | 953 | 953 | 953 | 953 | B-2-1c
HIBU41 | SJOW41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1770 | 1730 | 1600 | 1730 | B-2-1c
HIBU41 | SJOW41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1770 | 1730 | 1600 | 1730 | B-2-1c
IVER21 | NHYD2A | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 381 | B-2-1c
IVER22 | NHYD2B | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 381 | B-2-1c
JORD21 | NORL2B | 0 | 2.843 | Cable | 0.0109 | 0.0719 | 20.1177 | 419 | 419 | 381 | 381 | B-2-1c
KENG41 | SJOW41 | 0 | 4.756 | Cable | 0.0032 | 0.0562 | 51.9127 | 1770 | 1730 | 1600 | 1730 | B-2-1c
KENG41 | SJOW41 | 0 | 4.769 | Cable | 0.0032 | 0.0564 | 52.0546 | 1770 | 1730 | 1600 | 1730 | B-2-1c
KENG41 | WIMB41 | 0 | 12.329 | Cable | 0.0085 | 0.1557 | 134.5735 | 1770 | 1730 | 1600 | 1730 | B-2-1c
KENG41 | WIMB41 | 0 | 12.2 | Cable | 0.0084 | 0.1541 | 133.1654 | 1770 | 1730 | 1600 | 1730 | B-2-1c
KENG41 | WISD41 | 0 | 2.939 | Cable | 0.002 | 0.0347 | 32.0798 | 1770 | 1730 | 1600 | 1730 | B-2-1c
KENG41 | WISD42 | 0 | 2.989 | Cable | 0.002 | 0.0353 | 32.6255 | 1770 | 1730 | 1600 | 1730 | B-2-1c
KIBY21 | LISD21 | 0 | 10.239 | Cable | 0.0173 | 0.2966 | 60.8154 | 762 | 762 | 698 | 698 | B-2-1c
KIBY21 | LISD21 | 0 | 9.518 | Cable | 0.0228 | 0.2008 | 86.3283 | 762 | 762 | 619 | 619 | B-2-1c
KIRK2A | SKLG21 | 0 | 8.608 | Cable | 0.0146 | 0.2402 | 93.5689 | 762 | 762 | 619 | 619 | B-2-1c
LEIS11 | SIZE11 | 0 | 2.149 | Cable | 0.0196 | 0.2155 | 4.8028 | 301 | 301 | 243 | 243 | B-2-1c
LEIS11 | SIZE11 | 0 | 2.148 | Cable | 0.0195 | 0.2154 | 4.8006 | 301 | 301 | 243 | 243 | B-2-1c
LEIS11 | SIZE1A | 0 | 1.65 | Cable | 0.015 | 0.1655 | 3.6876 | 301 | 301 | 243 | 243 | B-2-1c
LEIS11 | SIZE1B | 0 | 1.65 | Cable | 0.015 | 0.1655 | 3.6876 | 301 | 301 | 243 | 243 | B-2-1c
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 827 | 827 | 779 | 779 | B-2-1c
NEWX21 | WIMB21 | 0 | 13.479 | Cable | 0.027 | 0.3087 | 136.5422 | 819 | 819 | 813 | 813 | B-2-1c
NORL2A | SHEC21 | 0 | 4.372 | Cable | 0.0192 | 0.1119 | 29.2487 | 419 | 419 | 381 | 381 | B-2-1c
NORL2B | PITS21 | 0 | 10.751 | Cable | 0.0473 | 0.2752 | 71.9242 | 419 | 419 | 381 | 381 | B-2-1c
PITS21 | TEMP21 | 0 | 6.69 | Cable | 0.0294 | 0.1713 | 44.7561 | 419 | 419 | 381 | 381 | B-2-1c
PUDM41 | WHAM4A | 0 | 2.17 | Cable | 0.002 | 0.0178 | 39.06 | 1282 | 1136 | 984 | 1136 | B-2-1c
PYLE21 | PYLE21 | 0 | 0.25 | Cable | 0.0004 | 0.0063 | 1.69 | 1204 | 1115 | 1018 | 1115 | B-2-1c
SELL4A | SELL4C | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 1642 | B-2-1c
SELL4A | SELL4D | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 1642 | B-2-1c
SELL4A | SELL4E | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 1642 | B-2-1c
SELL4A | SELL4F | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 1642 | B-2-1c
SPEN42 | SPEN42 | 0 | 0.131 | Cable | 0.0001 | 0.0015 | 1.4299 | 278 | 265 | 248 | 250 | B-2-1c
CLAY1Q | REDM1Q | 0 | 4.8 | Cable | 0.1402 | 0.4475 | 5.686 | 153 | 129 | 129 | 129 | B-2-2a | 2025 | Change
CLAY1R | REDM1R | 0 | 4.8 | Cable | 0.1402 | 0.4475 | 5.686 | 153 | 129 | 129 | 129 | B-2-2a | 2025 | Change
CONN1J | CONN1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2025 | Addition
CRSS1K | HICL1- | 0 | 0.4 | Cable | 0.0072 | 0.056 | 0.48 | 158 | 146 | 146 | 146 | B-2-2a | 2025 | Addition
DOUN1- | LIMK1A | 0 | 0.9 | Cable | 0.01 | 0.058 | 1.389 | 306 | 253 | 253 | 253 | B-2-2a | 2025 | Addition
GLAG1Q | GLAG1S | 0 | 2.25 | Cable | 0.0671 | 0.133 | 3.356 | 160 | 145 | 145 | 145 | B-2-2a | 2025 | Addition
GLAG1R | GLAG1T | 0 | 2.25 | Cable | 0.0671 | 0.133 | 3.356 | 160 | 145 | 145 | 145 | B-2-2a | 2025 | Addition
GREM1J | GREM1L | 0 | 3.83 | Cable | 0.02 | 0.305 | 6.898 | 272 | 272 | 250 | 272 | B-2-2a | 2025 | Addition
GREM1K | GREM1N | 0 | 1.72 | Cable | 0.0106 | 0.1372 | 3.098 | 272 | 272 | 272 | 272 | B-2-2a | 2025 | Addition
GREM1M | GREM1N | 0 | 2.3 | Cable | 0.0141 | 0.1834 | 4.143 | 272 | 272 | 272 | 272 | B-2-2a | 2025 | Addition
GREM1P | GREM1Q | 0 | 0.93 | Cable | 0.0057 | 0.0742 | 1.675 | 272 | 272 | 272 | 272 | B-2-2a | 2025 | Addition
KERG1J | KERG1L | 0 | 5.85 | Cable | 0.0359 | 0.4662 | 10.53 | 272 | 272 | 272 | 272 | B-2-2a | 2025 | Addition
KERG1K | KERG1M | 0 | 5.85 | Cable | 0.0359 | 0.4662 | 10.53 | 272 | 272 | 272 | 272 | B-2-2a | 2025 | Addition
AIGN1- | AIGN1A | 0 | 0.43 | Cable | 0.0121 | 0.0381 | 0.569 | 149 | 137 | 137 | 137 | B-2-2a | 2027 | Addition
ALYT4J | ALYT4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
BLEX1- | BLEX1B | 0 | 3 | Cable | 0.0315 | 0.168 | 2.851 | 199 | 199 | 199 | 199 | B-2-2a | 2027 | Addition
BLEX1A | FAUG1J | 0 | 2.2 | Cable | 0.0231 | 0.1232 | 2.09 | 199 | 199 | 199 | 199 | B-2-2a | 2027 | Addition
CONN1D | CONN1K | 0 | 0.66 | Cable | 0.0138 | 0.0553 | 0.905 | 200 | 178 | 178 | 178 | B-2-2a | 2027 | Addition
CRSS1K | HICL1- | 0 | 0.4 | Cable | 0.0072 | 0.056 | 0.48 | 158 | 146 | 146 | 146 | B-2-2a | 2027 | Addition
CULL1A | CULL1Q | 0 | 0.43 | Cable | 0.0046 | 0.0274 | 0.664 | 149 | 137 | 137 | 137 | B-2-2a | 2027 | Addition
DEAW1- | DEAW1A | 0 | 3.8 | Cable | 0.1067 | 0.3362 | 5.031 | 149 | 137 | 137 | 137 | B-2-2a | 2027 | Addition
DELL1- | DELL1B | 0 | 7.4 | Cable | 0.1902 | 0.4122 | 5.212 | 127 | 127 | 127 | 127 | B-2-2a | 2027 | Addition
DELL1A | MELG1K | 0 | 0.7 | Cable | 0.018 | 0.039 | 0.493 | 127 | 127 | 127 | 127 | B-2-2a | 2027 | Addition
DOUN1- | OWFD1- | 0 | 1 | Cable | 0.0206 | 0.0849 | 1.349 | 190 | 147 | 147 | 147 | B-2-2a | 2027 | Addition
FETT4J | FETT4Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
FETT4J | FETT4R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
FOYE2- | FOYE2J | 0 | 0.8 | Cable | 0.0053 | 0.0152 | 3.23 | 319 | 319 | 319 | 319 | B-2-2a | 2027 | Change
GILB1J | GILB1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
GILB1J | GILB1L | 0 | 7.06 | Cable | 0.0419 | 0.5395 | 12.655 | 348 | 348 | 348 | 348 | B-2-2a | 2027 | Addition
GILB1J | MEYG1- | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
GILB1K | GILB1M | 0 | 7.06 | Cable | 0.0419 | 0.5395 | 12.655 | 348 | 348 | 348 | 348 | B-2-2a | 2027 | Addition
GLAG1Q | STNG1D | 0 | 2.21 | Cable | 0.0663 | 0.1304 | 3.094 | 124 | 114 | 114 | 114 | B-2-2a | 2027 | Addition
GLAG1R | STNG1C | 0 | 2.21 | Cable | 0.0663 | 0.1304 | 3.094 | 124 | 114 | 114 | 114 | B-2-2a | 2027 | Addition
KINT4J | KINT4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
KION1- | KION1A | 0 | 0.28 | Cable | 0.0079 | 0.0248 | 0.371 | 149 | 137 | 137 | 137 | B-2-2a | 2027 | Addition
MILC1R | STNG1B | 0 | 1.53 | Cable | 0.0813 | 0.1409 | 1.691 | 131 | 113 | 113 | 113 | B-2-2a | 2027 | Addition
MILC1V | STNG1A | 0 | 1.53 | Cable | 0.0813 | 0.1409 | 1.691 | 131 | 113 | 113 | 113 | B-2-2a | 2027 | Addition
STNG1A | STNG1E | 0 | 0.63 | Cable | 0.0189 | 0.0372 | 0.882 | 160 | 145 | 145 | 145 | B-2-2a | 2027 | Addition
STNG1B | STNG1E | 0 | 0.63 | Cable | 0.0189 | 0.0372 | 0.882 | 160 | 145 | 145 | 145 | B-2-2a | 2027 | Addition
STNG1C | STNG1E | 0 | 0.81 | Cable | 0.0243 | 0.0478 | 1.134 | 160 | 145 | 145 | 145 | B-2-2a | 2027 | Addition
STNG1D | STNG1E | 0 | 0.81 | Cable | 0.0243 | 0.0478 | 1.134 | 160 | 145 | 145 | 145 | B-2-2a | 2027 | Addition
STRW1A | STWO1- | 0 | 5 | Cable | 0.455 | 1.08 | 0.27 | 126 | 119 | 108 | 119 | B-2-2a | 2027 | Addition
STSO1A | STSO1B | 0 | 0.27 | Cable | 0.0056 | 0.0226 | 0.37 | 200 | 178 | 178 | 178 | B-2-2a | 2027 | Addition
THUS1J | THUS1L | 0 | 3.03 | Cable | 0.018 | 0.2316 | 5.431 | 348 | 348 | 348 | 348 | B-2-2a | 2027 | Addition
THUS1K | THUS1M | 0 | 3.03 | Cable | 0.018 | 0.2316 | 5.431 | 348 | 348 | 348 | 348 | B-2-2a | 2027 | Addition
WIOW1- | WIOW1Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
WIOW1- | WIOW1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
ALYT4J | ASBS4B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
ANSN2- | ERED2- | 0 | 0.6 | Cable | 0.0016 | 0.011 | 3.435 | 580 | 546 | 546 | 546 | B-2-2a | 2029 | Addition
BANN4J | BANN4K | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BANN4J | OWPL4- | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BEWF1- | SYEL1- | 0 | 1.5 | Cable | 0.0315 | 0.1265 | 2.054 | 206 | 206 | 206 | 206 | B-2-2a | 2029 | Addition
BLGH1- | CRDH1J | 0 | 10 | Cable | 0.91 | 2.16 | 0.54 | 126 | 119 | 108 | 119 | B-2-2a | 2029 | Addition
BLHI2A | BLHI2J | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BLHI2B | BLHI2K | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BREC1Q | FASQ1- | 0 | 4 | Cable | 0.065 | 0.334 | 6.245 | 176 | 176 | 176 | 176 | B-2-2a | 2029 | Addition
BROA1- | BROA1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BROA1- | BROA1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BROA1A | BROA1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BROA1B | BROA1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BROA1C | EDIN1C | 0 | 15 | Cable | 0.1481 | 1.2148 | 27.585 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
BROA1C | EDIN1C | 0 | 15 | Cable | 0.1481 | 1.2148 | 27.585 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
BROA1D | EDIN1D | 0 | 15 | Cable | 0.1481 | 1.2148 | 27.585 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
BROA1D | EDIN1D | 0 | 15 | Cable | 0.1481 | 1.2148 | 27.585 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
BROA1J | BROA1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
CLOI1A | MELG1K | 0 | 0.7 | Cable | 0.0093 | 0.0536 | 0.95 | 220 | 211 | 211 | 211 | B-2-2a | 2029 | Addition
CMBS4A | CMBS4B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
COST1- | COST1A | 0 | 2.6 | Cable | 0.0346 | 0.1992 | 4.3 | 292 | 292 | 292 | 292 | B-2-2a | 2029 | Addition
COST1A | ELIB1- | 0 | 11.5 | Cable | 0.575 | 2.3805 | 0.644 | 292 | 292 | 292 | 292 | B-2-2a | 2029 | Addition
CRDH1J | CRDH1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
CRDH2J | CRDH2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
CRMU2J | CRMU2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
CRSN1Q | CRSN1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
CRSN1Q | CRSS1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
CRSN1R | CRSS1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
CRSN2Q | CRSN2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
DOUN2A | DOUN2B | 0 | 0.79 | Cable | 0.0048 | 0.0255 | 2.87 | 292 | 292 | 292 | 292 | B-2-2a | 2029 | Addition
DOUN2B | DOUN2C | 0 | 1.85 | Cable | 0.0141 | 0.0459 | 5.201 | 294 | 294 | 294 | 294 | B-2-2a | 2029 | Addition
DOUN2C | FINS2C | 0 | 48.3 | Cable | 0.5558 | 1.3971 | 104.968 | 231 | 231 | 231 | 231 | B-2-2a | 2029 | Addition
EDIN1A | EDIN1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
EDIN1B | EDIN1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
EDIN1J | EDIN1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
EDIN1J | GLUE1- | 0 | 2.8 | Cable | 0.0166 | 0.214 | 5.019 | 348 | 348 | 348 | 348 | B-2-2a | 2029 | Addition
EDIN1K | EDIN1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
ELIB1A | FINS1- | 0 | 3.1 | Cable | 0.0502 | 0.318 | 4.584 | 208 | 187 | 187 | 187 | B-2-2a | 2029 | Addition
ENEI1- | ENEI1N | 0 | 1 | Cable | 0.0133 | 0.0766 | 1.654 | 250 | 250 | 250 | 250 | B-2-2a | 2029 | Addition
FASN1A | FASN1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
FAUG1- | FAUG1R | 0 | 9 | Cable | 0.0889 | 0.7289 | 16.551 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
FAUG1- | FAUG1R | 0 | 9 | Cable | 0.0889 | 0.7289 | 16.551 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
FAUG1- | FAUG1S | 0 | 9 | Cable | 0.0889 | 0.7289 | 16.551 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
FAUG1- | FAUG1S | 0 | 9 | Cable | 0.0889 | 0.7289 | 16.551 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
FETT4J | FETT4K | 0 | 1 | Cable | 0 | 0.01 | 0 | 100 | 100 | 100 | 100 | B-2-2a | 2029 | Addition
FETT4K | FETT4R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
FINS2A | FINS2B | 0 | 13.61 | Cable | 0.0827 | 0.4387 | 49.435 | 292 | 292 | 292 | 292 | B-2-2a | 2029 | Addition
FINS2B | FINS2C | 0 | 2.2 | Cable | 0.0167 | 0.0545 | 6.185 | 294 | 294 | 294 | 294 | B-2-2a | 2029 | Addition
GRNV4- | NEDE4J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
KERG1A | KERG1W | 0 | 4 | Cable | 0.0246 | 0.319 | 7.205 | 272 | 272 | 272 | 272 | B-2-2a | 2029 | Addition
KERG1A | SYEL1A | 0 | 12 | Cable | 0.4007 | 0.7573 | 16.422 | 189 | 189 | 189 | 189 | B-2-2a | 2029 | Addition
KERG1B | KERG1W | 0 | 4 | Cable | 0.0246 | 0.319 | 7.205 | 272 | 272 | 272 | 272 | B-2-2a | 2029 | Addition
KERG1B | SYEL1B | 0 | 12 | Cable | 0.4007 | 0.7573 | 16.422 | 189 | 189 | 189 | 189 | B-2-2a | 2029 | Addition
KERG1K | KERG1N | 0 | 0.35 | Cable | 0.0021 | 0.0279 | 0.63 | 272 | 272 | 272 | 272 | B-2-2a | 2029 | Addition
KERG1N | KERG1U | 0 | 3 | Cable | 0.1551 | 0.651 | 0.158 | 295 | 295 | 295 | 295 | B-2-2a | 2029 | Addition
KERG1U | KERG1V | 0 | 2 | Cable | 0.0123 | 0.1595 | 3.602 | 272 | 272 | 272 | 272 | B-2-2a | 2029 | Addition
KERG1V | KERG1W | 0 | 12.5 | Cable | 0.6463 | 2.7125 | 0.659 | 295 | 295 | 295 | 295 | B-2-2a | 2029 | Addition
KINA4A | KINA4B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
KINM2A | KINM2C | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
KINM2B | KINM2C | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
LOCL1J | LOCL1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
LOCL4J | LOCL4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
PEHE4J | PEHE4L | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
SALM1A | SALM1C | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
SALM1B | SALM1C | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
STCS1A | STCS1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
STCS1A | STRW1A | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
STCS1B | STSO1A | 0 | 6 | Cable | 0.1181 | 0.1733 | 4.7 | 251 | 252 | 252 | 252 | B-2-2a | 2029 | Addition
SYEL1- | SYEL1M | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
SYEL1- | SYEL1N | 0 | 2.5 | Cable | 0.0333 | 0.1915 | 4.135 | 250 | 250 | 250 | 250 | B-2-2a | 2029 | Addition
SYEL1A | SYEL1M | 0 | 2 | Cable | 0.0123 | 0.1595 | 3.602 | 272 | 272 | 272 | 272 | B-2-2a | 2029 | Addition
SYEL1B | SYEL1M | 0 | 2 | Cable | 0.0123 | 0.1595 | 3.602 | 272 | 272 | 272 | 272 | B-2-2a | 2029 | Addition
BALA1A | BALA1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
BANN4J | BANN4R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
CAAI4J | CAAI4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
CAID2- | KNOC2N | 0 | 6 | Cable | 0.0465 | 0.1721 | 34.121 | 930 | 900 | 900 | 900 | B-2-2a | 2032 | Addition
CALD4- | GRNS4M | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
CLGO2- | KNOC2P | 0 | 6 | Cable | 0.0465 | 0.1721 | 34.121 | 930 | 900 | 900 | 900 | B-2-2a | 2032 | Addition
COFD4A | COFD4B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
DUBE1A | DUBE1Q | 0 | 4 | Cable | 0.1457 | 0.3676 | 4.74 | 152 | 140 | 140 | 140 | B-2-2a | 2032 | Addition
DUBE1B | DUBE1C | 0 | 4 | Cable | 0.1457 | 0.3676 | 4.74 | 152 | 140 | 140 | 140 | B-2-2a | 2032 | Addition
EDAY1A | EDAY1B | 0 | 18.6 | Cable | 0.5877 | 1.1107 | 24.085 | 189 | 189 | 189 | 189 | B-2-2a | 2032 | Addition
EDIN1J | GLUE1- | 0 | 2.8 | Cable | 0.0166 | 0.214 | 5.019 | 348 | 348 | 348 | 348 | B-2-2a | 2032 | Addition
EMMO4J | EMMO4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
FAUG2T | LHEU2- | 0 | 6 | Cable | 0.0099 | 0.1626 | 70 | 1100 | 1100 | 1100 | 1100 | B-2-2a | 2032 | Addition
FNLN4A | FNLN4B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
FNLN4B | FNLN4R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
FOYE2- | LKEM2- | 0 | 10.5 | Cable | 0.0285 | 0.1919 | 60.12 | 580 | 546 | 546 | 546 | B-2-2a | 2032 | Addition
FYRI2J | FYRI2M | 0 | 1.5 | Cable | 0.0116 | 0.043 | 8.53 | 930 | 900 | 900 | 900 | B-2-2a | 2032 | Addition
FYRI2K | FYRI2L | 0 | 1.5 | Cable | 0.0116 | 0.043 | 8.53 | 930 | 900 | 900 | 900 | B-2-2a | 2032 | Addition
GRNS4L | GRNS4M | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
GRNS4L | NEDE4J | 0 | 3 | Cable | 0.002 | 0.0164 | 33.651 | 1300 | 1235 | 1235 | 1235 | B-2-2a | 2032 | Addition
GRNS4L | NEDE4J | 0 | 3 | Cable | 0.002 | 0.0164 | 33.651 | 1300 | 1235 | 1235 | 1235 | B-2-2a | 2032 | Addition
GRNS4M | NEDE4K | 0 | 3 | Cable | 0.002 | 0.0164 | 33.651 | 1300 | 1235 | 1235 | 1235 | B-2-2a | 2032 | Addition
HURL4A | HURL4B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
KEIT1- | KEIT1M | 0 | 4.5 | Cable | 0.0591 | 0.3694 | 7.389 | 265 | 263 | 263 | 263 | B-2-2a | 2032 | Addition
KEIT1- | KEIT1N | 0 | 4.5 | Cable | 0.0591 | 0.3694 | 7.389 | 265 | 263 | 263 | 263 | B-2-2a | 2032 | Addition
KINA4A | KINA4B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
KINT2J | KINT2L | 0 | 1.5 | Cable | 0.0116 | 0.043 | 8.53 | 930 | 900 | 900 | 900 | B-2-2a | 2032 | Addition
KINT2K | KINT2M | 0 | 1.5 | Cable | 0.0116 | 0.043 | 8.53 | 930 | 900 | 900 | 900 | B-2-2a | 2032 | Addition
KNOC2J | KNOC2L | 0 | 1 | Cable | 0.0078 | 0.0287 | 5.687 | 930 | 900 | 900 | 900 | B-2-2a | 2032 | Addition
KNOC2J | REJO2A | 0 | 9 | Cable | 0.024 | 0.165 | 51.532 | 580 | 546 | 546 | 546 | B-2-2a | 2032 | Addition
KNOC2K | KNOC2M | 0 | 1 | Cable | 0.0078 | 0.0287 | 5.687 | 930 | 900 | 900 | 900 | B-2-2a | 2032 | Addition
KNOC2K | REJO2B | 0 | 9 | Cable | 0.024 | 0.165 | 51.532 | 580 | 546 | 546 | 546 | B-2-2a | 2032 | Addition
LEWI1J | LEWI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
LEWI4- | LEWI4J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
LEWI4J | LEWI4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
LEWI4J | LEWI4R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
LEWI4K | NPIC4- | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
LEWI4K | TLSK4- | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
LOCB2J | LOCB2M | 1 | 0 | Cable | 0.0078 | 0.0287 | 5.687 | 930 | 900 | 900 | 900 | B-2-2a | 2032 | Addition
LOCB2K | LOCB2L | 1 | 0 | Cable | 0.0078 | 0.0287 | 5.687 | 930 | 900 | 900 | 900 | B-2-2a | 2032 | Addition
LOSD1A | LOSD1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
LOSD4A | LOSD4B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
LOSD4A | LOSD4R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
LOSD4A | MARA4- | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2032 | Addition
SHIN1- | SHIN1A | 0 | 2.25 | Cable | 0.082 | 0.2068 | 2.666 | 152 | 140 | 140 | 140 | B-2-2a | 2032 | Addition
SHIN1- | SHIN1B | 0 | 2.25 | Cable | 0.082 | 0.2068 | 2.666 | 152 | 140 | 140 | 140 | B-2-2a | 2032 | Addition
AYRS4- | HBES4- | 0 | 0.1 | Cable | 0.0001 | 0.0013 | 1.1119 | 2770 | 2770 | 2770 | 2770 | B-2-2b | 2025 | Addition
AYRS4- | HESF4- | 0 | 0.1 | Cable | 0.0001 | 0.0013 | 1.1119 | 2770 | 2770 | 2770 | 2770 | B-2-2b | 2025 | Addition
AYRS4- | HUNE4- | 0 | 0.9 | Cable | 0.0005 | 0.012 | 10.0073 | 1247 | 1247 | 1247 | 1247 | B-2-2b | 2025 | Addition
BLAH3B | PLOE3- | 0 | 1.01 | Cable | 0.2795 | 0.8831 | 0.1185 | 40 | 38 | 38 | 38 | B-2-2b | 2025 | Addition
BLAH3B | PLOE3- | 0 | 1.01 | Cable | 0.2795 | 0.8831 | 0.1185 | 40 | 38 | 38 | 38 | B-2-2b | 2025 | Addition
COAB4- | COAL4- | 0 | 2.5 | Cable | 0.0017 | 0.032 | 27.7981 | 1247 | 1247 | 1247 | 1247 | B-2-2b | 2025 | Addition
DONO3A | DWEX3- | 0 | 4 | Cable | 0.5534 | 1.7488 | 0.9388 | 40 | 38 | 38 | 38 | B-2-2b | 2025 | Addition
FIGS2- | KINC2- | 0 | 0.7 | Cable | 0.0018 | 0.0075 | 5.395 | 352 | 352 | 352 | 352 | B-2-2b | 2025 | Addition
GLGL1- | SANQ1- | 0 | 4 | Cable | 0.0629 | 0.3444 | 6.5906 | 283 | 277 | 269 | 277 | B-2-2b | 2025 | Addition
HOLM1- | HOLM1T | 0 | 0.28 | Cable | 0.0025 | 0.0233 | 0.5242 | 293 | 293 | 293 | 293 | B-2-2b | 2025 | Addition
HUCR4- | HUNE4- | 0 | 0.4 | Cable | 0.0002 | 0.0053 | 4.4477 | 1247 | 1247 | 1247 | 1247 | B-2-2b | 2025 | Addition
HUNE1- | HUNF1Q | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 146 | 146 | 146 | B-2-2b | 2025 | Addition
HUNE1- | HUNF1R | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 146 | 146 | 146 | B-2-2b | 2025 | Addition
HUNE1- | JUNA1T | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 175 | 175 | 175 | B-2-2b | 2025 | Addition
NECU1B | OHLL1- | 0 | 3 | Cable | 0.0534 | 0.2861 | 3.5006 | 180 | 180 | 180 | 180 | B-2-2b | 2025 | Addition
NECU1C | SOKY1- | 0 | 4.5 | Cable | 0.0458 | 0.2435 | 7.265 | 242 | 223 | 192 | 223 | B-2-2b | 2025 | Change
ARCR2- | MAHI2- | 0 | 9.5 | Cable | 0.0488 | 0.2034 | 36.6087 | 352 | 352 | 352 | 352 | B-2-2b | 2027 | Addition
COAN4- | COBA4- | 0 | 2.5 | Cable | 0.0017 | 0.032 | 27.7981 | 1247 | 1247 | 1247 | 1247 | B-2-2b | 2027 | Addition
HARE1- | MOFF1- | 0 | 15.33 | Cable | 0.3071 | 0.8622 | 21.8179 | 184 | 184 | 184 | 184 | B-2-2b | 2027 | Change
AREX1- | AREX1A | 0 | 1.7 | Cable | 0.048 | 0.1103 | 2.0938 | 181 | 164 | 164 | 164 | B-2-2b | 2029 | Change
BLCW3- | BLKS3- | 0 | 2.801 | Cable | 0.3875 | 1.2246 | 0.6574 | 35 | 35 | 35 | 35 | B-2-2b | 2029 | Change
BRNX4- | BRNX4A | 0 | 0.25 | Cable | 0 | 0 | 0 | 2770 | 2770 | 2770 | 2770 | B-2-2b | 2029 | Addition
BRNX4- | TORN4- | 0 | 1.94 | Cable | 0.0005 | 0.013 | 43.1426 | 945 | 800 | 800 | 800 | B-2-2b | 2029 | Addition
BRNX4- | TORN4- | 0 | 2.1 | Cable | 0.0005 | 0.014 | 46.7008 | 1040 | 900 | 900 | 900 | B-2-2b | 2029 | Addition
BRNX4Q | TORN4- | 0 | 1.97 | Cable | 0.002 | 0.0326 | 38.612 | 935 | 785 | 785 | 785 | B-2-2b | 2029 | Addition
BRNX4R | TORN4- | 0 | 1.94 | Cable | 0.0019 | 0.0321 | 38.024 | 900 | 760 | 760 | 760 | B-2-2b | 2029 | Addition
BROC1- | BROT1- | 0 | 0.22 | Cable | 0.0044 | 0.0183 | 0.3167 | 234 | 234 | 234 | 234 | B-2-2b | 2029 | Change
BUSB2- | WLER2- | 0 | 12 | Cable | 0.0372 | 0.2829 | 51.3179 | 450 | 450 | 450 | 450 | B-2-2b | 2029 | Addition
CCSS1- | COAL1B | 0 | 6.97 | Cable | 0.1096 | 0.6 | 11.4841 | 241 | 241 | 241 | 241 | B-2-2b | 2029 | Change
CCSS1- | GAWH1Q | 0 | 2.6 | Cable | 0.0409 | 0.2238 | 4.2839 | 241 | 241 | 241 | 241 | B-2-2b | 2029 | Change
CCSS3- | CUMH3- | 0 | 2.3 | Cable | 0.3182 | 1.0055 | 0.5398 | 38 | 38 | 38 | 38 | B-2-2b | 2029 | Change
CLAU1- | MAHI1C | 0 | 4 | Cable | 0.0583 | 0.3646 | 5.0764 | 161 | 161 | 161 | 161 | B-2-2b | 2029 | Change
CLAW1- | NECU1- | 0 | 2.21 | Cable | 0.0438 | 0.2004 | 3.0848 | 133 | 133 | 133 | 133 | B-2-2b | 2029 | Change
COAL1A | LEGO1Q | 0 | 4 | Cable | 0.1129 | 0.2596 | 4.9265 | 134 | 123 | 123 | 123 | B-2-2b | 2029 | Addition
COAL1A | LEGO1R | 0 | 4 | Cable | 0.1129 | 0.2596 | 4.9265 | 134 | 123 | 123 | 123 | B-2-2b | 2029 | Addition
COAL1B | CUMW1- | 0 | 11.1 | Cable | 0.3134 | 0.7205 | 14.5825 | 122 | 107 | 107 | 107 | B-2-2b | 2029 | Change
COAL1B | DONO1- | 0 | 4.806 | Cable | 0.0662 | 0.3007 | 6.9978 | 165 | 165 | 165 | 165 | B-2-2b | 2029 | Change
DEBS2- | LOAN2- | 0 | 5 | Cable | 0.0102 | 0.1381 | 30.4106 | 820 | 736 | 674 | 736 | B-2-2b | 2029 | Addition
DONO1- | MIDM1- | 0 | 1.065 | Cable | 0.0208 | 0.0978 | 1.4807 | 211 | 211 | 211 | 211 | B-2-2b | 2029 | Addition
DUNB1Q | DUNB1S | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 133 | 133 | 133 | 133 | B-2-2b | 2029 | Change
DUNB1R | DUNB1T | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 133 | 133 | 133 | 133 | B-2-2b | 2029 | Change
DUNE3- | KEIH3- | 0 | 4.746 | Cable | 5.1628 | 4.7962 | 0.3798 | 23 | 23 | 23 | 23 | B-2-2b | 2029 | Change
DUNE3- | POGB3- | 0 | 3.809 | Cable | 4.4533 | 3.8497 | 0.3048 | 57 | 57 | 57 | 57 | B-2-2b | 2029 | Change
ELDE1Q | JOHN1Q | 0 | 4.37 | Cable | 0.1229 | 0.4314 | 4.832 | 1 | 1 | 1 | 1 | B-2-2b | 2029 | Change
ELDE1R | JOHN1R | 0 | 4.37 | Cable | 0.1229 | 0.4314 | 4.832 | 1 | 1 | 1 | 1 | B-2-2b | 2029 | Change
GHPS1- | LETH1- | 0 | 3 | Cable | 0.0404 | 0.2597 | 9.3604 | 229 | 229 | 229 | 229 | B-2-2b | 2029 | Change
GLGL1B | SAKN1- | 0 | 9 | Cable | 0.2541 | 0.5842 | 11.0847 | 181 | 164 | 164 | 164 | B-2-2b | 2029 | Change
GLGL1B | SANQ1- | 0 | 4 | Cable | 0.0629 | 0.3444 | 6.5906 | 241 | 241 | 241 | 241 | B-2-2b | 2029 | Change
GLGL3- | GLMU3- | 0 | 10 | Cable | 2.7669 | 8.7439 | 1.1735 | 40 | 38 | 38 | 38 | B-2-2b | 2029 | Addition
GORG1Q | TELR1Q | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 72 | 72 | 72 | 72 | B-2-2b | 2029 | Change
GORG1R | TELR1R | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 72 | 72 | 72 | 72 | B-2-2b | 2029 | Change
HUCS4- | HUNE4- | 0 | 0.675 | Cable | 0.0003 | 0.009 | 7.5055 | 1448 | 1448 | 1448 | 1448 | B-2-2b | 2029 | Change
INWI1Q | TORN1- | 0 | 1.15 | Cable | 0.038 | 0.061 | 2.365 | 110 | 110 | 110 | 110 | B-2-2b | 2029 | Change
INWI1R | TORN1- | 0 | 1.12 | Cable | 0.038 | 0.061 | 2.365 | 110 | 110 | 110 | 110 | B-2-2b | 2029 | Change
KINC2- | KINN2B | 0 | 1.9 | Cable | 0.0023 | 0.0168 | 17.1535 | 403 | 403 | 403 | 403 | B-2-2b | 2029 | Change
NECU1C | NOKY1- | 0 | 1.3 | Cable | 0.0084 | 0.0773 | 2.2771 | 242 | 242 | 242 | 242 | B-2-2b | 2029 | Change
NEIL2- | NEIL2D | 0 | 0.2 | Cable | 0.0002 | 0.0028 | 2.4328 | 820 | 736 | 674 | 736 | B-2-2b | 2029 | Change
NETH3- | WISH3T | 0 | 0.98 | Cable | 0.1354 | 0.45 | 0.2253 | 29 | 29 | 29 | 29 | B-2-2b | 2029 | Change
CRUA2S | CRUA2A | 0 | 0.4 | Cable | 0.0021 | 0.0086 | 1.5414 | 352 | 352 | 352 | 352 | B-2-2b | 2032 | Addition
CRUA2T | CRUA2B | 0 | 0.4 | Cable | 0.0021 | 0.0086 | 1.5414 | 352 | 352 | 352 | 352 | B-2-2b | 2032 | Addition
HAZE1T | REDS1A | 0 | 7.48 | Cable | 0.5334 | 1.5447 | 1.3203 | 112 | 112 | 112 | 112 | B-2-2b | 2032 | Addition
WFIE4- | WFIE4A | 0 | 0.1 | Cable | 0 | 0 | 0 | 2770 | 2770 | 2770 | 2770 | B-2-2b | 2032 | Addition
BENR41 | NEWX41 | 0 | 4.272 | Cable | 0.0029 | 0.0571 | 34.5413 | 1100 | 1100 | 1100 | 1100 | B-2-2c | 2025 | Addition
BENR41 | WIMB41 | 0 | 8.429 | Cable | 0.0058 | 0.1128 | 68.1528 | 1250 | 1250 | 1250 | 1250 | B-2-2c | 2025 | Addition
NEWX41 | WIMB41 | 0 | 12.688 | Cable | 0.0087 | 0.1697 | 102.5891 | 1100 | 1100 | 1100 | 1100 | B-2-2c | 2025 | Addition
CREB41 | CREB41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 1386 | 1386 | 1386 | 1386 | B-2-2c | 2027 | Addition
CREB41 | CREB41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 1386 | 1386 | 1386 | 1386 | B-2-2c | 2027 | Addition
HURS21 | NEWX21 | 0 | 18.442 | Cable | 0.0269 | 0.5219 | 70.4793 | 1200 | 1200 | 1200 | 1200 | B-2-2c | 2027 | Change
PITS21 | WIBA21 | 0 | 2.324 | Cable | 0.0036 | 0.0621 | 13.8036 | 530 | 530 | 445 | 530 | B-2-2c | 2027 | Change
TEMP22 | WIBA21 | 0 | 3.607 | Cable | 0.0055 | 0.0964 | 21.424 | 530 | 530 | 530 | 530 | B-2-2c | 2027 | Change
DINO41 | PENI4A | 0 | 7.31 | Cable | 0.0051 | 0.0804 | 146.1 | 1623 | 1623 | 1571 | 1571 | B-2-2c | 2029 | Addition
ELST41 | SJOW41 | 0 | 20 | Cable | 0.014 | 0.176 | 244.29 | 1767 | 2640 | 2640 | 2640 | B-2-2c | 2029 | Addition
ELST4A | ELST41 | 0 | 0.1 | Cable | 0 | 0 | 0 | 1590 | 1500 | 1346 | 1500 | B-2-2c | 2029 | Addition

## OHL
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
ABNE1Q | CHAR1- | 24.5 | 0 | OHL | 2.49 | 5.66 | 1.22 | 132 | 123 | 106 | 123 | B-2-1a
ALYT2A | FETT2P | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030 | B-2-1a
ALYT2A | KINB2J | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030 | B-2-1a
ALYT2A | TEAL2J | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030 | B-2-1a
ALYT2B | FETT2Q | 67.35 | 0 | OHL | 0.3046 | 2.7955 | 18.318 | 1090 | 1030 | 925 | 1030 | B-2-1a
ALYT2B | KINB2K | 69.98 | 0 | OHL | 0.3165 | 2.9046 | 19.034 | 1090 | 1030 | 925 | 1030 | B-2-1a
ALYT2B | TEAL2K | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030 | B-2-1a
AMUL1E | BUMU1R | 17.8 | 0 | OHL | 1.8184 | 4.1692 | 0.885 | 132 | 123 | 106 | 123 | B-2-1a
AMUL1F | GRIF1S | 6.85 | 0 | OHL | 0.7002 | 1.6054 | 0.341 | 132 | 123 | 106 | 123 | B-2-1a
AMUL1H | GRIF1T | 6.85 | 0 | OHL | 0.7002 | 1.6054 | 0.341 | 132 | 123 | 106 | 123 | B-2-1a
ANSU1- | INVE1K | 11.35 | 0 | OHL | 0.1816 | 2.009 | 0.738 | 739 | 710 | 662 | 710 | B-2-1a
ANSU1- | PORA1R | 24.95 | 0 | OHL | 0.3992 | 4.4162 | 1.622 | 739 | 710 | 662 | 710 | B-2-1a
ARBR1Q | DENS1Q | 14.5 | 0 | OHL | 1.3195 | 3.364 | 0.725 | 132 | 123 | 106 | 123 | B-2-1a
ARBR1R | DENS1R | 14.5 | 0 | OHL | 1.3195 | 3.364 | 0.725 | 132 | 123 | 106 | 123 | B-2-1a
ARDK1- | SLOY1T | 0 | 10 | OHL | 1.02 | 2.33 | 0.49 | 132 | 123 | 106 | 123 | B-2-1a
BEAU1J | CULL1Q | 14 | 0 | OHL | 1.43 | 3.28 | 0.69 | 126 | 117 | 101 | 117 | B-2-1a
BEAU1L | MOTA1R | 29.67 | 0 | OHL | 3.0145 | 6.9027 | 1.469 | 126 | 117 | 101 | 117 | B-2-1a
BEAU1M | MOTA1Q | 29.67 | 0 | OHL | 3.0145 | 6.9027 | 1.469 | 132 | 123 | 106 | 123 | B-2-1a
BEAU1N | KNOC1J | 17.1 | 0 | OHL | 1.5561 | 3.9843 | 0.855 | 132 | 123 | 106 | 123 | B-2-1a
BEAU1R | INNE1Q | 13.4 | 0 | OHL | 0.6834 | 3.0016 | 0.697 | 241 | 230 | 210 | 230 | B-2-1a
BEAU1S | INNE1R | 13.4 | 0 | OHL | 0.6834 | 3.0016 | 0.697 | 241 | 230 | 210 | 230 | B-2-1a
BEAU1T | KNOC1J | 17.1 | 0 | OHL | 1.5561 | 3.9843 | 0.855 | 132 | 123 | 106 | 123 | B-2-1a
BEAU2J | KNOC2L | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 935 | 880 | 790 | 880 | B-2-1a
BEAU2K | KNOC2M | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 935 | 880 | 790 | 880 | B-2-1a
BEAU4- | FAUG4J | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2780 | 2670 | 2480 | 2670 | B-2-1a
BEIN11 | CEAN1Q | 0.87 | 0 | OHL | 0.099 | 0.205 | 0.042 | 263 | 257 | 248 | 257 | B-2-1a
BEIN11 | MILW1S | 2.8 | 0 | OHL | 0.319 | 0.66 | 0.135 | 263 | 257 | 248 | 257 | B-2-1a
BERB2Q | BLHI2J | 46.26 | 0 | OHL | 0.2619 | 1.9044 | 12.613 | 935 | 880 | 790 | 880 | B-2-1a
BERB2Q | KNOC2J | 46.98 | 0 | OHL | 0.266 | 1.934 | 12.809 | 935 | 880 | 790 | 880 | B-2-1a
BIHI1Q | CHAR1R | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229 | 211 | 183 | 211 | B-2-1a
BIHI1Q | COUA1Q | 14.6 | 0 | OHL | 0.7446 | 3.2704 | 0.753 | 241 | 230 | 210 | 230 | B-2-1a
BIHI1Q | TEAL1- | 5.6 | 0 | OHL | 0.239 | 1.199 | 0.29 | 229 | 211 | 183 | 211 | B-2-1a
BIHI1R | CHAR1- | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229 | 211 | 183 | 211 | B-2-1a
BIHI1R | COUA1R | 14.6 | 0 | OHL | 0.7446 | 3.2704 | 0.753 | 241 | 230 | 210 | 230 | B-2-1a
BIHI1R | TEAL1- | 5.6 | 0 | OHL | 0.239 | 1.199 | 0.29 | 229 | 211 | 183 | 211 | B-2-1a
BLHI1J | DORE11 | 23.45 | 0 | OHL | 1.171 | 5.295 | 1.286 | 241 | 230 | 210 | 230 | B-2-1a
BLHI1K | DORE12 | 23.45 | 0 | OHL | 1.171 | 5.297 | 1.318 | 241 | 230 | 210 | 230 | B-2-1a
BLHI2J | KINT2K | 50.85 | 0 | OHL | 0.298 | 2.08 | 14.14 | 935 | 880 | 790 | 880 | B-2-1a
BLHI2K | CAIN2- | 9.77 | 0 | OHL | 0.0573 | 0.3997 | 2.717 | 935 | 880 | 790 | 880 | B-2-1a
BLHI2K | DAAS2- | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880 | B-2-1a
BLHI4- | ROTI4J | 35.4 | 0 | OHL | 0.0708 | 0.6832 | 20.826 | 2000 | 1920 | 1790 | 1920 | B-2-1a
BLHI4- | ROTI4K | 35.4 | 0 | OHL | 0.0708 | 0.6832 | 20.826 | 2000 | 1920 | 1790 | 1920 | B-2-1a
BOAG1L | TOMT1L | 19.19 | 0 | OHL | 2.1877 | 4.3562 | 0.96 | 215 | 211 | 203 | 211 | B-2-1a
BOAG1M | TOMT1M | 19.19 | 0 | OHL | 2.1877 | 4.3562 | 0.96 | 215 | 211 | 203 | 211 | B-2-1a
BONB2J | BRCW2K | 10.1 | 0 | OHL | 0.028 | 0.409 | 2.886 | 1910 | 1830 | 1710 | 1830 | B-2-1a
BONB4- | TUMM4- | 72.9 | 0 | OHL | 0.094 | 1.396 | 44.078 | 2780 | 2670 | 2480 | 2670 | B-2-1a
BRCW2J | KINA2K | 59.8 | 0 | OHL | 0.1638 | 2.4224 | 17.089 | 1910 | 1830 | 1710 | 1830 | B-2-1a
BREC1Q | BRID1Q | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104 | B-2-1a
BREC1Q | FIDD1B | 30.4 | 0 | OHL | 3.13 | 6.52 | 2.66 | 112 | 104 | 90 | 104 | B-2-1a
BREC1R | BRID1R | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104 | B-2-1a
BREC1R | DENS1Q | 26.1 | 0 | OHL | 3.08 | 6.33 | 1.29 | 112 | 104 | 90 | 104 | B-2-1a
BROA1Q | EDIN1- | 44.9 | 0 | OHL | 6.014 | 9.963 | 2.332 | 99 | 92 | 79 | 92 | B-2-1a
BROA1Q | QUOI1Q | 63.4 | 0 | OHL | 8.99 | 14.87 | 3.11 | 99 | 92 | 79 | 92 | B-2-1a
BROR1- | BROR1Q | 1.1 | 0 | OHL | 0.1004 | 0.2561 | 0.0546 | 126 | 117 | 101 | 117 | B-2-1a
BROR1Q | DUBE1Q | 38.58 | 0 | OHL | 3.522 | 8.9813 | 1.914 | 126 | 117 | 101 | 117 | B-2-1a
BROR1Q | LOCB1T | 25.88 | 0 | OHL | 2.3626 | 6.0248 | 1.2842 | 126 | 117 | 101 | 117 | B-2-1a
CAAD1Q | CRSS1J | 13.08 | 0 | OHL | 0.3091 | 2.7749 | 0.721 | 448 | 430 | 398 | 430 | B-2-1a
CAAD1R | CRSS1K | 13.08 | 0 | OHL | 0.3091 | 2.7749 | 0.721 | 448 | 430 | 398 | 430 | B-2-1a
CAIN2- | KINT2J | 41.08 | 0 | OHL | 0.2407 | 1.6803 | 11.423 | 935 | 880 | 790 | 880 | B-2-1a
CASS1Q | DLCH1A | 28 | 0 | OHL | 2.562 | 6.09 | 1.2 | 111 | 103 | 89 | 103 | B-2-1a
CHAR1S | LYND1Q | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117 | B-2-1a
CHAR1T | LYND1R | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117 | B-2-1a
CLAC1Q | INVE1J | 8.4 | 0 | OHL | 0.85 | 1.95 | 0.41 | 126 | 117 | 101 | 117 | B-2-1a
CLAC1Q | SLOY1F | 13.05 | 0 | OHL | 1.1875 | 3.0406 | 0.653 | 132 | 123 | 106 | 123 | B-2-1a
CLUN1S | COUA1Q | 38.1 | 0 | OHL | 1.9301 | 8.5468 | 1.966 | 241 | 230 | 210 | 230 | B-2-1a
CLUN1T | COUA1R | 38.1 | 0 | OHL | 1.9301 | 8.5468 | 1.966 | 241 | 230 | 210 | 230 | B-2-1a
COGA1- | COGA1C | 13.9 | 0 | OHL | 0.7002 | 2.8782 | 0.778 | 241 | 230 | 210 | 230 | B-2-1a
CONN1C | STRW1A | 12 | 0 | OHL | 0.605 | 2.485 | 0.672 | 241 | 230 | 210 | 230 | B-2-1a
CORI1J | LUIC1Q | 10.43 | 0 | OHL | 0.2443 | 2.2748 | 0.551 | 464 | 446 | 414 | 446 | B-2-1a
CORI1K | LUIC1R | 10.35 | 0 | OHL | 0.2425 | 2.2577 | 0.547 | 464 | 446 | 414 | 446 | B-2-1a
CORI1P | MOSS1S | 1.45 | 0 | OHL | 0.074 | 0.3248 | 0.075 | 224 | 211 | 189 | 211 | B-2-1a
CORI1Q | MOSS1T | 1.45 | 0 | OHL | 0.074 | 0.3248 | 0.075 | 224 | 211 | 189 | 211 | B-2-1a
CRAI1- | FOGG1Q | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 132 | 123 | 106 | 123 | B-2-1a
CRAI1- | FOGG1R | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 132 | 123 | 106 | 123 | B-2-1a
CRAI1- | REDM1R | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146 | B-2-1a
CRAI1P | KINT1P | 17.5 | 0 | OHL | 0.8925 | 3.92 | 0.903 | 241 | 230 | 210 | 230 | B-2-1a
CRAI1Q | REDM1Q | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146 | B-2-1a
CRAI1R | KINT1R | 17.5 | 0 | OHL | 0.8925 | 3.92 | 0.903 | 241 | 230 | 210 | 230 | B-2-1a
CRAR1R | INVE1J | 22.58 | 0 | OHL | 0.3613 | 3.9967 | 1.468 | 739 | 710 | 662 | 710 | B-2-1a
CRAR1R | PORA1S | 13.72 | 0 | OHL | 0.2195 | 2.4284 | 0.892 | 739 | 710 | 662 | 710 | B-2-1a
CREA1- | CREA1B | 4 | 0 | OHL | 0.2 | 0.828 | 0.224 | 203 | 193 | 176 | 193 | B-2-1a
CREA1A | DLCH1B | 16.6 | 0 | OHL | 0.83 | 3.4362 | 0.93 | 203 | 193 | 176 | 193 | B-2-1a
CRSS1Q | PORA1R | 44.7 | 0 | OHL | 0.7152 | 7.9119 | 2.905 | 739 | 710 | 662 | 710 | B-2-1a
CRSS1R | PORA1S | 44.7 | 0 | OHL | 0.7152 | 7.9119 | 2.905 | 739 | 710 | 662 | 710 | B-2-1a
CULL1Q | DEAN1Q | 9 | 0 | OHL | 0.93 | 2.12 | 0.45 | 126 | 117 | 101 | 117 | B-2-1a
DAAS2- | KNOC2K | 60.22 | 0 | OHL | 0.341 | 2.479 | 16.419 | 935 | 880 | 790 | 880 | B-2-1a
DENS1Q | TEAL1- | 8.7 | 0 | OHL | 0.3393 | 1.9053 | 0.461 | 183 | 160 | 149 | 160 | B-2-1a
DENS1R | TEAL1- | 8.7 | 0 | OHL | 0.3393 | 1.9053 | 0.461 | 183 | 160 | 149 | 160 | B-2-1a
DLCH1A | LOCB1L | 17 | 0 | OHL | 0.3992 | 3.7085 | 0.898 | 464 | 446 | 414 | 446 | B-2-1a
DLCH1B | LOCB1M | 17 | 0 | OHL | 0.3992 | 3.7085 | 0.898 | 464 | 446 | 414 | 446 | B-2-1a
DOUN2- | GORW2- | 58.1 | 0 | OHL | 0.3486 | 3.196 | 12.32 | 702 | 665 | 599 | 665 | B-2-1a
DOUN2- | THUS2J | 15.4 | 0 | OHL | 0.077 | 0.847 | 3.28 | 965 | 925 | 865 | 925 | B-2-1a
DOUN2- | THUS2K | 15.4 | 0 | OHL | 0.077 | 0.847 | 3.28 | 965 | 925 | 865 | 925 | B-2-1a
DUBE1Q | MYBS1R | 20.84 | 0 | OHL | 1.9025 | 4.8515 | 1.034 | 126 | 117 | 101 | 117 | B-2-1a
DUCC1J | ORRI1S | 10.76 | 0 | OHL | 0.2526 | 2.3466 | 0.568 | 464 | 446 | 414 | 446 | B-2-1a
DUCC1K | ORRI1T | 10.76 | 0 | OHL | 0.2526 | 2.3466 | 0.568 | 464 | 446 | 414 | 446 | B-2-1a
DUGR1Q | EDIN1- | 9 | 0 | OHL | 1.206 | 1.997 | 0.468 | 99 | 92 | 79 | 92 | B-2-1a
DUNM1- | DUNM1T | 2.76 | 0 | OHL | 0.1391 | 0.5715 | 0.155 | 203 | 193 | 176 | 193 | B-2-1a
DUNM1- | DUNM1T | 2.76 | 0 | OHL | 0.1391 | 0.5715 | 0.155 | 203 | 193 | 176 | 193 | B-2-1a
DUNM1C | DUNM1T | 3.24 | 0 | OHL | 0.1632 | 0.6709 | 0.181 | 203 | 193 | 176 | 193 | B-2-1a
DUNM1C | DUNM1T | 3.24 | 0 | OHL | 0.1632 | 0.6709 | 0.181 | 203 | 193 | 176 | 193 | B-2-1a
DYCE1J | DYCE1Q | 1.93 | 0 | OHL | 0.0978 | 0.4332 | 0.33 | 241 | 230 | 210 | 230 | B-2-1a
DYCE1T | KINT1T | 10.17 | 0 | OHL | 0.5187 | 2.2781 | 0.525 | 241 | 230 | 210 | 230 | B-2-1a
DYCE1U | KINT1U | 10.17 | 0 | OHL | 0.6335 | 2.2972 | 0.519 | 145 | 131 | 116 | 131 | B-2-1a
ELGI1L | NAIR1Q | 33.9 | 0 | OHL | 1.7289 | 7.5936 | 1.763 | 241 | 230 | 210 | 230 | B-2-1a
ELGI1M | NAIR1R | 33.9 | 0 | OHL | 1.7289 | 7.5936 | 1.763 | 241 | 230 | 210 | 230 | B-2-1a
ELGI1Q | KEIT1- | 27.4 | 0 | OHL | 1.3974 | 6.1376 | 1.425 | 241 | 230 | 210 | 230 | B-2-1a
ELGI1R | KEIT1- | 27.4 | 0 | OHL | 1.3974 | 6.1376 | 1.425 | 241 | 230 | 210 | 230 | B-2-1a
ERRO1J | TUMB1R | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117 | B-2-1a
ERRO1J | WHIB1A | 4.87 | 0 | OHL | 0.4973 | 1.1403 | 0.242 | 132 | 123 | 106 | 123 | B-2-1a
ERRO1K | TUMB1Q | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117 | B-2-1a
ERRO1K | WHIB1B | 4.87 | 0 | OHL | 0.4973 | 1.1403 | 0.242 | 132 | 123 | 106 | 123 | B-2-1a
ERRO1T | KIIN1- | 36.9 | 0 | OHL | 3.75 | 8.58 | 1.82 | 132 | 123 | 106 | 123 | B-2-1a
FAAR1Q | TOMT1K | 7.2 | 0 | OHL | 0.6544 | 1.6631 | 0.361 | 132 | 123 | 106 | 123 | B-2-1a
FAAR1R | TOMT1J | 7.2 | 0 | OHL | 0.6544 | 1.6631 | 0.361 | 132 | 123 | 106 | 123 | B-2-1a
FARI2J | FOYE2- | 8.4 | 0 | OHL | 0.0479 | 0.3363 | 2.358 | 935 | 880 | 790 | 880 | B-2-1a
FARI2J | KNOC2J | 14.9 | 0 | OHL | 0.0851 | 0.5967 | 4.182 | 935 | 880 | 790 | 880 | B-2-1a
FARI2K | FOYE2- | 8.4 | 0 | OHL | 0.0479 | 0.3363 | 2.358 | 935 | 880 | 790 | 880 | B-2-1a
FARI2K | KNOC2K | 14.9 | 0 | OHL | 0.0851 | 0.5967 | 4.182 | 935 | 880 | 790 | 880 | B-2-1a
FAUG1J | LAGG1Q | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 221 | 216 | 208 | 216 | B-2-1a
FAUG1K | LAGG1R | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 221 | 216 | 208 | 216 | B-2-1a
FAUG1M | LOCL1Q | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247 | B-2-1a
FAUG1N | LOCL1R | 8.5 | 0 | OHL | 0.969 | 1.9295 | 0.425 | 255 | 247 | 237 | 247 | B-2-1a
FAUG1P | QUOI1Q | 28.2 | 0 | OHL | 1.41 | 5.8391 | 1.5759 | 241 | 230 | 210 | 230 | B-2-1a
FAUG2K | TUMM2J | 77.2 | 0 | OHL | 0.211 | 3.128 | 22.063 | 1910 | 1830 | 1710 | 1830 | B-2-1a
FAUG4J | MELG4J | 24.01 | 0 | OHL | 0.0311 | 0.4597 | 14.517 | 2780 | 2670 | 2480 | 2670 | B-2-1a
FERO1- | FERO1S | 5.1 | 0 | OHL | 0.7089 | 1.0659 | 0.265 | 99 | 92 | 79 | 92 | B-2-1a
FERO1S | INVE1J | 15.21 | 0 | OHL | 2.157 | 3.571 | 0.744 | 99 | 92 | 79 | 92 | B-2-1a
FETT2P | KINT2K | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030 | B-2-1a
FETT2Q | KINT2K | 32.15 | 0 | OHL | 0.1624 | 1.4035 | 8.454 | 1090 | 1030 | 925 | 1030 | B-2-1a
FIDD1A | FOGG1R | 25 | 0 | OHL | 2.96 | 6.06 | 1.22 | 112 | 104 | 90 | 104 | B-2-1a
FINL1Q | KIIN1- | 2.1 | 0 | OHL | 0.21 | 0.5 | 0.1 | 126 | 117 | 101 | 117 | B-2-1a
FOGG1Q | KINT1- | 15.6 | 0 | OHL | 1.826 | 3.742 | 0.752 | 112 | 104 | 90 | 104 | B-2-1a
FOGG1Q | TARL1Q | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123 | B-2-1a
FOGG1R | TARL1R | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123 | B-2-1a
FRAS1Q | LUMB1Q | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 126 | 117 | 101 | 117 | B-2-1a
FRAS1R | LUMB1R | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 126 | 117 | 101 | 117 | B-2-1a
FWIL1Q | LOCL1Q | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247 | B-2-1a
FWIL1R | LOCL1R | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247 | B-2-1a
FWIL1R | LUND1- | 9.3 | 0 | OHL | 0.849 | 2.16 | 0.463 | 136 | 129 | 118 | 129 | B-2-1a
GLEN1Q | LAGG1Q | 4.8 | 0 | OHL | 0.546 | 1.132 | 0.232 | 263 | 257 | 248 | 257 | B-2-1a
GLFA1- | KEIT1- | 29.6 | 0 | OHL | 3.0087 | 6.8969 | 1.466 | 126 | 117 | 101 | 117 | B-2-1a
GLRB2- | TEAL2K | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030 | B-2-1a
GRIF1S | WHIB1H | 14.17 | 0 | OHL | 1.4476 | 3.3191 | 0.704 | 132 | 123 | 106 | 123 | B-2-1a
GRIF1T | WHIB1G | 14.17 | 0 | OHL | 1.4476 | 3.3191 | 0.704 | 132 | 123 | 106 | 123 | B-2-1a
GRUB1Q | MOSS1S | 2.73 | 0 | OHL | 0.1392 | 0.6115 | 0.142 | 224 | 211 | 189 | 211 | B-2-1a
GRUB1R | MOSS1T | 2.73 | 0 | OHL | 0.1392 | 0.6115 | 0.142 | 224 | 211 | 189 | 211 | B-2-1a
INGA1Q | LOCL1Q | 2.4 | 0 | OHL | 0.2184 | 0.5592 | 0.12 | 111 | 103 | 89 | 103 | B-2-1a
INNE1Q | SLKB1J | 1.97 | 0 | OHL | 0.1005 | 0.4413 | 0.102 | 241 | 230 | 210 | 230 | B-2-1a
INNE1R | SLKB1K | 1.97 | 0 | OHL | 0.1005 | 0.4413 | 0.102 | 241 | 230 | 210 | 230 | B-2-1a
INRU1Q | PEHG1Q | 1.8 | 0 | OHL | 0.0918 | 0.4032 | 0.094 | 241 | 230 | 210 | 230 | B-2-1a
INRU1Q | SFER1L | 6.1 | 0 | OHL | 0.3111 | 1.3664 | 0.317 | 241 | 230 | 210 | 230 | B-2-1a
INRU1R | PEHG1R | 1.8 | 0 | OHL | 0.0918 | 0.4032 | 0.094 | 241 | 230 | 210 | 230 | B-2-1a
INRU1R | SFER1M | 6.1 | 0 | OHL | 0.3111 | 1.3664 | 0.317 | 241 | 230 | 210 | 230 | B-2-1a
INRU1S | SFER1J | 11.3 | 0 | OHL | 0.6 | 2.379 | 0.617 | 195 | 181 | 157 | 181 | B-2-1a
INVE1K | KILC1Q | 15.1 | 0 | OHL | 2.15 | 3.55 | 0.74 | 99 | 92 | 79 | 92 | B-2-1a
INVE1K | SLOY1E | 21.3 | 0 | OHL | 1.9383 | 4.9629 | 1.065 | 126 | 117 | 101 | 117 | B-2-1a
INVR1- | INVR1A | 6.18 | 0 | OHL | 0.6294 | 1.4386 | 0.305 | 132 | 126 | 106 | 126 | B-2-1a
INVR1- | INVR1B | 6.18 | 0 | OHL | 0.6294 | 1.4386 | 0.305 | 132 | 126 | 106 | 126 | B-2-1a
INVR1- | SLOY1K | 11.22 | 0 | OHL | 1.14 | 2.614 | 0.55 | 132 | 126 | 106 | 126 | B-2-1a
INVR1- | SLOY1T | 5.82 | 0 | OHL | 0.59 | 1.356 | 0.285 | 132 | 126 | 106 | 126 | B-2-1a
INVR1C | KIIN1- | 23 | 0 | OHL | 2.3423 | 5.3538 | 1.134 | 132 | 126 | 106 | 126 | B-2-1a
INVR1D | KIIN1- | 23 | 0 | OHL | 2.3423 | 5.3538 | 1.134 | 132 | 126 | 106 | 126 | B-2-1a
KEIT1J | MACD1Q | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 132 | 123 | 106 | 123 | B-2-1a
KEIT1K | MACD1R | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 132 | 123 | 106 | 123 | B-2-1a
KIIN1- | LOCH1- | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 126 | 117 | 101 | 117 | B-2-1a
KIIN1- | SFIL1Q | 21.6 | 0 | OHL | 2.19 | 5.2 | 1.03 | 126 | 117 | 101 | 117 | B-2-1a
KILC1Q | NANT1Q | 4.2 | 0 | OHL | 0.59 | 1.03 | 0.19 | 99 | 92 | 79 | 92 | B-2-1a
KILO1- | LUND1- | 15.2 | 0 | OHL | 1.054 | 3.441 | 0.775 | 126 | 117 | 101 | 117 | B-2-1a
KINA2J | TUMM2K | 3 | 0 | OHL | 0.0082 | 0.1216 | 0.858 | 1910 | 1830 | 1710 | 1830 | B-2-1a
KINT2J | PERS2R | 28.2 | 0 | OHL | 0.14 | 1.23 | 7.42 | 1090 | 1030 | 920 | 1030 | B-2-1a
KINT2J | TEAL2A | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640 | B-2-1a
KINT2K | PEHE2R | 50.4 | 0 | OHL | 0.26 | 2.19 | 13.22 | 1090 | 1030 | 920 | 1030 | B-2-1a
KINT2K | TEAL2B | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640 | B-2-1a
KINT4J | ROTI4J | 23.2 | 0 | OHL | 0.0464 | 0.4478 | 13.649 | 2000 | 1920 | 1790 | 1920 | B-2-1a
KINT4K | ROTI4K | 23.2 | 0 | OHL | 0.0464 | 0.4478 | 13.649 | 2000 | 1920 | 1790 | 1920 | B-2-1a
KNOC2N | TOMT2K | 18.6 | 0 | OHL | 0.093 | 1.023 | 3.962 | 810 | 765 | 685 | 765 | B-2-1a
KNOC2P | TOMT2J | 18.6 | 0 | OHL | 0.093 | 1.023 | 3.962 | 810 | 765 | 685 | 765 | B-2-1a
LAGG1R | MILW1S | 5.7 | 0 | OHL | 0.648 | 1.344 | 0.276 | 263 | 257 | 248 | 257 | B-2-1a
LOCB1U | MYBS1Q | 85.3 | 0 | OHL | 7.7872 | 19.8576 | 4.2327 | 126 | 117 | 101 | 117 | B-2-1a
LUIC1Q | ORRI1S | 5.4 | 0 | OHL | 0.1271 | 1.1789 | 0.285 | 464 | 446 | 414 | 446 | B-2-1a
LUIC1R | ORRI1T | 5.53 | 0 | OHL | 0.1301 | 1.2064 | 0.292 | 464 | 446 | 414 | 446 | B-2-1a
LUMB1Q | SFER1K | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117 | B-2-1a
LUMB1Q | STRI1Q | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 126 | 117 | 101 | 117 | B-2-1a
LUMB1R | SFER1J | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117 | B-2-1a
LUMB1R | STRI1R | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 126 | 117 | 101 | 117 | B-2-1a
LUNA1Q | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160 | B-2-1a
LUNA1R | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160 | B-2-1a
MELG4J | TUMM4- | 53.19 | 0 | OHL | 0.0689 | 1.0183 | 32.161 | 2780 | 2670 | 2480 | 2670 | B-2-1a
MILC1S | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 183 | 160 | 149 | 160 | B-2-1a
MILC1T | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 183 | 160 | 149 | 160 | B-2-1a
MILW1Q | MILW1S | 1.3 | 0 | OHL | 0.065 | 0.2691 | 0.073 | 203 | 193 | 176 | 193 | B-2-1a
MOSS1Q | MOSS1S | 0.21 | 0 | OHL | 0.0191 | 0.0504 | 0.01 | 132 | 123 | 106 | 123 | B-2-1a
MOSS1R | MOSS1T | 0.21 | 0 | OHL | 0.0191 | 0.0504 | 0.01 | 132 | 123 | 106 | 123 | B-2-1a
MOTA1Q | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 132 | 123 | 106 | 123 | B-2-1a
MOTA1R | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 126 | 117 | 101 | 117 | B-2-1a
MYBS1Q | SPIT1J | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117 | B-2-1a
MYBS1R | SPIT1J | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117 | B-2-1a
MYBS1S | SPIT1M | 5 | 0 | OHL | 0.1182 | 1.0607 | 0.276 | 465 | 445 | 415 | 445 | B-2-1a
MYBS1T | SPIT1K | 5 | 0 | OHL | 0.1182 | 1.0607 | 0.276 | 465 | 445 | 415 | 445 | B-2-1a
NAIR1Q | SLKB1L | 26.33 | 0 | OHL | 1.3428 | 5.8979 | 1.369 | 241 | 230 | 210 | 230 | B-2-1a
NAIR1R | SLKB1M | 26.33 | 0 | OHL | 1.3428 | 5.8979 | 1.369 | 241 | 230 | 210 | 230 | B-2-1a
NEDE4J | PEHE4J | 30.04 | 0 | OHL | 0.0601 | 0.5798 | 17.673 | 2000 | 1920 | 1790 | 1920 | B-2-1a
NEDE4J | ROTI4J | 17.3 | 0 | OHL | 0.0346 | 0.3339 | 10.178 | 2000 | 1920 | 1790 | 1920 | B-2-1a
NEDE4K | PEHE4K | 30.04 | 0 | OHL | 0.0601 | 0.5798 | 17.673 | 2000 | 1920 | 1790 | 1920 | B-2-1a
NEDE4K | ROTI4K | 17.3 | 0 | OHL | 0.0346 | 0.3339 | 10.178 | 2000 | 1920 | 1790 | 1920 | B-2-1a
PEHE2- | PERS2Q | 47.6 | 0 | OHL | 0.24 | 2.08 | 12.52 | 1090 | 1030 | 920 | 1030 | B-2-1a
PORA1R | PORA1T | 6.14 | 0 | OHL | 0.8535 | 1.3692 | 0.301 | 99 | 92 | 79 | 92 | B-2-1a
PORA1S | PORA1U | 6.14 | 0 | OHL | 0.8535 | 1.3692 | 0.301 | 99 | 92 | 79 | 92 | B-2-1a
PORA1S | PORA1U | 6.14 | 0 | OHL | 0.8535 | 1.3692 | 0.301 | 99 | 92 | 79 | 92 | B-2-1a
QUOI1- | QUOI1Q | 1.6 | 0 | OHL | 0.12 | 0.28 | 0.05 | 150 | 142 | 128 | 142 | B-2-1a
RANN1Q | TUMB1Q | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117 | B-2-1a
RANN1R | TUMB1R | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117 | B-2-1a
SFEE1A | SFEG1Q | 0.39 | 0 | OHL | 0.0469 | 0.092 | 0.019 | 126 | 117 | 101 | 117 | B-2-1a
SFEE1A | SFER1L | 1.71 | 0 | OHL | 0.2031 | 0.398 | 0.081 | 126 | 117 | 101 | 117 | B-2-1a
SFEE1B | SFEG1R | 0.39 | 0 | OHL | 0.0469 | 0.092 | 0.019 | 126 | 117 | 101 | 117 | B-2-1a
SFEE1B | SFER1M | 1.71 | 0 | OHL | 0.2031 | 0.398 | 0.081 | 126 | 117 | 101 | 117 | B-2-1a
SLOY1A | SLOY1M | 0.617 | 0 | OHL | 0.0561 | 0.1438 | 0.0309 | 126 | 117 | 101 | 117 | B-2-1a
SLOY1B | SLOY1L | 0.617 | 0 | OHL | 0.0561 | 0.1438 | 0.0309 | 126 | 117 | 101 | 117 | B-2-1a
SLOY1C | SLOY1N | 0.627 | 0 | OHL | 0.0571 | 0.1461 | 0.0313 | 126 | 117 | 101 | 117 | B-2-1a
SLOY1D | SLOY1P | 0.627 | 0 | OHL | 0.0571 | 0.1461 | 0.0313 | 126 | 117 | 101 | 117 | B-2-1a
SLOY1J | SLOY1T | 5.4 | 0 | OHL | 0.547 | 1.254 | 0.266 | 132 | 123 | 106 | 123 | B-2-1a
SPIT2J | THUS2J | 10.54 | 0 | OHL | 0.0527 | 0.5586 | 2.319 | 965 | 925 | 865 | 925 | B-2-1a
SPIT2K | THUS2K | 10.54 | 0 | OHL | 0.0527 | 0.5586 | 2.319 | 965 | 925 | 865 | 925 | B-2-1a
WHIB1C | WHIB1E | 3.57 | 0 | OHL | 0.3644 | 0.8355 | 0.177 | 132 | 123 | 106 | 123 | B-2-1a
WHIB1D | WHIB1F | 3.57 | 0 | OHL | 0.3644 | 0.8355 | 0.177 | 132 | 123 | 106 | 123 | B-2-1a
AUCH2- | MAHI2- | 14.5 | 0 | OHL | 0.109 | 0.8301 | 2.9503 | 570 | 570 | 570 | 570 | B-2-1b
BLAH1- | DUNH1Q | 1.15 | 0 | OHL | 0.0294 | 0.2043 | 0.0733 | 418 | 386 | 386 | 386 | B-2-1b
BLAH1- | DUNH1R | 1.15 | 0 | OHL | 0.0294 | 0.2043 | 0.0733 | 466 | 430 | 418 | 430 | B-2-1b
BONB2J | DENN2- | 19.894 | 0 | OHL | 0.054 | 0.7739 | 5.8126 | 1500 | 1500 | 1500 | 1500 | B-2-1b
BONN1- | CUMB1Q | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135 | B-2-1b
BONN1- | CUMB1R | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135 | B-2-1b
BROX1Q | CURR1A | 10.34 | 0 | OHL | 0.8009 | 2.4722 | 0.505 | 132 | 123 | 106 | 123 | B-2-1b
BROX1R | CURR1B | 10.34 | 0 | OHL | 0.8009 | 2.4722 | 0.505 | 132 | 123 | 106 | 123 | B-2-1b
BUSB2- | NEIL2- | 20.24 | 0 | OHL | 0.0856 | 0.8267 | 5.625 | 1120 | 1060 | 990 | 1060 | B-2-1b
BUSB2- | STHA2A | 15.14 | 0 | OHL | 0.064 | 0.6181 | 4.2097 | 750 | 690 | 630 | 690 | B-2-1b
CLYM2- | DALM2Q | 4.21 | 0 | OHL | 0.019 | 0.1713 | 1.1692 | 750 | 690 | 630 | 690 | B-2-1b
CLYM2- | EERH2- | 8.75 | 0 | OHL | 0.0197 | 0.3069 | 2.8023 | 1500 | 1500 | 1500 | 1500 | B-2-1b
CLYM2- | EKIL2Q | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060 | B-2-1b
CLYM2- | EKIL2R | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060 | B-2-1b
CLYM2- | LOAN2- | 54.57 | 0 | OHL | 0.1231 | 1.9141 | 17.477 | 1500 | 1500 | 1500 | 1500 | B-2-1b
COAL4- | ELVA4- | 26.71 | 0 | OHL | 0.0467 | 0.5062 | 15.9918 | 2210 | 2130 | 1980 | 2130 | B-2-1b
COCK2- | KAIM2- | 18.29 | 0 | OHL | 0.0779 | 0.756 | 5.0669 | 1120 | 1060 | 990 | 1060 | B-2-1b
COCK2- | SMEA2- | 9.51 | 0 | OHL | 0.0405 | 0.3931 | 2.6346 | 1120 | 1060 | 990 | 1060 | B-2-1b
COCK4Q | ECCL4A | 65.9 | 0 | OHL | 0.135 | 1.4191 | 35.4794 | 1120 | 1060 | 990 | 1060 | B-2-1b
COCK4R | ECCL4B | 65.89 | 0 | OHL | 0.135 | 1.4189 | 35.4739 | 1120 | 1060 | 990 | 1060 | B-2-1b
COYL2- | COYW2T | 1.32 | 0 | OHL | 0.0058 | 0.0522 | 0.3778 | 1500 | 1500 | 1500 | 1500 | B-2-1b
COYL2- | MAHI2- | 49.5 | 0 | OHL | 0.3612 | 2.813 | 10.0797 | 1110 | 1090 | 1060 | 1090 | B-2-1b
COYW2S | KILS2- | 13.37 | 0 | OHL | 0.0588 | 0.5269 | 3.8357 | 1500 | 1500 | 1500 | 1500 | B-2-1b
COYW2T | KILS2- | 13.37 | 0 | OHL | 0.0588 | 0.5269 | 3.8357 | 1500 | 1500 | 1500 | 1500 | B-2-1b
CUPA1Q | LEVT1Q | 13.27 | 0 | OHL | 1.2026 | 2.9807 | 0.6715 | 143 | 142 | 128 | 142 | B-2-1b
CUPA1R | LEVT1R | 13.27 | 0 | OHL | 1.2026 | 2.9807 | 0.6715 | 143 | 142 | 128 | 142 | B-2-1b
CURR2- | GRMO2- | 42.2 | 0 | OHL | 0.1916 | 1.7399 | 11.6642 | 1090 | 1030 | 925 | 1030 | B-2-1b
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.0398 | 0.3865 | 2.5902 | 1380 | 1320 | 1230 | 1320 | B-2-1b
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.0398 | 0.3865 | 2.5902 | 1380 | 1320 | 1230 | 1320 | B-2-1b
CURR2- | KINC2- | 55.76 | 0 | OHL | 0.2531 | 2.2958 | 15.4272 | 1090 | 1030 | 925 | 1030 | B-2-1b
DALL2- | INVR2- | 22.55 | 0 | OHL | 0.0954 | 0.921 | 6.2707 | 570 | 570 | 570 | 570 | B-2-1b
DALL2- | WIYH2- | 78.15 | 0 | OHL | 0.3305 | 3.192 | 21.732 | 570 | 570 | 570 | 570 | B-2-1b
DENN2- | LAMB2T | 31.991 | 0 | OHL | 0.1442 | 1.3015 | 8.8844 | 955 | 880 | 760 | 885 | B-2-1b
DENN2- | LOAN2- | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500 | B-2-1b
DENN2- | LOAN2T | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500 | B-2-1b
DEVM4- | NEIL4R | 28.474 | 0 | OHL | 0.058184 | 0.59672 | 15.8233 | 2000 | 1920 | 1790 | 1920 | B-2-1b
DEVO1- | WFIE1B | 31.8 | 0 | OHL | 2.8944 | 7.5329 | 1.5454 | 162 | 154 | 141 | 154 | B-2-1b
DRUM2R | WIYH2- | 2.46 | 0 | OHL | 0.0111 | 0.1001 | 0.6832 | 120 | 120 | 120 | 120 | B-2-1b
DUMF1- | TONG1Q | 43.58 | 0 | OHL | 4.447 | 10.71 | 2.18 | 132 | 123 | 106 | 123 | B-2-1b
DUNE1- | GALA1- | 23.64 | 0 | OHL | 2.1456 | 5.5767 | 1.1477 | 164 | 151 | 127 | 151 | B-2-1b
DUNF1Q | MOSM1A | 10.46 | 0 | OHL | 0.5557 | 2.2694 | 0.5549 | 215 | 215 | 198 | 215 | B-2-1b
DUNF1R | MOSM1B | 10.46 | 0 | OHL | 0.5557 | 2.2694 | 0.5549 | 215 | 215 | 198 | 215 | B-2-1b
DUNH1Q | NECU1- | 13.65 | 0 | OHL | 0.3486 | 2.4244 | 0.8703 | 484 | 458 | 418 | 458 | B-2-1b
DUNH1R | NECU1- | 13.65 | 0 | OHL | 0.3486 | 2.4244 | 0.8703 | 484 | 458 | 418 | 458 | B-2-1b
EAST1Q | GLLE1- | 1.69 | 0 | OHL | 0.1536 | 0.3503 | 0.094 | 132 | 123 | 106 | 123 | B-2-1b
ECCL1- | GALA1- | 31.37 | 0 | OHL | 2.8482 | 7.3807 | 1.5285 | 132 | 123 | 106 | 123 | B-2-1b
ECCL1- | GALA1- | 30.94 | 0 | OHL | 2.8144 | 7.1441 | 1.5364 | 132 | 123 | 106 | 123 | B-2-1b
ECCL4C | STWB4Q | 7.39 | 0 | OHL | 0.0063 | 0.1209 | 5.1175 | 2770 | 2770 | 2660 | 2770 | B-2-1b
ECCL4D | STWB4R | 7.39 | 0 | OHL | 0.0063 | 0.1209 | 5.1175 | 2770 | 2770 | 2660 | 2770 | B-2-1b
EERH2- | LOAN2- | 45.82 | 0 | OHL | 0.1034 | 1.6072 | 14.6747 | 1500 | 1500 | 1500 | 1500 | B-2-1b
EERH2- | NEAR2Q | 15.34 | 0 | OHL | 0.077 | 0.632 | 4.283 | 950 | 885 | 760 | 885 | B-2-1b
EKIL2Q | EKIL2S | 5.17 | 0 | OHL | 0.0138 | 0.1834 | 1.6594 | 865 | 825 | 750 | 825 | B-2-1b
EKIL2R | STHA2B | 4.79 | 0 | OHL | 0.0216 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965 | B-2-1b
EKIS2- | NEIL2- | 29.58 | 0 | OHL | 0.1251 | 1.2082 | 8.2207 | 1110 | 1030 | 885 | 1030 | B-2-1b
ELVA3A | PRST3A | 1.01 | 0 | OHL | 0.8089 | 2.9543 | 0.004 | 49 | 45 | 39 | 45 | B-2-1b
ELVA4- | STHA4A | 48.56 | 0 | OHL | 0.085 | 0.9204 | 29.0717 | 2210 | 2130 | 1980 | 2130 | B-2-1b
GALA1- | HAWI1B | 23.55 | 0 | OHL | 1.211 | 2.684 | 7.57 | 132 | 122 | 106 | 122 | B-2-1b
GARB1Q | HELE1Q | 15.313 | 0 | OHL | 1.3875 | 3.4126 | 0.7803 | 132 | 123 | 106 | 123 | B-2-1b
GARB1R | STLE1Q | 26.909 | 0 | OHL | 2.4383 | 5.997 | 1.3713 | 132 | 123 | 106 | 123 | B-2-1b
GARB1S | GARE1S | 5.03 | 0 | OHL | 0.4558 | 1.1211 | 0.2564 | 132 | 123 | 106 | 123 | B-2-1b
GARB1T | GARE1T | 5.061 | 0 | OHL | 0.4586 | 1.1279 | 0.2579 | 132 | 123 | 106 | 123 | B-2-1b
GARE1S | WHTL1S | 1.68 | 0 | OHL | 0.2125 | 0.3513 | 0.0919 | 100 | 94 | 80 | 94 | B-2-1b
GARE1T | WHTL1T | 1.67 | 0 | OHL | 0.2112 | 0.3492 | 0.0913 | 100 | 94 | 80 | 94 | B-2-1b
GLLE1- | KEOO1- | 7.68 | 0 | OHL | 0.6969 | 1.6787 | 0.405 | 132 | 123 | 106 | 123 | B-2-1b
GLLU1Q | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49 | B-2-1b
GLNI1- | WFIE1B | 7.11 | 0 | OHL | 0.5359 | 1.6524 | 0.3546 | 264 | 246 | 212 | 246 | B-2-1b
GLRB2- | GLRO2- | 14.68 | 0 | OHL | 0.0664 | 0.6181 | 3.956 | 1090 | 1030 | 925 | 1030 | B-2-1b
GLRO2- | WFIE2- | 12.08 | 0 | OHL | 0.0547 | 0.5102 | 3.2488 | 1090 | 1030 | 925 | 1030 | B-2-1b
GRMO2- | KINC2- | 14.96 | 0 | OHL | 0.068 | 0.6184 | 4.1277 | 1050 | 965 | 880 | 965 | B-2-1b
GRNA1- | HAWI1- | 55.35 | 0 | OHL | 4.2501 | 13.0393 | 2.7334 | 132 | 123 | 106 | 123 | B-2-1b
HAWI1- | JUNV1- | 50.34 | 0 | OHL | 3.7968 | 11.8507 | 2.4895 | 132 | 123 | 106 | 123 | B-2-1b
HUER4- | KILS4- | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930 | B-2-1b
HUER4- | KILS4T | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930 | B-2-1b
HUNE4- | NEIL4Q | 35.43 | 0 | OHL | 0.0706 | 0.7289 | 20.0655 | 1390 | 1280 | 1110 | 1280 | B-2-1b
HUNE4- | NEIL4R | 35.43 | 0 | OHL | 0.0706 | 0.7289 | 20.0655 | 1390 | 1280 | 1110 | 1280 | B-2-1b
INVR2- | WIYH2- | 55.6 | 0 | OHL | 0.2351 | 2.2709 | 15.4613 | 570 | 570 | 570 | 570 | B-2-1b
JUNA1T | KILW1Q | 12.418 | 0 | OHL | 0.4909 | 2.779 | 0.643 | 146 | 146 | 146 | 146 | B-2-1b
JUNA1T | SACO1Q | 8.14 | 0 | OHL | 0.3086 | 1.8332 | 0.4224 | 151 | 151 | 151 | 151 | B-2-1b
KEOO1- | NECU1R | 26.51 | 0 | OHL | 0.8345 | 5.2149 | 1.561 | 132 | 123 | 106 | 123 | B-2-1b
KILS1- | MEAD1- | 12.57 | 0 | OHL | 0.874 | 2.581 | 2.166 | 162 | 154 | 141 | 154 | B-2-1b
KILS4- | STHA4A | 34.948 | 0 | OHL | 0.0712 | 0.7173 | 19.8386 | 2000 | 1920 | 1790 | 1920 | B-2-1b
KILS4T | STHA4B | 34.948 | 0 | OHL | 0.0712 | 0.7173 | 19.8386 | 2000 | 1920 | 1790 | 1920 | B-2-1b
KILW1Q | MEAD1- | 13.8 | 0 | OHL | 0.7331 | 2.9941 | 0.732 | 146 | 146 | 138 | 146 | B-2-1b
KILW1R | MEAD1- | 13.8 | 0 | OHL | 0.7331 | 2.9941 | 0.732 | 146 | 146 | 138 | 146 | B-2-1b
KINB2J | KINC2- | 10.71 | 0 | OHL | 0.0482 | 0.4368 | 2.969 | 1090 | 1030 | 925 | 1030 | B-2-1b
KINC2- | LOAN2Q | 4.28 | 0 | OHL | 0.0186 | 0.1855 | 1.1454 | 765 | 620 | 620 | 620 | B-2-1b
KINC2- | LOAN2R | 4.28 | 0 | OHL | 0.0186 | 0.1855 | 1.1454 | 765 | 620 | 620 | 620 | B-2-1b
LAMB2- | LAMB2T | 0.001 | 0 | OHL | 0 | 0 | 0 | 1120 | 1060 | 990 | 1060 | B-2-1b
LAMB2- | PORD2Q | 3.94 | 0 | OHL | 0.0182 | 0.1701 | 1.0531 | 955 | 885 | 760 | 885 | B-2-1b
LEVE1Q | LEVT1Q | 2.16 | 0 | OHL | 0.1957 | 0.4852 | 0.1093 | 143 | 142 | 128 | 142 | B-2-1b
LEVE1R | LEVT1R | 2.26 | 0 | OHL | 0.2048 | 0.5083 | 0.1143 | 143 | 142 | 128 | 142 | B-2-1b
LEVT1Q | REDH1- | 8.61 | 0 | OHL | 0.7803 | 1.9339 | 0.4357 | 143 | 142 | 128 | 142 | B-2-1b
LEVT1R | WFIE1B | 18.707 | 0 | OHL | 1.588 | 4.18 | 0.9537 | 143 | 142 | 128 | 142 | B-2-1b
LOAN2- | LOAN2T | 0.001 | 0 | OHL | 0 | 0 | 0 | 1500 | 1500 | 1500 | 1500 | B-2-1b
LOAN2T | WFIE2- | 29.209 | 0 | OHL | 0.1316 | 1.2106 | 7.9335 | 1090 | 1030 | 925 | 1030 | B-2-1b
MOSM2- | WFIE2- | 8.243 | 0 | OHL | 0.0378 | 0.3641 | 2.1507 | 1090 | 1030 | 925 | 1030 | B-2-1b
NEAR2Q | WISH2- | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 955 | 885 | 760 | 885 | B-2-1b
NEAR2R | WISH2- | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 285 | 285 | 285 | 285 | B-2-1b
PAIS1Q | PAIS1S | 1.87 | 0 | OHL | 0.0366 | 0.3302 | 0.1197 | 460 | 425 | 365 | 425 | B-2-1b
PAIS1R | PAIS1T | 1.87 | 0 | OHL | 0.0366 | 0.3302 | 0.1197 | 460 | 425 | 365 | 425 | B-2-1b
REDH1- | WFIE1A | 10.097 | 0 | OHL | 0.8077 | 2.2461 | 0.5179 | 157 | 152 | 141 | 152 | B-2-1b
SMEA4Q | STHA4B | 73.37 | 0 | OHL | 0.1593 | 1.4873 | 41.7375 | 900 | 760 | 760 | 760 | B-2-1b
WFIB2- | WFIE2- | 22.48 | 0 | OHL | 0.1014 | 0.933 | 6.1144 | 1090 | 1030 | 925 | 1030 | B-2-1b
WHTB1S | WHTL1S | 2.05 | 0 | OHL | 0.2593 | 0.4287 | 0.1121 | 100 | 94 | 80 | 94 | B-2-1b
WHTB1T | WHTL1T | 2.05 | 0 | OHL | 0.2593 | 0.4287 | 0.1121 | 100 | 94 | 80 | 94 | B-2-1b
ABHA4A | EXET41 | 48.785 | 0 | OHL | 0.0778 | 0.9831 | 27.9792 | 2078 | 2078 | 2078 | 2078 | B-2-1c
ABHA4A | LAGA41 | 26.121 | 0 | OHL | 0.0417 | 0.5027 | 15.6941 | 2423 | 2327 | 2168 | 2327 | B-2-1c
ABHA4B | EXET41 | 49.051 | 0 | OHL | 0.0783 | 0.9885 | 28.1313 | 2423 | 2327 | 2168 | 2327 | B-2-1c
ABHA4B | LAGA41 | 26.121 | 0 | OHL | 0.0417 | 0.5027 | 15.6941 | 2423 | 2327 | 2168 | 2327 | B-2-1c
ABTH21 | COWT2A | 13.318 | 0 | OHL | 0.0503 | 0.5449 | 3.758 | 932 | 879 | 790 | 879 | B-2-1c
ABTH21 | PYLE21 | 35.388 | 0 | OHL | 0.1819 | 1.4523 | 9.9528 | 932 | 879 | 790 | 879 | B-2-1c
ABTH21 | TREM21 | 46.451 | 0 | OHL | 0.2267 | 2.1393 | 11.8321 | 682 | 629 | 538 | 629 | B-2-1c
ABTH21 | UPPB21 | 26.996 | 0 | OHL | 0.1234 | 1.1426 | 7.3237 | 955 | 882 | 762 | 882 | B-2-1c
ALDW21 | BRIN21 | 17.961 | 0 | OHL | 0.1442 | 0.7628 | 4.8487 | 626 | 591 | 535 | 591 | B-2-1c
ALDW21 | WMEL21 | 8.96 | 0 | OHL | 0.0409 | 0.3891 | 2.3695 | 955 | 882 | 762 | 882 | B-2-1c
ALVE4A | INDQ41 | 97.176 | 0 | OHL | 0.2121 | 1.9367 | 56.1415 | 1389 | 1284 | 1108 | 1284 | B-2-1c
ALVE4A | TAUN41 | 73.293 | 0 | OHL | 0.117 | 1.477 | 42.0344 | 1389 | 1284 | 1108 | 1284 | B-2-1c
ALVE4B | INDQ41 | 97.294 | 0 | OHL | 0.2123 | 1.9391 | 56.209 | 1389 | 1284 | 1108 | 1284 | B-2-1c
ALVE4B | TAUN42 | 73.298 | 0 | OHL | 0.117 | 1.4771 | 42.0372 | 1389 | 1284 | 1108 | 1284 | B-2-1c
AMEM4A | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2009 | 1911 | 1746 | 1911 | B-2-1c
AMEM4A | IVER4A | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2009 | 1911 | 1746 | 1911 | B-2-1c
AMEM4B | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2032 | 1933 | 1766 | 1933 | B-2-1c
AMEM4B | IVER4B | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2032 | 1933 | 1766 | 1933 | B-2-1c
AXMI41 | EXET41 | 36.184 | 0 | OHL | 0.0404 | 0.6915 | 21.9115 | 2779 | 2568 | 2217 | 2568 | B-2-1c
BARK21 | REBR22 | 10.879 | 0 | OHL | 0.0411 | 0.4451 | 3.0706 | 1129 | 1081 | 1000 | 1081 | B-2-1c
BARK22 | REBR21 | 10.854 | 0 | OHL | 0.041 | 0.4441 | 3.0636 | 1205 | 1127 | 1044 | 1127 | B-2-1c
BARK41 | CHUE4A | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048 | B-2-1c
BARK41 | CHUE4B | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048 | B-2-1c
BARK41 | WTHU4A | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911 | B-2-1c
BARK41 | WTHU4B | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911 | B-2-1c
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882 | B-2-1c
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882 | B-2-1c
BESW21 | FECK21 | 35.814 | 0 | OHL | 0.1425 | 1.5095 | 9.7917 | 955 | 882 | 762 | 882 | B-2-1c
BICF41 | SPLN41 | 20.109 | 0 | OHL | 0.0191 | 0.355 | 13.187 | 3156 | 3032 | 2823 | 3032 | B-2-1c
BICF41 | WALP41 | 37.775 | 0 | OHL | 0.0335 | 0.6488 | 25.3895 | 3189 | 3063 | 2853 | 3063 | B-2-1c
BICF41 | WBUR41 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160 | B-2-1c
BICF41 | WBUR42 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160 | B-2-1c
BIGG41 | EASO41 | 16.5 | 0 | OHL | 0.0146 | 0.2834 | 11.1085 | 3326 | 2790 | 3320 | 3320 | B-2-1c
BIGG41 | WYMO41 | 18.772 | 0 | OHL | 0.0166 | 0.3225 | 12.6381 | 3326 | 2790 | 3320 | 3320 | B-2-1c
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882 | B-2-1c
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882 | B-2-1c
BISW21 | FECK21 | 22.83 | 0 | OHL | 0.0938 | 0.9633 | 6.2301 | 955 | 882 | 762 | 882 | B-2-1c
BISW21 | KITW21 | 24.226 | 0 | OHL | 0.0932 | 1.0024 | 6.7545 | 955 | 882 | 762 | 882 | B-2-1c
BISW21 | KITW21 | 27.111 | 0 | OHL | 0.1054 | 1.1236 | 7.5448 | 955 | 882 | 762 | 882 | B-2-1c
BISW21 | PENN21 | 30.172 | 0 | OHL | 0.1233 | 1.2726 | 8.2379 | 1040 | 1031 | 762 | 762 | B-2-1c
BLYT21 | STEW21 | 26.779 | 0 | OHL | 0.1472 | 1.3916 | 5.9965 | 682 | 629 | 538 | 629 | B-2-1c
BLYT21 | STEW21 | 26.711 | 0 | OHL | 0.1469 | 1.388 | 5.9813 | 682 | 629 | 538 | 629 | B-2-1c
BLYT21 | TYNE21 | 16.818 | 0 | OHL | 0.0742 | 0.7144 | 4.5642 | 1360 | 1310 | 1220 | 1310 | B-2-1c
BLYT21 | TYNE2A | 16.866 | 0 | OHL | 0.0744 | 0.7164 | 4.5772 | 1360 | 1310 | 1220 | 1310 | B-2-1c
BODE41 | GWYN4B | 0.5 | 0 | OHL | 0.0005 | 0.0087 | 0.3284 | 2771 | 2695 | 2510 | 2695 | B-2-1c
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 3102 | 2935 | 2765 | 2935 | B-2-1c
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 2771 | 2771 | 2765 | 2771 | B-2-1c
BOTW41 | CHIL41 | 7.479 | 0 | OHL | 0.0066 | 0.1285 | 5.027 | 3341 | 3160 | 2971 | 3160 | B-2-1c
BOTW41 | LOVE41 | 14.672 | 0 | OHL | 0.013 | 0.252 | 9.8617 | 3341 | 3160 | 2971 | 3160 | B-2-1c
BRAI4A | BRFO41 | 48.267 | 0 | OHL | 0.0449 | 0.8314 | 32.3122 | 3326 | 3326 | 3317 | 3326 | B-2-1c
BRAI4A | BULL41 | 12.343 | 0 | OHL | 0.0121 | 0.2133 | 8.2261 | 3066 | 2830 | 2418 | 2830 | B-2-1c
BRAI4B | PELH41 | 65.942 | 0 | OHL | 0.0648 | 1.1396 | 43.9331 | 2779 | 2568 | 2217 | 2568 | B-2-1c
BRAI4B | RAYL41 | 33.03 | 0 | OHL | 0.0325 | 0.5709 | 22.0036 | 2779 | 2568 | 2217 | 2568 | B-2-1c
BRAW21 | MONF21 | 51.155 | 0 | OHL | 0.1174 | 1.8824 | 15.9388 | 1204 | 1115 | 1018 | 1115 | B-2-1c
BRAW4A | PADI41 | 59.3 | 0 | OHL | 0.0754 | 1.1321 | 35.9226 | 2470 | 2350 | 2146 | 2350 | B-2-1c
BRED21 | MACC21 | 19.612 | 0 | OHL | 0.0768 | 0.8127 | 5.4608 | 948 | 882 | 753 | 753 | B-2-1c
BRED21 | STAL21 | 15.054 | 0 | OHL | 0.0665 | 0.6343 | 4.1113 | 1093 | 1031 | 925 | 1031 | B-2-1c
BRFO41 | FRIS4A | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2779 | 2568 | 2217 | 2568 | B-2-1c
BRFO41 | FRIS4B | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2779 | 2568 | 2217 | 2568 | B-2-1c
BRFO41 | FRIS4C | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2779 | 2569 | 2217 | 2569 | B-2-1c
BRFO41 | FRIS4D | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2779 | 2568 | 2217 | 2568 | B-2-1c
BRFO41 | PELH41 | 69.301 | 0 | OHL | 0.0655 | 1.1949 | 46.3271 | 3102 | 2935 | 2765 | 2935 | B-2-1c
BRIM2C | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031 | B-2-1c
BRIM2D | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031 | B-2-1c
BRIN21 | TEMP21 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882 | B-2-1c
BRIN21 | TEMP22 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882 | B-2-1c
BRIN22 | CHTE21 | 22.375 | 0 | OHL | 0.0513 | 0.8236 | 6.9689 | 1204 | 1115 | 1018 | 1115 | B-2-1c
BRIN22 | THUR21 | 5.704 | 0 | OHL | 0.0599 | 0.2384 | 1.5621 | 626 | 591 | 535 | 591 | B-2-1c
BRIN22 | TINP21 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 955 | 882 | 762 | 882 | B-2-1c
BRIN22 | TINP22 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 919 | 869 | 762 | 869 | B-2-1c
BRIN41 | THOM41 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2518 | 2395 | 2188 | 2395 | B-2-1c
BRIN41 | THOM42 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2545 | 2421 | 2211 | 2421 | B-2-1c
BRLE41 | WWEY4A | 49.375 | 0 | OHL | 0.0789 | 0.9495 | 29.6914 | 2199 | 2092 | 1911 | 2092 | B-2-1c
BRLE41 | WWEY4B | 49.375 | 0 | OHL | 0.0789 | 0.9495 | 29.6914 | 2199 | 2092 | 1911 | 2092 | B-2-1c
BRWA41 | BRWA4A | 4.371 | 0 | OHL | 0.0079 | 0.087 | 2.5326 | 2030 | 1930 | 1770 | 1930 | B-2-1c
BRWA4A | MELK41 | 77.004 | 0 | OHL | 0.1368 | 1.5195 | 45.0234 | 2009 | 1911 | 1746 | 1911 | B-2-1c
BRWA4A | SHUR41 | 14.02 | 0 | OHL | 0.0218 | 0.269 | 8.4136 | 3100 | 3050 | 2960 | 3050 | B-2-1c
BRWA4B | MELK41 | 76.264 | 0 | OHL | 0.1356 | 1.5048 | 44.5918 | 2009 | 2009 | 2009 | 2009 | B-2-1c
BRWA4B | SHUR41 | 14.02 | 0 | OHL | 0.0218 | 0.269 | 8.4136 | 3100 | 3050 | 2960 | 3050 | B-2-1c
BULL41 | RAYL41 | 20.646 | 0 | OHL | 0.0203 | 0.3568 | 13.7565 | 2779 | 2569 | 2217 | 2569 | B-2-1c
BURW41 | PELH41 | 42.782 | 0 | OHL | 0.0379 | 0.7348 | 28.7545 | 3326 | 3159 | 2971 | 3159 | B-2-1c
BURW41 | PELH41 | 42.934 | 0 | OHL | 0.0381 | 0.7374 | 28.8562 | 3035 | 2876 | 2238 | 2515 | B-2-1c
BURW41 | WALP41 | 51.189 | 0 | OHL | 0.0454 | 0.8792 | 34.4056 | 3326 | 3160 | 2971 | 3160 | B-2-1c
BURW41 | WALP41 | 51.183 | 0 | OHL | 0.0454 | 0.8791 | 34.4016 | 3326 | 3160 | 2971 | 3160 | B-2-1c
BUSH21 | DRAK21 | 38.153 | 0 | OHL | 0.146 | 1.6016 | 10.4839 | 1204 | 1115 | 1018 | 1115 | B-2-1c
BUSH21 | PENN21 | 21.653 | 0 | OHL | 0.0824 | 0.9078 | 5.9595 | 1038 | 1038 | 762 | 762 | B-2-1c
BUST4A | DRAK41 | 34.592 | 0 | OHL | 0.0375 | 0.6017 | 22.8026 | 1203 | 1203 | 1103 | 1119 | B-2-1c
BUST4B | DRAK41 | 34.537 | 0 | OHL | 0.0375 | 0.6007 | 22.7664 | 2779 | 2568 | 2217 | 2568 | B-2-1c
CANT41 | CLEH41 | 14.7 | 0 | OHL | 0.0229 | 0.282 | 8.8214 | 3102 | 3048 | 2853 | 3048 | B-2-1c
CANT41 | KEMS4A | 28.2 | 0 | OHL | 0.0439 | 0.5411 | 16.9228 | 3102 | 2935 | 2765 | 2935 | B-2-1c
CANT41 | RICH41 | 25 | 0 | OHL | 0.0399 | 0.4808 | 15.0336 | 2038 | 2038 | 1801 | 1801 | B-2-1c
CANT41 | RICH41 | 25 | 0 | OHL | 0.0399 | 0.4808 | 15.0336 | 2038 | 2038 | 1801 | 1801 | B-2-1c
CANT41 | SELL4C | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3102 | 3048 | 2958 | 3048 | B-2-1c
CANT41 | SELL4D | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3103 | 3048 | 2959 | 3048 | B-2-1c
CAPE4A | CONQ41 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3326 | 3160 | 2971 | 3160 | B-2-1c
CAPE4A | FROD41 | 18.404 | 0 | OHL | 0.0199 | 0.2926 | 13.3521 | 2889 | 2748 | 2418 | 2748 | B-2-1c
CAPE4B | CONQ41 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3326 | 3160 | 2971 | 3160 | B-2-1c
CAPE4B | FROD41 | 18.315 | 0 | OHL | 0.0198 | 0.2912 | 13.2878 | 2890 | 2749 | 2418 | 2749 | B-2-1c
CARE21 | COWT2A | 27.881 | 0 | OHL | 0.1533 | 1.4488 | 6.2406 | 682 | 629 | 538 | 629 | B-2-1c
CARE21 | USKM2B | 19.94 | 0 | OHL | 0.1096 | 1.0362 | 4.4651 | 682 | 629 | 538 | 629 | B-2-1c
CARR41 | KEAR41 | 13.154 | 0 | OHL | 0.0225 | 0.2574 | 7.7626 | 2212 | 2125 | 1979 | 2125 | B-2-1c
CARR41 | PEWO4A | 56.9 | 0 | OHL | 0.0988 | 1.1179 | 33.4404 | 2169 | 2084 | 1940 | 2084 | B-2-1c
CARR4B | DAIN41 | 2.036 | 0 | OHL | 0.0037 | 0.0405 | 1.1791 | 1553 | 1553 | 1553 | 1553 | B-2-1c
CELL41 | DRAK41 | 45.012 | 0 | OHL | 0.0719 | 0.8656 | 27.0675 | 2397 | 2302 | 2144 | 2302 | B-2-1c
CELL41 | DRAK41 | 45.712 | 0 | OHL | 0.073 | 0.8791 | 27.4871 | 2397 | 2302 | 2144 | 2302 | B-2-1c
CELL41 | MACC41 | 31.617 | 0 | OHL | 0.0494 | 0.6067 | 18.9767 | 3102 | 3048 | 2958 | 3048 | B-2-1c
CHIC41 | MANN41 | 53.913 | 0 | OHL | 0.0585 | 0.9377 | 35.5401 | 3065 | 2829 | 2418 | 2829 | B-2-1c
CHIC4A | MANN41 | 54.066 | 0 | OHL | 0.0587 | 0.9404 | 35.6406 | 3065 | 2829 | 2418 | 2829 | B-2-1c
CHSI21 | WWEY21 | 15.318 | 0 | OHL | 0.0519 | 0.6229 | 4.351 | 1316 | 1213 | 1104 | 1213 | B-2-1c
CHSI21 | WWEY22 | 15.347 | 0 | OHL | 0.052 | 0.6241 | 4.3592 | 1316 | 1213 | 1104 | 1213 | B-2-1c
CHTE21 | HIGM21 | 43.792 | 0 | OHL | 0.1218 | 1.806 | 12.2763 | 1381 | 1339 | 1258 | 1339 | B-2-1c
CHTE21 | HIGM21 | 43.651 | 0 | OHL | 0.1214 | 1.8002 | 12.2369 | 1381 | 1381 | 1375 | 1381 | B-2-1c
CHUE4A | WTHU4D | 2.419 | 0 | OHL | 0.0038 | 0.0488 | 1.378 | 3102 | 3048 | 2958 | 3048 | B-2-1c
CHUE4B | WTHU4C | 2.581 | 0 | OHL | 0.004 | 0.0519 | 1.4744 | 3102 | 3048 | 2958 | 3048 | B-2-1c
CILF2A | UPPB21 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882 | B-2-1c
CILF2B | UPPB22 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882 | B-2-1c
CILF41 | IMPP41 | 25.119 | 0 | OHL | 0.0273 | 0.4396 | 16.4758 | 2779 | 2568 | 2217 | 2568 | B-2-1c
CILF41 | RASS41 | 26.901 | 0 | OHL | 0.0292 | 0.4679 | 17.7332 | 2779 | 2568 | 2217 | 2568 | B-2-1c
CILF41 | RHIG41 | 25.011 | 0 | OHL | 0.0271 | 0.435 | 16.4876 | 2779 | 2568 | 2217 | 2568 | B-2-1c
CILF41 | SWAN41 | 61.595 | 0 | OHL | 0.0668 | 1.0713 | 40.6034 | 2779 | 2568 | 2217 | 2568 | B-2-1c
CILF41 | SWAN42 | 61.655 | 0 | OHL | 0.0669 | 1.0724 | 40.6428 | 3180 | 3000 | 2692 | 3000 | B-2-1c
CILF41 | WHSO4A | 35.208 | 0 | OHL | 0.0383 | 0.6151 | 23.1262 | 2779 | 2568 | 2217 | 2568 | B-2-1c
CLEH41 | KEMS4B | 13.5 | 0 | OHL | 0.021 | 0.259 | 8.1013 | 3102 | 3048 | 2853 | 3048 | B-2-1c
CONQ41 | DAIN41 | 60.331 | 0 | OHL | 0.094 | 1.1575 | 36.2038 | 3102 | 3048 | 2853 | 3048 | B-2-1c
CONQ41 | DAIN41 | 60.294 | 0 | OHL | 0.0938 | 1.1562 | 36.2009 | 3102 | 3048 | 2853 | 3048 | B-2-1c
CONQ41 | TREU4A | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2397 | 2302 | 2144 | 2302 | B-2-1c
CONQ41 | TREU4B | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2212 | 2125 | 1979 | 2125 | B-2-1c
COSO41 | RAYL41 | 13.913 | 0 | OHL | 0.0217 | 0.2698 | 8.2601 | 2886 | 2835 | 2663 | 2835 | B-2-1c
COSO41 | TILB4B | 12.363 | 0 | OHL | 0.0193 | 0.24 | 7.3306 | 3075 | 2876 | 2663 | 2876 | B-2-1c
COTT41 | MARH4B | 100.853 | 0 | OHL | 0.1772 | 1.9852 | 59.1294 | 2009 | 1912 | 1746 | 1912 | B-2-1c
COTT41 | RYHA4A | 76.891 | 0 | OHL | 0.0682 | 1.3211 | 51.7563 | 3326 | 3326 | 3317 | 3326 | B-2-1c
COTT42 | RYHA4B | 76.816 | 0 | OHL | 0.0681 | 1.3196 | 51.7119 | 2807 | 2696 | 2511 | 2696 | B-2-1c
COTT42 | STAY41 | 27.698 | 0 | OHL | 0.0441 | 0.5297 | 16.7334 | 2212 | 2125 | 1979 | 2125 | B-2-1c
COVE21 | NECH21 | 30.715 | 0 | OHL | 0.0736 | 1.1961 | 9.1449 | 1204 | 1115 | 1018 | 1115 | B-2-1c
COWL41 | CULJ4A | 6.496 | 0 | OHL | 0.0085 | 0.1266 | 3.8528 | 2771 | 2568 | 2217 | 2568 | B-2-1c
COWL41 | DIDC41 | 11.503 | 0 | OHL | 0.0151 | 0.2242 | 6.8223 | 2779 | 2568 | 2217 | 2568 | B-2-1c
COWL41 | ECLA41 | 36.301 | 0 | OHL | 0.0322 | 0.6236 | 24.4394 | 3326 | 3326 | 3326 | 3326 | B-2-1c
COWL41 | LEIB4A | 52.495 | 0 | OHL | 0.0465 | 0.9017 | 35.3306 | 2779 | 2568 | 2217 | 2568 | B-2-1c
COWT2A | PYLE21 | 22.6 | 0 | OHL | 0.1334 | 0.9291 | 6.3441 | 932 | 879 | 790 | 879 | B-2-1c
CREB2A | HEDO21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1749 | 1664 | 1520 | 1664 | B-2-1c
CREB2B | SAEN21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1749 | 1664 | 1520 | 1664 | B-2-1c
CREB41 | GART4A | 32.081 | 0 | OHL | 0.0348 | 0.558 | 21.1475 | 3075 | 2876 | 2663 | 2876 | B-2-1c
CREB41 | GART4B | 32.109 | 0 | OHL | 0.0348 | 0.5585 | 21.1659 | 3326 | 3159 | 2971 | 3159 | B-2-1c
CREB41 | THTO41 | 29.671 | 0 | OHL | 0.0263 | 0.5096 | 19.9438 | 3075 | 2876 | 2663 | 2876 | B-2-1c
CREB41 | THTO42 | 29.809 | 0 | OHL | 0.0264 | 0.512 | 20.0362 | 3075 | 2876 | 2663 | 2876 | B-2-1c
CULJ4A | DIDC41 | 4.898 | 0 | OHL | 0.0064 | 0.0955 | 2.905 | 2771 | 2568 | 2217 | 2568 | B-2-1c
DISS4A | YAXL41 | 0.05 | 0 | OHL | 0 | 0.0009 | 0.0336 | 3326 | 3326 | 3326 | 3326 | B-2-1c
DISS4B | NORM41 | 29.7 | 0 | OHL | 0.0263 | 0.5101 | 19.9633 | 3326 | 3326 | 3326 | 3326 | B-2-1c
DISS4B | YAXL41 | 0.05 | 0 | OHL | 0 | 0.0009 | 0.0336 | 3326 | 3326 | 3326 | 3326 | B-2-1c
DRAK41 | HAMH41 | 29.434 | 0 | OHL | 0.0534 | 0.5857 | 17.0575 | 2009 | 1911 | 1746 | 1911 | B-2-1c
DRAK41 | RATS41 | 32.907 | 0 | OHL | 0.0489 | 0.6238 | 20.201 | 2009 | 1911 | 1746 | 1911 | B-2-1c
DRAK41 | RUGE41 | 20.966 | 0 | OHL | 0.0379 | 0.4173 | 12.1495 | 2009 | 1911 | 1746 | 1911 | B-2-1c
DRAK41 | WILE41 | 16.937 | 0 | OHL | 0.0208 | 0.3015 | 11.0841 | 2009 | 1911 | 1746 | 1911 | B-2-1c
DRAX41 | FENW4A | 13.443 | 0 | OHL | 0.0146 | 0.2338 | 8.8618 | 3180 | 3000 | 2692 | 3000 | B-2-1c
DRAX41 | THTO42 | 22.579 | 0 | OHL | 0.0198 | 0.3877 | 15.2046 | 3075 | 2876 | 2663 | 2876 | B-2-1c
DRAX42 | EGGB41 | 11.188 | 0 | OHL | 0.0124 | 0.1983 | 7.2605 | 2973 | 2778 | 2447 | 2778 | B-2-1c
DRAX42 | THOM41 | 21.73 | 0 | OHL | 0.0311 | 0.3992 | 13.6444 | 2981 | 2867 | 2248 | 2505 | B-2-1c
DRAX42 | THTO41 | 22.579 | 0 | OHL | 0.0198 | 0.3877 | 15.2046 | 3075 | 2876 | 2663 | 2876 | B-2-1c
DUNG41 | NINF41 | 44.081 | 0 | OHL | 0.0391 | 0.7571 | 29.6278 | 3065 | 2829 | 2418 | 2829 | B-2-1c
DUNG41 | NINF41 | 44.056 | 0 | OHL | 0.0391 | 0.7567 | 29.6111 | 3066 | 2830 | 2418 | 2830 | B-2-1c
DUNG41 | SELL4E | 25.387 | 0 | OHL | 0.0395 | 0.4871 | 15.2346 | 3066 | 2830 | 2418 | 2830 | B-2-1c
DUNG41 | SELL4F | 25.403 | 0 | OHL | 0.0396 | 0.4874 | 15.2441 | 3066 | 2830 | 2418 | 2830 | B-2-1c
EASO4A | RYHA4B | 58.769 | 0 | OHL | 0.0521 | 1.0095 | 39.5649 | 2779 | 2569 | 2217 | 2569 | B-2-1c
EASO4B | RYHA4A | 58.95 | 0 | OHL | 0.0522 | 1.0126 | 39.6863 | 3326 | 3160 | 2971 | 3160 | B-2-1c
EASO4B | WYMO41 | 35.272 | 0 | OHL | 0.0313 | 0.6059 | 23.7466 | 2779 | 2568 | 2217 | 2568 | B-2-1c
ECLA41 | LEIB4B | 15.985 | 0 | OHL | 0.0141 | 0.2745 | 10.7511 | 2779 | 2568 | 2217 | 2568 | B-2-1c
ECLA41 | PAFB4A | 44.72 | 0 | OHL | 0.0814 | 0.8898 | 25.9172 | 2009 | 1911 | 1746 | 1911 | B-2-1c
ECLA41 | PAFB4B | 44.886 | 0 | OHL | 0.0817 | 0.8931 | 26.0131 | 2009 | 1911 | 1746 | 1911 | B-2-1c
EGGB41 | MONF4A | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 1970 | 1970 | 1970 | 1970 | B-2-1c
EGGB42 | FERR4A | 11.864 | 0 | OHL | 0.0128 | 0.2063 | 7.8228 | 2779 | 2568 | 2217 | 2568 | B-2-1c
EGGB42 | MONF41 | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 2779 | 2568 | 2217 | 2568 | B-2-1c
EGGB42 | STSB4B | 48.084 | 0 | OHL | 0.052 | 0.8361 | 31.7071 | 2779 | 2568 | 2217 | 2568 | B-2-1c
ELLA21 | FERR22 | 45.565 | 0 | OHL | 0.1573 | 1.8245 | 13.1474 | 1324 | 1260 | 1151 | 1260 | B-2-1c
ELLA21 | STAL21 | 39.6 | 0 | OHL | 0.1647 | 1.6624 | 10.8691 | 955 | 882 | 762 | 882 | B-2-1c
ELST4A | SUND41 | 34.834 | 0 | OHL | 0.0556 | 0.6699 | 20.9635 | 2400 | 2300 | 2140 | 2300 | B-2-1c
ENDE41 | PAFB4A | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911 | B-2-1c
ENDE41 | PAFB4B | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911 | B-2-1c
ENDE41 | RATS41 | 36.941 | 0 | OHL | 0.0399 | 0.5872 | 26.8034 | 2779 | 2568 | 2217 | 2568 | B-2-1c
ENDE41 | RATS41 | 36.873 | 0 | OHL | 0.0398 | 0.5862 | 26.7543 | 2779 | 2568 | 2217 | 2568 | B-2-1c
EXET41 | TAUN41 | 38.147 | 0 | OHL | 0.0694 | 0.759 | 22.1074 | 2009 | 1911 | 1746 | 1911 | B-2-1c
EXET41 | TAUN42 | 38.107 | 0 | OHL | 0.0693 | 0.7582 | 22.0842 | 2009 | 1911 | 1746 | 1911 | B-2-1c
FAWL41 | MANN41 | 61.115 | 0 | OHL | 0.066 | 1.0014 | 43.0253 | 2779 | 2568 | 2217 | 2568 | B-2-1c
FAWL41 | MAWO41 | 18.639 | 0 | OHL | 0.0214 | 0.3062 | 13.1667 | 2423 | 2327 | 2167 | 2327 | B-2-1c
FECK41 | HAMH41 | 43.314 | 0 | OHL | 0.078 | 0.8621 | 25.1018 | 2009 | 1911 | 1746 | 1911 | B-2-1c
FECK41 | IRON41 | 66.123 | 0 | OHL | 0.123 | 1.3148 | 38.3377 | 2009 | 1911 | 1746 | 1911 | B-2-1c
FENW4A | KEAD42 | 42.517 | 0 | OHL | 0.0198 | 0.2161 | 24.6399 | 3075 | 2876 | 2663 | 2876 | B-2-1c
FENW4A | THOM42 | 8.287 | 0 | OHL | 0.0165 | 0.1653 | 4.7826 | 2009 | 1911 | 1746 | 1911 | B-2-1c
FERR21 | MONF21 | 4.485 | 0 | OHL | 0.0103 | 0.1651 | 1.3966 | 1372 | 1307 | 1207 | 1307 | B-2-1c
FERR23 | FERR2A | 0.586 | 0 | OHL | 0.0013 | 0.0216 | 0.1825 | 1381 | 1307 | 1227 | 1307 | B-2-1c
FERR2A | MONF22 | 3.922 | 0 | OHL | 0.009 | 0.1444 | 1.2212 | 1204 | 1115 | 1018 | 1115 | B-2-1c
FFES22 | TRAW21 | 7.358 | 0 | OHL | 0.0772 | 0.3075 | 2.0153 | 551 | 512 | 442 | 512 | B-2-1c
FIDF21 | FROD21 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213 | B-2-1c
FIDF21 | FROD22 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213 | B-2-1c
FIDF21 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213 | B-2-1c
FIDF21 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213 | B-2-1c
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 3140 | 3086 | 2999 | 3086 | B-2-1c
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 3140 | 3086 | 2999 | 3086 | B-2-1c
FOUR21 | HARK24 | 55.711 | 0 | OHL | 0.3289 | 2.3608 | 15.2112 | 854 | 795 | 700 | 795 | B-2-1c
FOUR21 | STEW21 | 27.731 | 0 | OHL | 0.1637 | 1.1751 | 7.5717 | 854 | 795 | 700 | 795 | B-2-1c
FRIS4A | SIZE41 | 7.61 | 0 | OHL | 0.0083 | 0.1324 | 5.0166 | 2779 | 2568 | 2217 | 2568 | B-2-1c
FRIS4B | SIZE41 | 7.61 | 0 | OHL | 0.0083 | 0.1324 | 5.0166 | 2779 | 2568 | 2217 | 2568 | B-2-1c
FRIS4C | LEIS4A | 6.8 | 0 | OHL | 0.0074 | 0.1183 | 4.4826 | 2779 | 2569 | 2217 | 2569 | B-2-1c
FRIS4D | SIZE41 | 7.61 | 0 | OHL | 0.0083 | 0.1324 | 5.0166 | 2779 | 2568 | 2217 | 2568 | B-2-1c
FROD41 | ROCK41 | 1.197 | 0 | OHL | 0.0022 | 0.0238 | 0.6917 | 1100 | 1100 | 1100 | 1100 | B-2-1c
GART4A | HUMR41 | 37.372 | 0 | OHL | 0.0413 | 0.7015 | 23.0779 | 3156 | 3032 | 2823 | 3032 | B-2-1c
GART4A | KEAD43 | 5.711 | 0 | OHL | 0.0062 | 0.0993 | 3.7642 | 3075 | 2876 | 2663 | 2876 | B-2-1c
GART4B | KILL41 | 34.462 | 0 | OHL | 0.038 | 0.6467 | 21.2883 | 3156 | 3032 | 2823 | 3032 | B-2-1c
GRAI41 | MEDW41 | 2.5 | 0 | OHL | 0.0054 | 0.0513 | 1.3945 | 1390 | 1390 | 1390 | 1390 | B-2-1c
GREN41 | MARH4A | 28.74 | 0 | OHL | 0.0522 | 0.5717 | 16.6594 | 2514 | 2439 | 2314 | 2439 | B-2-1c
GREN41 | MARH4B | 28.56 | 0 | OHL | 0.052 | 0.5682 | 16.5517 | 2009 | 1912 | 1746 | 1912 | B-2-1c
GRIW41 | KEAD41 | 49.379 | 0 | OHL | 0.047 | 0.873 | 32.3362 | 3075 | 2876 | 2663 | 2876 | B-2-1c
GRIW41 | SHBA41 | 12.673 | 0 | OHL | 0.0127 | 0.2284 | 8.1498 | 2860 | 2720 | 2484 | 2720 | B-2-1c
GWYN4A | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568 | B-2-1c
GWYN4B | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568 | B-2-1c
HAKB1- | HARK13 | 1 | 0 | OHL | 0.7047 | 2.0317 | 0.451 | 132 | 123 | 106 | 123 | B-2-1c
HAKB4B | HARK41 | 9.857 | 0 | OHL | 0.0176 | 0.1957 | 5.7308 | 2170 | 2084 | 1941 | 2084 | B-2-1c
HAMB4A | HEYS41 | 25.85 | 0 | OHL | 0.0229 | 0.444 | 17.3733 | 3326 | 3299 | 3098 | 3299 | B-2-1c
HAMB4B | HEYS41 | 26.02 | 0 | OHL | 0.0231 | 0.4469 | 17.4871 | 3326 | 3326 | 3152 | 3326 | B-2-1c
HAMH2A | NECH21 | 10.439 | 0 | OHL | 0.0263 | 0.4067 | 3.0955 | 1362 | 1285 | 1202 | 1285 | B-2-1c
HARK41 | HUTT41 | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2663 | 2771 | B-2-1c
HARK41 | HUTT43 | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2771 | 2771 | B-2-1c
HARM21 | HATL21 | 13.983 | 0 | OHL | 0.0472 | 0.5702 | 3.9648 | 1093 | 1031 | 925 | 1031 | B-2-1c
HARM21 | HAWP21 | 17.287 | 0 | OHL | 0.0584 | 0.7033 | 4.9126 | 1204 | 1115 | 1018 | 1115 | B-2-1c
HATL21 | HAWP2A | 31.443 | 0 | OHL | 0.1066 | 1.2811 | 8.9228 | 1093 | 1031 | 926 | 1031 | B-2-1c
HATL21 | SALH21 | 7.794 | 0 | OHL | 0.0327 | 0.3353 | 2.0878 | 1381 | 1279 | 1157 | 1279 | B-2-1c
HATL21 | TODP21 | 18.433 | 0 | OHL | 0.0713 | 0.7756 | 5.0465 | 1381 | 1279 | 1157 | 1279 | B-2-1c
HAWP21 | OFFE21 | 9.514 | 0 | OHL | 0.0379 | 0.3948 | 2.6412 | 1093 | 1031 | 925 | 1031 | B-2-1c
HAWP2A | WBOL21 | 17.721 | 0 | OHL | 0.0705 | 0.7355 | 4.9196 | 1176 | 1119 | 1024 | 1119 | B-2-1c
HEDO21 | SAES21 | 0.605 | 0 | OHL | 0.0017 | 0.0226 | 0.1876 | 1749 | 1664 | 1520 | 1664 | B-2-1c
HEYS41 | MIDL41 | 0.9 | 0 | OHL | 0.0008 | 0.0155 | 0.6049 | 3326 | 3160 | 2971 | 3160 | B-2-1c
HEYS41 | QUER4B | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3326 | 3299 | 3098 | 3299 | B-2-1c
HIGM21 | THUR2A | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 626 | 591 | 535 | 591 | B-2-1c
HIGM4A | STOB41 | 39.671 | 0 | OHL | 0.0722 | 0.7893 | 22.9886 | 2147 | 2056 | 1904 | 2056 | B-2-1c
HINP41 | SHUR41 | 1.2 | 0 | OHL | 0.0019 | 0.0235 | 0.7057 | 3103 | 3048 | 2959 | 3048 | B-2-1c
HINP41 | SHUR41 | 1.213 | 0 | OHL | 0.002 | 0.024 | 0.707 | 3103 | 3048 | 2959 | 3048 | B-2-1c
HUMR41 | KILL41 | 2.879 | 0 | OHL | 0.0032 | 0.0543 | 1.7706 | 2771 | 2771 | 2771 | 2771 | B-2-1c
HUTT41 | QUER4A | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048 | B-2-1c
HUTT41 | QUER4B | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048 | B-2-1c
INDQ41 | LAND41 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 2199 | 2092 | 1911 | 2092 | B-2-1c
INDQ41 | LAND42 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 1389 | 1284 | 1108 | 1284 | B-2-1c
IROA11 | OLDS12 | 1 | 0 | OHL | 0.298 | 2.366 | 3.453 | 452 | 423 | 365 | 372 | B-2-1c
IROA12 | OLDS12 | 1 | 0 | OHL | 0.297 | 2.361 | 2.693 | 457 | 424 | 366 | 372 | B-2-1c
IROA21 | WHSO2A | 34.621 | 0 | OHL | 0.2033 | 1.4667 | 9.4554 | 750 | 750 | 715 | 750 | B-2-1c
IROA21 | WHSO2B | 34.555 | 0 | OHL | 0.2034 | 1.4638 | 9.4375 | 750 | 750 | 715 | 750 | B-2-1c
IRON41 | LEGA4B | 62.073 | 0 | OHL | 0.0991 | 1.1937 | 37.3273 | 2002 | 2002 | 2002 | 2002 | B-2-1c
IRON41 | PENN4A | 27.761 | 0 | OHL | 0.0574 | 0.5549 | 15.9851 | 1389 | 1284 | 1108 | 1284 | B-2-1c
IRON41 | PENN4B | 24.617 | 0 | OHL | 0.0488 | 0.491 | 14.2132 | 1590 | 1500 | 1346 | 1500 | B-2-1c
IRON41 | RUGE41 | 58.681 | 0 | OHL | 0.1135 | 1.1701 | 33.9045 | 1389 | 1284 | 1108 | 1284 | B-2-1c
IRON41 | SHRE4A | 15.129 | 0 | OHL | 0.0242 | 0.2909 | 9.0977 | 2397 | 2302 | 2144 | 2302 | B-2-1c
KEAD42 | WBUR42 | 28.425 | 0 | OHL | 0.0252 | 0.4882 | 19.1053 | 3326 | 3249 | 3098 | 3249 | B-2-1c
KEAD43 | KILL41 | 41.067 | 0 | OHL | 0.0403 | 0.7345 | 26.6033 | 3060 | 2931 | 2715 | 2931 | B-2-1c
KEAD43 | WBUR41 | 28.266 | 0 | OHL | 0.0251 | 0.4855 | 18.9976 | 3326 | 3249 | 3098 | 3249 | B-2-1c
KEAR41 | PADI41 | 39.101 | 0 | OHL | 0.0567 | 0.7296 | 24.2055 | 2169 | 2084 | 1940 | 2084 | B-2-1c
KEMS41 | LOFI4A | 38.035 | 0 | OHL | 0.0623 | 0.726 | 23.0007 | 3102 | 2935 | 2765 | 2935 | B-2-1c
KEMS41 | LOFI4B | 37.572 | 0 | OHL | 0.0617 | 0.7176 | 22.7061 | 3102 | 2935 | 2765 | 2935 | B-2-1c
KIBY21 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339 | B-2-1c
KIBY21 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339 | B-2-1c
KIBY21 | WASF2A | 10.945 | 0 | OHL | 0.0414 | 0.4478 | 3.0891 | 1521 | 1461 | 1360 | 1461 | B-2-1c
KIBY21 | WASF2B | 10.978 | 0 | OHL | 0.0415 | 0.4491 | 3.0984 | 1521 | 1461 | 1360 | 1461 | B-2-1c
KILL41 | SHBA41 | 17.05 | 0 | OHL | 0.0179 | 0.3134 | 10.7556 | 2860 | 2720 | 2484 | 2720 | B-2-1c
KINO41 | NFLE41 | 23.626 | 0 | OHL | 0.0284 | 0.4216 | 15.2234 | 3102 | 2935 | 2692 | 2935 | B-2-1c
KINO41 | SING41 | 17.685 | 0 | OHL | 0.0192 | 0.3076 | 11.6582 | 2889 | 2748 | 2510 | 2748 | B-2-1c
KNAR21 | POPP21 | 49.192 | 0 | OHL | 0.3299 | 2.3254 | 12.2192 | 551 | 512 | 442 | 512 | B-2-1c
LACK21 | TODP21 | 5.965 | 0 | OHL | 0.0212 | 0.2477 | 1.654 | 1408 | 1332 | 1251 | 1332 | B-2-1c
LAGA41 | LAND41 | 21.224 | 0 | OHL | 0.0339 | 0.4081 | 12.7621 | 2423 | 2327 | 2168 | 2327 | B-2-1c
LAGA41 | LAND42 | 21.355 | 0 | OHL | 0.0341 | 0.4108 | 12.8369 | 2423 | 2327 | 2168 | 2327 | B-2-1c
LALE21 | WWEY2A | 8.395 | 0 | OHL | 0.0317 | 0.3434 | 2.3695 | 1316 | 1213 | 1104 | 1213 | B-2-1c
LEGA41 | TREU4A | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720 | B-2-1c
LEGA41 | TREU4B | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720 | B-2-1c
LEGA4A | SHRE4A | 46.944 | 0 | OHL | 0.075 | 0.9028 | 28.2295 | 2002 | 2002 | 2002 | 2002 | B-2-1c
LEIB4A | SUND42 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568 | B-2-1c
LEIB4B | SUND41 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568 | B-2-1c
LEIS4A | SIZE41 | 0.81 | 0 | OHL | 0.0009 | 0.0141 | 0.534 | 2779 | 2569 | 2217 | 2569 | B-2-1c
LITT41 | LOFI4A | 8.152 | 0 | OHL | 0.0127 | 0.157 | 4.8712 | 3103 | 3048 | 2959 | 3048 | B-2-1c
LITT41 | LOFI4B | 8.152 | 0 | OHL | 0.0127 | 0.157 | 4.8712 | 3103 | 3048 | 2959 | 3048 | B-2-1c
LOFI4A | ROWD4A | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1500 | 1346 | 1500 | B-2-1c
LOFI4B | ROWD4B | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1500 | 1346 | 1500 | B-2-1c
LOVE41 | NURS41 | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2771 | 2568 | 2217 | 2568 | B-2-1c
LOVE41 | NURS4A | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2779 | 2568 | 2217 | 2568 | B-2-1c
MACC41 | STAL4B | 31.196 | 0 | OHL | 0.062 | 0.617 | 18.1761 | 1710 | 1627 | 1488 | 1627 | B-2-1c
MAGA21 | PYLE21 | 6.238 | 0 | OHL | 0.0211 | 0.2537 | 1.7667 | 1204 | 1115 | 1018 | 1115 | B-2-1c
MANN41 | NURS4A | 39.823 | 0 | OHL | 0.043 | 0.6631 | 27.5672 | 2779 | 2568 | 2217 | 2568 | B-2-1c
MARH4A | STAY41 | 73.027 | 0 | OHL | 0.1328 | 1.4529 | 42.3252 | 2514 | 2439 | 2314 | 2439 | B-2-1c
MARV41 | MARV4A | 0.145 | 0 | OHL | 0.0003 | 0.0029 | 0.0839 | 2009 | 2009 | 2009 | 2009 | B-2-1c
MARV41 | MARV4B | 0.077 | 0 | OHL | 0.0001 | 0.0015 | 0.0446 | 2009 | 2009 | 2009 | 2009 | B-2-1c
MAWO41 | NURS41 | 7.441 | 0 | OHL | 0.0093 | 0.1281 | 5.0417 | 2423 | 2327 | 2167 | 2327 | B-2-1c
MEDB4A | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3326 | 3326 | 3326 | B-2-1c
MEDB4A | STWB4R | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3326 | 3326 | 3326 | B-2-1c
MEDB4B | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3326 | 3326 | 3326 | B-2-1c
MEDB4B | STWB4Q | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3326 | 3326 | 3326 | B-2-1c
MELK41 | MITY41 | 28.101 | 0 | OHL | 0.0511 | 0.5591 | 16.2853 | 2105 | 2016 | 1867 | 2016 | B-2-1c
MELK41 | MITY41 | 28.052 | 0 | OHL | 0.051 | 0.5581 | 16.257 | 2105 | 2016 | 1867 | 2016 | B-2-1c
MELK41 | SEAB41 | 53.558 | 0 | OHL | 0.0598 | 0.9451 | 34.8897 | 2545 | 2421 | 2211 | 2421 | B-2-1c
MIDL41 | QUER4A | 9.704 | 0 | OHL | 0.0086 | 0.1667 | 6.5225 | 3326 | 3159 | 2971 | 3159 | B-2-1c
MONF22 | POPP21 | 37.84 | 0 | OHL | 0.208 | 2.0034 | 8.337 | 682 | 629 | 538 | 629 | B-2-1c
MONF41 | PADI41 | 87.848 | 0 | OHL | 0.1064 | 1.6286 | 54.7416 | 2518 | 2395 | 2188 | 2395 | B-2-1c
NECT4A | NORM41 | 35.652 | 0 | OHL | 0.0316 | 0.6124 | 23.9626 | 3326 | 3326 | 3317 | 3326 | B-2-1c
NECT4A | WALP41 | 43.459 | 0 | OHL | 0.0385 | 0.7464 | 29.2107 | 3326 | 3326 | 3317 | 3326 | B-2-1c
NECT4B | NORM41 | 35.652 | 0 | OHL | 0.0316 | 0.6124 | 23.9626 | 3326 | 3258 | 3060 | 3258 | B-2-1c
NECT4B | WALP41 | 43.459 | 0 | OHL | 0.0385 | 0.7464 | 29.2107 | 3326 | 3160 | 2971 | 3160 | B-2-1c
NEEP4A | STSB4B | 12.801 | 0 | OHL | 0.0276 | 0.2627 | 7.1402 | 2779 | 2568 | 2217 | 2568 | B-2-1c
NFLE41 | SING41 | 5.941 | 0 | OHL | 0.0093 | 0.114 | 3.5652 | 2889 | 2748 | 2510 | 2748 | B-2-1c
NFLE41 | WTHU4A | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907 | B-2-1c
NFLE41 | WTHU4B | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907 | B-2-1c
NORT21 | SALH21 | 12.178 | 0 | OHL | 0.0464 | 0.526 | 3.2482 | 1381 | 1293 | 1197 | 1293 | B-2-1c
NORT41 | OSBA41 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911 | B-2-1c
NORT41 | OSBA42 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911 | B-2-1c
NORT41 | SALH42 | 12.206 | 0 | OHL | 0.022 | 0.2492 | 6.888 | 1831 | 1739 | 1588 | 1739 | B-2-1c
NORW11 | NOTR11 | 1 | 0 | OHL | 0.236 | 0.778 | 0.315 | 265 | 246 | 212 | 246 | B-2-1c
NORW12 | NOTR12 | 1 | 0 | OHL | 0.2362 | 0.778 | 0.3149 | 350 | 350 | 350 | 350 | B-2-1c
OCKH21 | OLDB2A | 5.46 | 0 | OHL | 0.0208 | 0.2294 | 1.4988 | 772 | 772 | 619 | 619 | B-2-1c
OCKH2A | WIEN2B | 4.67 | 0 | OHL | 0.0213 | 0.1977 | 1.2665 | 760 | 760 | 760 | 760 | B-2-1c
OFFE21 | WBOL21 | 8.207 | 0 | OHL | 0.0327 | 0.3406 | 2.2784 | 1176 | 1115 | 1018 | 1115 | B-2-1c
OSBA42 | THTO41 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2779 | 2568 | 2217 | 2568 | B-2-1c
PADI41 | PEWO4B | 37.608 | 0 | OHL | 0.0556 | 0.7049 | 23.1779 | 2169 | 2084 | 1940 | 2084 | B-2-1c
PELH41 | SUND42 | 45.13 | 0 | OHL | 0.0487 | 0.752 | 31.2185 | 3180 | 3000 | 2692 | 3000 | B-2-1c
PEMB41 | SWAN42 | 84.57 | 0 | OHL | 0.0918 | 1.4709 | 55.7496 | 2779 | 2568 | 2217 | 2568 | B-2-1c
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568 | B-2-1c
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568 | B-2-1c
PEWO2C | WASF2A | 23.481 | 0 | OHL | 0.0887 | 0.9606 | 6.6274 | 1521 | 1461 | 1360 | 1461 | B-2-1c
PEWO2D | WASF2B | 23.521 | 0 | OHL | 0.0889 | 0.9623 | 6.6386 | 1521 | 1461 | 1360 | 1461 | B-2-1c
PEWO41 | QUER4A | 31.939 | 0 | OHL | 0.0498 | 0.6128 | 19.1665 | 3102 | 3048 | 2853 | 3048 | B-2-1c
PEWO41 | QUER4B | 32.087 | 0 | OHL | 0.05 | 0.6156 | 19.2551 | 3102 | 3048 | 2853 | 3048 | B-2-1c
RATS41 | WILE41 | 21.684 | 0 | OHL | 0.0394 | 0.4314 | 12.5666 | 2009 | 1911 | 1746 | 1911 | B-2-1c
RAYL41 | TILB4A | 20.499 | 0 | OHL | 0.0319 | 0.3933 | 12.3014 | 3102 | 2935 | 2765 | 2935 | B-2-1c
RHIG41 | SWAN41 | 34.34 | 0 | OHL | 0.0373 | 0.5973 | 22.6374 | 2779 | 2568 | 2217 | 2568 | B-2-1c
ROCH21 | STAL21 | 31.256 | 0 | OHL | 0.1235 | 1.3183 | 8.54 | 1324 | 1260 | 1151 | 1260 | B-2-1c
RYEH4A | RYEH43 | 0.264 | 0 | OHL | 0.0004 | 0.0051 | 0.1585 | 2779 | 2569 | 2217 | 2569 | B-2-1c
RYEH4B | RYEH42 | 0.215 | 0 | OHL | 0.0003 | 0.0041 | 0.1291 | 2779 | 2569 | 2217 | 2569 | B-2-1c
SAEN21 | SAES21 | 0.484 | 0 | OHL | 0.0013 | 0.018 | 0.1501 | 1749 | 1664 | 1520 | 1664 | B-2-1c
SAFO41 | SEAB41 | 31.28 | 0 | OHL | 0.0345 | 0.5479 | 20.4859 | 3190 | 3060 | 2850 | 3060 | B-2-1c
SELL4B | SELL4C | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3326 | 3159 | 2971 | 3159 | B-2-1c
SELL4B | SELL4D | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3326 | 3326 | 3326 | 3326 | B-2-1c
SELL4B | SELL4E | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3159 | 2971 | 3159 | B-2-1c
SELL4B | SELL4F | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3159 | 2971 | 3159 | B-2-1c
SHRE4A | SHRE4B | 0.054 | 0 | OHL | 0.0001 | 0.001 | 0.0324 | 240 | 240 | 240 | 240 | B-2-1c
SHUR41 | TAUN41 | 27 | 0 | OHL | 0.0487 | 0.5369 | 15.6574 | 2213 | 2126 | 1980 | 2126 | B-2-1c
SHUR41 | TAUN42 | 27 | 0 | OHL | 0.0487 | 0.5369 | 15.6574 | 2213 | 2126 | 1980 | 2126 | B-2-1c
SPLN41 | WALP41 | 29.234 | 0 | OHL | 0.0272 | 0.5117 | 19.3195 | 3189 | 3063 | 2853 | 3063 | B-2-1c
SSHI22 | TYNE2A | 7.028 | 0 | OHL | 0.031 | 0.2985 | 1.9072 | 1247 | 1180 | 1065 | 1180 | B-2-1c
SSHI22 | WBOL21 | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1176 | 1119 | 1024 | 1119 | B-2-1c
STEN11 | STES11 | 1 | 0 | OHL | 0.0266 | 0.1193 | 0.1077 | 198 | 198 | 181 | 181 | B-2-1c
SWAN41 | SWAN4B | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 3048 | 3048 | 2971 | 3048 | B-2-1c
SWAN42 | SWAN4A | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 1389 | 1284 | 1108 | 1284 | B-2-1c
THUR21 | THUR2A | 4.653 | 0 | OHL | 0.0488 | 0.1944 | 1.2745 | 551 | 512 | 442 | 512 | B-2-1c
THUR2A | WMEL21 | 16.348 | 0 | OHL | 0.0746 | 0.7099 | 4.3235 | 955 | 882 | 762 | 882 | B-2-1c
TILB21 | WARL21 | 13.065 | 0 | OHL | 0.0597 | 0.553 | 3.5441 | 1175 | 1119 | 1023 | 1119 | B-2-1c
TILB21 | WARL21 | 12.897 | 0 | OHL | 0.059 | 0.5459 | 3.4987 | 1175 | 1119 | 1023 | 1119 | B-2-1c
TILB41 | TILB4A | 0.058 | 0 | OHL | 0.0001 | 0.0012 | 0.033 | 3102 | 3048 | 2958 | 3048 | B-2-1c
TILB41 | TILB4B | 0.059 | 0 | OHL | 0.0001 | 0.0011 | 0.0353 | 3102 | 3048 | 2853 | 3048 | B-2-1c
TRAW41 | TREU4A | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5731 | 3102 | 3048 | 2958 | 3048 | B-2-1c
TREM21 | USKM2A | 15.048 | 0 | OHL | 0.0854 | 0.7095 | 3.7487 | 695 | 641 | 548 | 641 | B-2-1c
TYNE21 | WBOL21 | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1131 | 1052 | 912 | 1052 | B-2-1c
USKM21 | USKM2A | 0.692 | 0 | OHL | 0.0038 | 0.036 | 0.1546 | 695 | 642 | 548 | 642 | B-2-1c
USKM21 | USKM2B | 0.391 | 0 | OHL | 0.0039 | 0.0167 | 0.1052 | 682 | 629 | 538 | 629 | B-2-1c
USKM21 | WHSO21 | 5.841 | 0 | OHL | 0.0345 | 0.2401 | 1.6394 | 1005 | 956 | 874 | 956 | B-2-1c
USKM21 | WHSO22 | 5.849 | 0 | OHL | 0.0345 | 0.2405 | 1.6417 | 1005 | 956 | 873 | 956 | B-2-1c
USKM2A | WHSO21 | 5.562 | 0 | OHL | 0.0306 | 0.289 | 1.2455 | 695 | 641 | 548 | 641 | B-2-1c
USKM2B | WHSO22 | 5.851 | 0 | OHL | 0.0322 | 0.304 | 1.3103 | 682 | 629 | 538 | 629 | B-2-1c
WHSO41 | WHSO4A | 0.077 | 0 | OHL | 0.0001 | 0.0013 | 0.0506 | 992 | 916 | 783 | 916 | B-2-1c
CHAR1S | GLAG1S | 1.4 | 0 | OHL | 0.1274 | 0.3262 | 0.07 | 126 | 117 | 101 | 117 | B-2-2a | 2025 | Addition
CHAR1T | GLAG1T | 1.4 | 0 | OHL | 0.1274 | 0.3262 | 0.07 | 126 | 117 | 101 | 117 | B-2-2a | 2025 | Addition
GREM1L | GREM1P | 2.3 | 0 | OHL | 0.115 | 0.4761 | 0.129 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Addition
GREM1M | KERG1M | 0 | 11.1 | OHL | 0.555 | 2.2977 | 0.622 | 203 | 193 | 176 | 193 | B-2-2a | 2025 | Addition
GREM1Q | KERG1L | 0 | 7.94 | OHL | 0.397 | 1.6436 | 0.445 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Addition
INRU1Q | PEHE1- | 6.7 | 0 | OHL | 0.3417 | 1.5008 | 0.348 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Change
INRU1R | PEHE1- | 6.7 | 0 | OHL | 0.3417 | 1.5008 | 0.348 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Change
LIMK1- | LIMK1A | 4.9 | 0 | OHL | 0.245 | 1.014 | 0.652 | 203 | 193 | 176 | 193 | B-2-2a | 2025 | Addition
ABED1- | DUNM1T | 5 | 0 | OHL | 0.25 | 1.035 | 0.28 | 163 | 152 | 131 | 152 | B-2-2a | 2027 | Addition
ACHE1- | SHIN1- | 17.5 | 0 | OHL | 0.875 | 3.6225 | 0.98 | 203 | 193 | 176 | 193 | B-2-2a | 2027 | Addition
AIGN1A | KION1A | 2.92 | 0 | OHL | 0.264 | 0.594 | 0.66 | 111 | 103 | 89 | 103 | B-2-2a | 2027 | Addition
BAGP2- | BAGP2J | 0.25 | 0 | OHL | 0.01 | 0.0138 | 0.053 | 965 | 925 | 865 | 925 | B-2-2a | 2027 | Addition
BAGP2- | BAGP2K | 0.25 | 0 | OHL | 0.01 | 0.0138 | 0.053 | 965 | 925 | 865 | 925 | B-2-2a | 2027 | Addition
BEAU1J | KION1B | 1.5 | 0 | OHL | 0.0295 | 0.0433 | 1.175 | 251 | 252 | 252 | 252 | B-2-2a | 2027 | Addition
BEAU1K | KION1A | 1.5 | 0 | OHL | 0.0295 | 0.0433 | 1.175 | 251 | 252 | 252 | 252 | B-2-2a | 2027 | Addition
BEAU2J | FYRI2J | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 702 | 665 | 599 | 665 | B-2-2a | 2027 | Change
BEAU2K | FYRI2K | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 702 | 665 | 599 | 665 | B-2-2a | 2027 | Change
BERB2Q | CAID2- | 7.99 | 0 | OHL | 0.0452 | 0.3288 | 2.178 | 935 | 880 | 790 | 880 | B-2-2a | 2027 | Addition
BLEX1A | BLEX1B | 14.4 | 0 | OHL | 0.7191 | 3.2528 | 0.79 | 203 | 193 | 176 | 193 | B-2-2a | 2027 | Addition
BLHI1J | ELCH1- | 24 | 0 | OHL | 1.209 | 4.97 | 1.344 | 203 | 193 | 176 | 193 | B-2-2a | 2027 | Addition
BLHI2J | CLGO2A | 45.8 | 0 | OHL | 0.2593 | 1.8854 | 12.487 | 935 | 880 | 790 | 880 | B-2-2a | 2027 | Addition
CAID2- | KNOC2J | 0 | 38.99 | OHL | 0.2208 | 1.6052 | 10.631 | 935 | 880 | 790 | 880 | B-2-2a | 2027 | Addition
CLGO2- | KNOC2K | 0 | 47.45 | OHL | 0.2687 | 1.9535 | 12.938 | 935 | 880 | 790 | 880 | B-2-2a | 2027 | Addition
CONN1D | STSO1A | 12.2 | 0 | OHL | 0.6059 | 2.5084 | 0.6786 | 203 | 193 | 176 | 193 | B-2-2a | 2027 | Addition
CONN2J | DOUN2- | 10.34 | 0 | OHL | 0.0621 | 0.5689 | 2.193 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
CONN2K | DOUN2- | 10.34 | 0 | OHL | 0.0621 | 0.5689 | 2.193 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
CONN2K | GORW2- | 47.76 | 0 | OHL | 0.2866 | 2.6272 | 10.127 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
CULL1Q | DEAW1A | 9 | 0 | OHL | 0.93 | 2.12 | 0.45 | 111 | 103 | 89 | 103 | B-2-2a | 2027 | Addition
CULL1Q | KION1B | 12.6 | 0 | OHL | 1.287 | 2.952 | 0.621 | 111 | 103 | 89 | 103 | B-2-2a | 2027 | Addition
DELL1A | DELL1B | 7.2 | 0 | OHL | 0.2304 | 1.5696 | 0.382 | 280 | 270 | 245 | 270 | B-2-2a | 2027 | Addition
DLCH1B | LAIS1A | 3.7 | 0 | OHL | 0.0869 | 0.8073 | 0.195 | 464 | 446 | 414 | 446 | B-2-2a | 2027 | Addition
DOUN2- | BAGP2J | 5 | 0 | OHL | 0.025 | 0.275 | 1.065 | 965 | 925 | 865 | 925 | B-2-2a | 2027 | Addition
DUNO1Q | WHTB1S | 18.1 | 0 | OHL | 0.9231 | 4.1087 | 0.923 | 241 | 230 | 210 | 230 | B-2-2a | 2027 | Change
DUNO1R | WHTB1T | 18.1 | 0 | OHL | 0.9231 | 4.1087 | 0.923 | 241 | 230 | 210 | 230 | B-2-2a | 2027 | Change
FYRI2J | LOCB2K | 35.93 | 0 | OHL | 0.2156 | 1.9762 | 7.617 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
FYRI2K | LOCB2J | 35.93 | 0 | OHL | 0.2156 | 1.9762 | 7.617 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
GILB1L | THUS1L | 13.1 | 0 | OHL | 0.303 | 2.776 | 0.72 | 463 | 444 | 415 | 444 | B-2-2a | 2027 | Addition
GILB1M | THUS1M | 13.1 | 0 | OHL | 0.303 | 2.776 | 0.72 | 463 | 444 | 415 | 444 | B-2-2a | 2027 | Addition
GORW2- | STRB2- | 10.3 | 0 | OHL | 0.0618 | 0.5665 | 2.184 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
KINT4J | FETT4Q | 32.19 | 0 | OHL | 0.0644 | 0.6052 | 19.977 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2027 | Addition
KINT4K | FETT4R | 32.19 | 0 | OHL | 0.0644 | 0.6052 | 19.977 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2027 | Addition
LAIS1A | LAIS1B | 1.6 | 0 | OHL | 0.1456 | 0.3456 | 0.0864 | 111 | 103 | 89 | 103 | B-2-2a | 2027 | Addition
LAIS1A | LOCB1M | 13.3 | 0 | OHL | 0.3123 | 2.9012 | 0.703 | 464 | 446 | 414 | 446 | B-2-2a | 2027 | Addition
LOCB2K | STRB2- | 18.9 | 0 | OHL | 0.1134 | 1.0395 | 4.007 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
THUS2J | BAGP2K | 10.4 | 0 | OHL | 0.052 | 0.572 | 2.215 | 965 | 925 | 865 | 925 | B-2-2a | 2027 | Addition
ANSN2- | CRDH2J | 20.25 | 0 | OHL | 0.081 | 0.8303 | 5.711 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
ANSN2- | CRMU2J | 24.95 | 0 | OHL | 0.0998 | 1.023 | 7.036 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
ARMA1- | STCS1B | 15 | 0 | OHL | 0.49 | 2.0286 | 0.549 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
ARMO1J | DUGR1Q | 14 | 0 | OHL | 0.7 | 2.898 | 0.784 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Change
BEAU4- | BING4- | 25.3 | 0 | OHL | 0.0328 | 0.4847 | 15.298 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
BING4- | FAUG4K | 25.4 | 0 | OHL | 0.0329 | 0.4866 | 15.358 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
BLHI2A | CLGO2A | 45.8 | 0 | OHL | 0.2593 | 1.8854 | 12.487 | 935 | 880 | 790 | 880 | B-2-2a | 2029 | Addition
BLHI2B | DAAS2- | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880 | B-2-2a | 2029 | Addition
BONB4A | CMBS4B | 10.1 | 0 | OHL | 0.0131 | 0.1935 | 6.107 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
BROA1A | QUOI1Q | 63 | 0 | OHL | 1.4888 | 13.3653 | 3.474 | 465 | 445 | 415 | 445 | B-2-2a | 2029 | Addition
BROA1B | FAUG1S | 82 | 0 | OHL | 1.9378 | 17.3962 | 4.522 | 465 | 445 | 415 | 445 | B-2-2a | 2029 | Addition
BROA1C | BROA1J | 7.75 | 0 | OHL | 0.1831 | 1.6441 | 0.427 | 465 | 445 | 415 | 445 | B-2-2a | 2029 | Addition
BROA1D | BROA1K | 7.75 | 0 | OHL | 0.1831 | 1.6441 | 0.427 | 465 | 445 | 415 | 445 | B-2-2a | 2029 | Addition
CAAD1Q | TNGF1- | 1 | 0 | OHL | 0.0236 | 0.2121 | 0.055 | 448 | 430 | 398 | 430 | B-2-2a | 2029 | Addition
CHLS1- | DLCH1A | 10.5 | 0 | OHL | 0.525 | 2.1735 | 0.588 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
CLUN1S | ERRO1K | 15.4 | 0 | OHL | 0.7801 | 3.4546 | 0.795 | 241 | 230 | 210 | 230 | B-2-2a | 2029 | Change
CLUN1T | ERRO1J | 15.4 | 0 | OHL | 0.7801 | 3.4546 | 0.795 | 241 | 230 | 210 | 230 | B-2-2a | 2029 | Change
CMBS4A | KINA4B | 59.8 | 0 | OHL | 0.0775 | 1.1456 | 36.158 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
COGL4J | LOCL4J | 3.5 | 0 | OHL | 0.0045 | 0.067 | 2.116 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
COGL4K | LOCL4K | 3.5 | 0 | OHL | 0.0045 | 0.067 | 2.116 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
CONN1J | STCS1A | 11 | 0 | OHL | 0.2159 | 1.9817 | 0.689 | 335 | 320 | 290 | 320 | B-2-2a | 2029 | Addition
CONN1K | KRKN1- | 2 | 0 | OHL | 0.1 | 0.414 | 0.112 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
CONN1K | STCS1B | 11 | 0 | OHL | 0.2159 | 1.9817 | 0.689 | 335 | 320 | 290 | 320 | B-2-2a | 2029 | Addition
CRAS2- | CRDH2K | 31.48 | 0 | OHL | 0.1259 | 1.2907 | 8.877 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRAS2- | CRMU2K | 13.72 | 0 | OHL | 0.0549 | 0.5625 | 3.869 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRDH1J | KILC1Q | 4.98 | 0 | OHL | 0.7095 | 1.1715 | 0.244 | 99 | 92 | 79 | 92 | B-2-2a | 2029 | Addition
CRDH2J | DALB2A | 14 | 0 | OHL | 0.0516 | 0.5615 | 3.962 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRDH2K | DALB2B | 14 | 0 | OHL | 0.0516 | 0.5615 | 3.962 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRMU2J | ANSN2- | 24.95 | 0 | OHL | 0.0998 | 1.023 | 7.036 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRMU2J | CRSN2Q | 44.7 | 0 | OHL | 0.1788 | 1.8327 | 12.605 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRMU2K | EARR21 | 28.34 | 0 | OHL | 0.1134 | 1.1621 | 7.993 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRSN2R | EARR2A | 16.36 | 0 | OHL | 0.0654 | 0.6706 | 4.612 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRSS1J | TNGF1- | 12.08 | 0 | OHL | 0.2855 | 2.5628 | 0.666 | 448 | 430 | 398 | 430 | B-2-2a | 2029 | Addition
DUGR1Q | EDIN1J | 9.5 | 0 | OHL | 0.475 | 1.9665 | 0.532 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
EARR21 | EARR2B | 5.6 | 0 | OHL | 0.0224 | 0.2296 | 1.579 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
EARR2A | EARR2B | 5.6 | 0 | OHL | 0.0224 | 0.2296 | 1.579 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
EDIN1A | EDIN1C | 20.25 | 0 | OHL | 0.4785 | 4.296 | 1.117 | 465 | 445 | 415 | 445 | B-2-2a | 2029 | Addition
EDIN1B | EDIN1D | 20.25 | 0 | OHL | 0.4785 | 4.296 | 1.117 | 465 | 445 | 415 | 445 | B-2-2a | 2029 | Addition
EDIN1K | GLNU1- | 0.5 | 0 | OHL | 0.0118 | 0.1061 | 0.028 | 448 | 430 | 398 | 430 | B-2-2a | 2029 | Addition
ELIB1- | ELIB1A | 7.5 | 0 | OHL | 0.375 | 1.5525 | 0.42 | 241 | 230 | 210 | 230 | B-2-2a | 2029 | Addition
ENEI1N | SYEL1N | 18 | 0 | OHL | 0.9 | 3.726 | 1.008 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
FASQ1- | FASQ1J | 10 | 0 | OHL | 1 | 4.14 | 1.12 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
FAUG1R | QUOI1Q | 19 | 0 | OHL | 0.449 | 4.0308 | 1.048 | 465 | 445 | 415 | 445 | B-2-2a | 2029 | Addition
FAUG4J | LOCL4K | 8.5 | 0 | OHL | 0.0109 | 0.1627 | 5.139 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
FAUG4K | KINA4A | 80.2 | 0 | OHL | 0.104 | 1.5363 | 48.493 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
FAUG4K | LOCL4J | 8.5 | 0 | OHL | 0.0109 | 0.1627 | 5.139 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
FETT1- | GLDY1- | 19 | 0 | OHL | 0.9488 | 4.2918 | 1.068 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
FWIL1Q | LOCL1K | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247 | B-2-2a | 2029 | Addition
FWIL1R | LOCL1K | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247 | B-2-2a | 2029 | Addition
GILB1J | SLCK1- | 7.5 | 0 | OHL | 0.375 | 1.5525 | 0.42 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
INGA1Q | LOCL1K | 2.4 | 0 | OHL | 0.2184 | 0.5592 | 0.12 | 111 | 103 | 89 | 103 | B-2-2a | 2029 | Addition
INRU1Q | SALM1A | 3.05 | 0 | OHL | 0.1555 | 0.6832 | 0.158 | 241 | 230 | 210 | 230 | B-2-2a | 2029 | Addition
INRU1R | SALM1B | 3.05 | 0 | OHL | 0.1555 | 0.6832 | 0.158 | 241 | 230 | 210 | 230 | B-2-2a | 2029 | Addition
KILC1Q | CRDH1J | 4.98 | 0 | OHL | 0.7095 | 1.1715 | 0.244 | 99 | 92 | 79 | 92 | B-2-2a | 2029 | Addition
KINM2A | PEHE2- | 23.8 | 0 | OHL | 0.12 | 1.04 | 6.26 | 1090 | 1030 | 920 | 1030 | B-2-2a | 2029 | Addition
KINM2B | PERS2Q | 23.8 | 0 | OHL | 0.12 | 1.04 | 6.26 | 1090 | 1030 | 920 | 1030 | B-2-2a | 2029 | Addition
SALM1A | SFER1L | 3.05 | 0 | OHL | 0.1555 | 0.6832 | 0.158 | 241 | 230 | 210 | 230 | B-2-2a | 2029 | Addition
SALM1B | SFER1M | 3.05 | 0 | OHL | 0.1555 | 0.6832 | 0.158 | 241 | 230 | 210 | 230 | B-2-2a | 2029 | Addition
TNGF1- | TNGF1A | 21.5 | 0 | OHL | 1.075 | 4.4505 | 1.204 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
ALYT4J | EMMO4K | 16.2 | 0 | OHL | 0.0324 | 0.3078 | 10.417 | 2349 | 2266 | 2120 | 2266 | B-2-2a | 2032 | Addition
ALYT4J | FETT4R | 67.06 | 0 | OHL | 0.1341 | 1.2741 | 41.1751 | 2349 | 2266 | 2120 | 2266 | B-2-2a | 2032 | Change
ALYT4J | KINB4J | 69.22 | 0 | OHL | 0.1384 | 1.3152 | 42.501 | 2349 | 2266 | 2120 | 2266 | B-2-2a | 2032 | Change
ALYT4K | EMMO4J | 16.2 | 0 | OHL | 0.0324 | 0.3078 | 10.417 | 2349 | 2266 | 2120 | 2266 | B-2-2a | 2032 | Addition
ALYT4K | FETT4Q | 67.06 | 0 | OHL | 0.1341 | 1.2741 | 41.1751 | 2349 | 2266 | 2120 | 2266 | B-2-2a | 2032 | Change
ALYT4K | KINB4K | 69.22 | 0 | OHL | 0.1384 | 1.3152 | 42.501 | 2349 | 2266 | 2120 | 2266 | B-2-2a | 2032 | Change
BALA1A | HARI1- | 32.5 | 0 | OHL | 1.6575 | 7.28 | 1.69 | 241 | 230 | 210 | 230 | B-2-2a | 2032 | Addition
BALA1A | LEWI1J | 26 | 0 | OHL | 1.326 | 5.824 | 1.352 | 241 | 230 | 210 | 230 | B-2-2a | 2032 | Addition
BALA1A | MUAI1A | 13 | 0 | OHL | 0.65 | 2.691 | 0.728 | 203 | 193 | 176 | 193 | B-2-2a | 2032 | Addition
BALA1B | LEWI1K | 26 | 0 | OHL | 1.326 | 5.824 | 1.352 | 241 | 230 | 210 | 230 | B-2-2a | 2032 | Addition
BANN4J | CAAI4J | 85 | 0 | OHL | 0.085 | 1.445 | 58.395 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
BANN4K | CAAI4K | 85 | 0 | OHL | 0.085 | 1.445 | 58.395 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
BEAU2J | FYRI2M | 29 | 0 | OHL | 0.174 | 1.5947 | 6.147 | 780 | 750 | 700 | 750 | B-2-2a | 2032 | Addition
BEAU2K | FYRI2L | 29 | 0 | OHL | 0.174 | 1.5947 | 6.147 | 780 | 750 | 700 | 750 | B-2-2a | 2032 | Addition
BEAU4- | FNLN4A | 5 | 0 | OHL | 0.0065 | 0.0958 | 3.023 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
BEAU4- | FNLN4B | 5 | 0 | OHL | 0.0065 | 0.0958 | 3.023 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
BING4- | FNLN4A | 20.3 | 0 | OHL | 0.0263 | 0.3889 | 12.274 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
BLHI4- | COFD4A | 2.5 | 0 | OHL | 0.005 | 0.0483 | 1.471 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2032 | Addition
BLHI4- | COFD4B | 2.5 | 0 | OHL | 0.005 | 0.0483 | 1.471 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2032 | Addition
BROR1Q | DUBE1A | 34.58 | 0 | OHL | 3.1568 | 8.0501 | 1.716 | 126 | 117 | 101 | 117 | B-2-2a | 2032 | Addition
CAAI4J | FNLN4A | 82 | 0 | OHL | 0.082 | 1.394 | 56.334 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
CAAI4K | FNLN4B | 82 | 0 | OHL | 0.082 | 1.394 | 56.334 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
COFD4A | FNLN4A | 110 | 0 | OHL | 0.11 | 1.87 | 75.57 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
COFD4A | GRNS4L | 60.37 | 0 | OHL | 0.0604 | 1.0263 | 41.474 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
COFD4A | ROTI4J | 32.9 | 0 | OHL | 0.0658 | 0.635 | 19.355 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2032 | Addition
COFD4B | FNLN4B | 110 | 0 | OHL | 0.11 | 1.87 | 75.57 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
COFD4B | GRNS4M | 60.37 | 0 | OHL | 0.0604 | 1.0263 | 41.474 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
COFD4B | ROTI4K | 32.9 | 0 | OHL | 0.0658 | 0.635 | 19.355 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2032 | Addition
CONN2J | LOCB2M | 75.34 | 0 | OHL | 0.452 | 4.1437 | 15.972 | 780 | 750 | 700 | 750 | B-2-2a | 2032 | Addition
CRDH1J | KILC1Q | 4.9 | 0 | OHL | 0.1158 | 1.0399 | 0.269 | 463 | 444 | 415 | 444 | B-2-2a | 2032 | Addition
CRDH1K | FERO1S | 5.01 | 0 | OHL | 0.1184 | 1.0632 | 0.275 | 463 | 444 | 415 | 444 | B-2-2a | 2032 | Change
DUBE1B | MYBS1Q | 20.84 | 0 | OHL | 1.9025 | 4.8515 | 1.034 | 126 | 117 | 101 | 117 | B-2-2a | 2032 | Addition
DUBE1C | LOCB1U | 60.46 | 0 | OHL | 5.5195 | 14.0749 | 3 | 126 | 117 | 101 | 117 | B-2-2a | 2032 | Addition
EDAY1- | EDAY1B | 4.4 | 0 | OHL | 0.22 | 0.9108 | 0.246 | 203 | 193 | 173 | 193 | B-2-2a | 2032 | Addition
EDAY1A | ELIB1- | 3 | 0 | OHL | 0.15 | 0.621 | 0.168 | 203 | 193 | 173 | 193 | B-2-2a | 2032 | Addition
ELGI1Q | KEIT1N | 22.9 | 0 | OHL | 1.1679 | 5.1296 | 1.191 | 241 | 230 | 210 | 230 | B-2-2a | 2032 | Addition
ELGI1R | KEIT1M | 22.9 | 0 | OHL | 1.1679 | 5.1296 | 1.191 | 241 | 230 | 210 | 230 | B-2-2a | 2032 | Addition
EMMO4J | GLRB4- | 38.8 | 0 | OHL | 0.0825 | 0.7703 | 22.612 | 2780 | 2740 | 2660 | 2740 | B-2-2a | 2032 | Addition
EMMO4J | HURL4A | 59 | 0 | OHL | 0.059 | 1.003 | 40.533 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
EMMO4K | HURL4B | 59 | 0 | OHL | 0.059 | 1.003 | 40.533 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
EMMO4K | WFIB4- | 38.8 | 0 | OHL | 0.0825 | 0.7703 | 22.612 | 2780 | 2740 | 2660 | 2740 | B-2-2a | 2032 | Addition
FAUG4J | FNLN4B | 43.6 | 0 | OHL | 0.0565 | 0.8352 | 26.363 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
FERO1S | TAYN1R | 7.49 | 0 | OHL | 0.177 | 1.5895 | 0.411 | 463 | 444 | 415 | 444 | B-2-2a | 2032 | Change
FETT4Q | KINT4J | 32.19 | 0 | OHL | 0.0644 | 0.6116 | 19.765 | 2349 | 2266 | 2120 | 2266 | B-2-2a | 2032 | Change
FETT4R | KINT4K | 32.19 | 0 | OHL | 0.0644 | 0.6116 | 19.765 | 2349 | 2266 | 2120 | 2266 | B-2-2a | 2032 | Change
GILB1J | HOME1- | 3.5 | 0 | OHL | 0.175 | 0.7245 | 0.196 | 203 | 193 | 176 | 193 | B-2-2a | 2032 | Addition
GRNS4L | LOSD4A | 22.39 | 0 | OHL | 0.0224 | 0.3806 | 15.382 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
GRNS4M | LOSD4B | 22.39 | 0 | OHL | 0.0224 | 0.3806 | 15.382 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
HURL4A | KINT4K | 41 | 0 | OHL | 0.041 | 0.697 | 28.167 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
HURL4B | KINT4J | 41 | 0 | OHL | 0.041 | 0.697 | 28.167 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2032 | Addition
KILC1Q | TAYN1Q | 7.6 | 0 | OHL | 0.1796 | 1.6129 | 0.417 | 463 | 444 | 415 | 444 | B-2-2a | 2032 | Change
KINT2L | TEAL2A | 99.1 | 0 | OHL | 0.6009 | 5.2801 | 21.812 | 695 | 640 | 550 | 640 | B-2-2a | 2032 | Addition
KINT2M | TEAL2B | 99.1 | 0 | OHL | 0.6009 | 5.2801 | 21.812 | 695 | 640 | 550 | 640 | B-2-2a | 2032 | Addition
KNOC2L | KNOC2N | 31.99 | 0 | OHL | 0.1811 | 1.317 | 8.723 | 935 | 880 | 790 | 880 | B-2-2a | 2032 | Addition
KNOC2M | KNOC2P | 40.45 | 0 | OHL | 0.2291 | 1.6653 | 11.029 | 935 | 880 | 790 | 880 | B-2-2a | 2032 | Addition
LEWI1J | STOR1- | 1 | 0 | OHL | 0.0452 | 0.1608 | 0.07 | 300 | 285 | 255 | 285 | B-2-2a | 2032 | Addition
LEWI1K | STOR1- | 1 | 0 | OHL | 0.0452 | 0.1608 | 0.07 | 300 | 285 | 255 | 285 | B-2-2a | 2032 | Addition
LOCB1R | SHIN1- | 8.34 | 0 | OHL | 0.1958 | 0.9525 | 0.203 | 464 | 446 | 414 | 446 | B-2-2a | 2032 | Change
LOCB1S | SHIN1- | 8.34 | 0 | OHL | 0.1958 | 0.9525 | 0.203 | 464 | 446 | 414 | 446 | B-2-2a | 2032 | Change
LOCB2L | STRB2- | 17.9 | 0 | OHL | 0.1074 | 0.9845 | 3.795 | 780 | 750 | 700 | 750 | B-2-2a | 2032 | Addition
LOSD4A | NEDE4K | 24.5 | 0 | OHL | 0.049 | 0.4728 | 14.413 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2032 | Addition
LOSD4A | PEHE4J | 7.3 | 0 | OHL | 0.0146 | 0.1409 | 4.295 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2032 | Addition
LOSD4B | NEDE4J | 24.5 | 0 | OHL | 0.049 | 0.4728 | 14.413 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2032 | Addition
LOSD4B | PEHE4K | 7.3 | 0 | OHL | 0.0146 | 0.1409 | 4.295 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2032 | Addition
MOTA1Q | SHIN1B | 28.95 | 0 | OHL | 3.127 | 7.1633 | 1.522 | 132 | 123 | 106 | 123 | B-2-2a | 2032 | Addition
MOTA1R | SHIN1A | 28.95 | 0 | OHL | 3.127 | 7.1633 | 1.522 | 126 | 117 | 101 | 117 | B-2-2a | 2032 | Addition
AREX1A | CHMO1T | 4.7 | 0 | OHL | 0.35711 | 1.0182 | 0.24839 | 284 | 272 | 249 | 278 | B-2-2b | 2025 | Addition
BENB1- | BENB1T | 2.5 | 0 | OHL | 0.1875 | 0.5505 | 0.1315 | 167 | 160 | 148 | 160 | B-2-2b | 2025 | Addition
BENB1T | NECU1B | 4 | 0 | OHL | 0.1038 | 0.7722 | 0.2394 | 482 | 460 | 420 | 460 | B-2-2b | 2025 | Addition
CHAP1- | HAKB1- | 14.72 | 0 | OHL | 0.78187 | 3.1313 | 0.80314 | 242 | 225 | 194 | 225 | B-2-2b | 2025 | Change
CHMO1- | CHMO1T | 0.3 | 0 | OHL | 0.0225 | 0.066 | 0.0158 | 167 | 160 | 148 | 160 | B-2-2b | 2025 | Addition
CHMO1T | STOC1- | 5.9 | 0 | OHL | 0.4426 | 1.2993 | 0.3103 | 167 | 160 | 148 | 160 | B-2-2b | 2025 | Addition
DEVM1- | ERSK1Q | 16.5 | 0 | OHL | 1.0026 | 3.563 | 0.8861 | 213 | 202 | 185 | 202 | B-2-2b | 2025 | Change
DEVM1- | SPAV1Q | 7.63 | 0 | OHL | 0.5726 | 1.7268 | 0.3878 | 107 | 107 | 101 | 107 | B-2-2b | 2025 | Change
DEVM1- | SPAV1R | 7.51 | 0 | OHL | 0.5636 | 1.699 | 0.3818 | 107 | 107 | 101 | 107 | B-2-2b | 2025 | Change
FASI1- | FASI1A | 5 | 0 | OHL | 0.3756 | 1.1002 | 0.2633 | 199 | 191 | 178 | 191 | B-2-2b | 2025 | Addition
FASI1- | FASI1B | 5 | 0 | OHL | 0.3756 | 1.1002 | 0.2633 | 199 | 191 | 178 | 191 | B-2-2b | 2025 | Addition
FASI1A | HAWI1- | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124 | B-2-2b | 2025 | Addition
FASI1A | JUNV1- | 31.5 | 0 | OHL | 2.3859 | 7.5314 | 1.5385 | 199 | 191 | 178 | 191 | B-2-2b | 2025 | Addition
FASI1B | HAWI1- | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124 | B-2-2b | 2025 | Addition
FASI1B | JUNV1A | 31.5 | 0 | OHL | 2.3859 | 7.5314 | 1.5385 | 199 | 191 | 178 | 191 | B-2-2b | 2025 | Addition
GRNA1- | JUNV1- | 4.74 | 0 | OHL | 0.359 | 1.1333 | 0.2315 | 199 | 191 | 178 | 191 | B-2-2b | 2025 | Change
GRNA1- | JUNV1A | 4.74 | 0 | OHL | 0.359 | 1.1333 | 0.2315 | 199 | 191 | 178 | 191 | B-2-2b | 2025 | Addition
HOLM1- | SHRG1T | 8 | 0 | OHL | 0.6078 | 1.7331 | 0.4228 | 365 | 360 | 350 | 360 | B-2-2b | 2025 | Addition
HOLM1T | KEOO1- | 10.16 | 0 | OHL | 0.4101 | 2.0583 | 0.5825 | 132 | 123 | 106 | 123 | B-2-2b | 2025 | Addition
HOLM1T | NECU1B | 16.35 | 0 | OHL | 0.4243 | 3.1565 | 0.9785 | 482 | 460 | 420 | 460 | B-2-2b | 2025 | Addition
HUNE4- | KILS4- | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930 | B-2-2b | 2025 | Addition
HUNE4- | KILS4T | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930 | B-2-2b | 2025 | Addition
JUNB1A | JUNV1A | 1 | 0 | OHL | 0 | 0.0001 | 0 | 2286 | 2286 | 2286 | 2286 | B-2-2b | 2025 | Addition
LAMB2T | WIYH2- | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1380 | 1320 | 1230 | 1320 | B-2-2b | 2025 | Change
BENB1T | KEOO1Q | 20.25 | 0 | OHL | 0.5256 | 3.9095 | 1.2119 | 482 | 460 | 420 | 460 | B-2-2b | 2027 | Addition
BLCW1- | GNSH1- | 1.8 | 0 | OHL | 0.1352 | 0.3961 | 0.0948 | 167 | 160 | 148 | 160 | B-2-2b | 2027 | Addition
CAFA1Q | KEOO1- | 2.58 | 0 | OHL | 0.198 | 0.5682 | 0.1357 | 135 | 126 | 110 | 126 | B-2-2b | 2027 | Change
COAL4- | REDS4- | 11 | 0 | OHL | 0.0192 | 0.2085 | 6.5859 | 2210 | 2130 | 1980 | 2130 | B-2-2b | 2027 | Addition
COAN4- | REDS4- | 11 | 0 | OHL | 0.0192 | 0.2085 | 6.5859 | 2210 | 2130 | 1980 | 2130 | B-2-2b | 2027 | Addition
COAN4- | STHA4A | 21.79 | 0 | OHL | 0.0381 | 0.413 | 13.045 | 2210 | 2130 | 1980 | 2130 | B-2-2b | 2027 | Addition
COYL2- | CRCK2- | 25 | 0 | OHL | 0.1824 | 1.4207 | 5.0907 | 1110 | 1090 | 1060 | 1090 | B-2-2b | 2027 | Addition
CRCK2- | MAHI2- | 25 | 0 | OHL | 0.1824 | 1.4207 | 5.0907 | 1110 | 1090 | 1060 | 1090 | B-2-2b | 2027 | Addition
CULR2- | DEBS2- | 1.6 | 0 | OHL | 0.0069 | 0.0697 | 0.4224 | 1010 | 930 | 805 | 930 | B-2-2b | 2027 | Addition
CULR2- | MOSM2- | 27.746 | 0 | OHL | 0.1257 | 1.1735 | 7.4554 | 1090 | 1030 | 925 | 1030 | B-2-2b | 2027 | Addition
CULR2T | LOAN2T | 3.79 | 0 | OHL | 0.0169 | 0.1556 | 1.02 | 1090 | 1030 | 925 | 1030 | B-2-2b | 2027 | Addition
CULR2T | WFIE2- | 25.419 | 0 | OHL | 0.1146 | 1.055 | 6.9136 | 1096 | 1029 | 924 | 1029 | B-2-2b | 2027 | Addition
DUMF1- | OFOA1T | 2.08 | 0 | OHL | 0.0822 | 0.4694 | 0.1069 | 229 | 212 | 183 | 212 | B-2-2b | 2027 | Addition
ELVA4- | REDS4- | 15.77 | 0 | OHL | 0.0276 | 0.2989 | 9.4418 | 2210 | 2130 | 1980 | 2130 | B-2-2b | 2027 | Addition
ELVA4- | REDS4- | 15.77 | 0 | OHL | 0.0276 | 0.2989 | 9.4418 | 2210 | 2130 | 1980 | 2130 | B-2-2b | 2027 | Addition
ENHI3- | MONQ3- | 7 | 0 | OHL | 8.424 | 21.315 | 0.0269 | 34 | 32 | 28 | 32 | B-2-2b | 2027 | Addition
EWEH1Q | HORI1- | 6 | 0 | OHL | 0.4507 | 1.3202 | 0.316 | 199 | 191 | 178 | 191 | B-2-2b | 2027 | Addition
FASI1A | HAWI1D | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124 | B-2-2b | 2027 | Addition
FASI1B | HAWI1C | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124 | B-2-2b | 2027 | Addition
FELL1- | WNUK1- | 5 | 0 | OHL | 0.3751 | 1.1011 | 0.263 | 167 | 160 | 148 | 160 | B-2-2b | 2027 | Addition
GALA1- | HAWI1- | 23.55 | 0 | OHL | 1.7838 | 5.6307 | 1.1502 | 167 | 160 | 148 | 160 | B-2-2b | 2027 | Addition
GALA1- | HAWI1- | 23.55 | 0 | OHL | 1.7838 | 5.6307 | 1.1502 | 167 | 160 | 148 | 160 | B-2-2b | 2027 | Addition
GHPS1- | GLGL1- | 10 | 0 | OHL | 0.2554 | 1.7761 | 0.6376 | 12 | 12 | 11 | 12 | B-2-2b | 2027 | Addition
GHPS1- | GLGL1- | 10 | 0 | OHL | 0.2554 | 1.7761 | 0.6376 | 12 | 12 | 11 | 12 | B-2-2b | 2027 | Addition
GLLE1- | HOLM1T | 18.58 | 0 | OHL | 0.479 | 3.4684 | 1.142 | 482 | 460 | 420 | 460 | B-2-2b | 2027 | Addition
GLLE1- | KEOO1- | 7.68 | 0 | OHL | 0.1961 | 1.3641 | 0.4896 | 482 | 445 | 385 | 445 | B-2-2b | 2027 | Addition
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.3011 | 7.0802 | 1.472 | 284 | 278 | 270 | 278 | B-2-2b | 2027 | Change
GLLE1- | TONG1- | 33.1 | 0 | OHL | 2.0116 | 7.2879 | 1.729 | 197.7656 | 186.1054 | 168.0436 | 186.1054 | B-2-2b | 2027 | Change
GNSH1- | TRSN1- | 5 | 0 | OHL | 0.3751 | 1.1011 | 0.263 | 167 | 160 | 148 | 160 | B-2-2b | 2027 | Addition
GRNA4- | HAKB4B | 1.97 | 0 | OHL | 0.0035 | 0.0381 | 1.1674 | 2370 | 2270 | 2270 | 2270 | B-2-2b | 2027 | Change
HAKB4- | MOFF4C | 43.79 | 0 | OHL | 0.0772 | 0.8467 | 25.9494 | 2370 | 2270 | 2270 | 2270 | B-2-2b | 2027 | Change
KEOO1- | KEOO1Q | 3 | 0 | OHL | 0.0779 | 0.5792 | 0.1795 | 482 | 460 | 420 | 460 | B-2-2b | 2027 | Addition
KINB4J | KINN4- | 8.8 | 0 | OHL | 0.0181 | 0.1864 | 4.8531 | 2000 | 1920 | 1790 | 1920 | B-2-2b | 2027 | Addition
KINB4K | KINN4- | 8.8 | 0 | OHL | 0.0181 | 0.1864 | 4.8531 | 2000 | 1920 | 1790 | 1920 | B-2-2b | 2027 | Addition
OFOA1- | OFOA1T | 20 | 0 | OHL | 1.5025 | 4.4007 | 1.0533 | 167 | 160 | 148 | 160 | B-2-2b | 2027 | Addition
DENN2T | KINC2- | 17.75 | 0 | OHL | 0.0442 | 0.6378 | 5.5815 | 1500 | 1500 | 1500 | 1500 | B-2-2b | 2028 | Addition
AYR-2Q | COYW2S | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 955 | 885 | 760 | 885 | B-2-2b | 2029 | Change
AYR-2R | COYW2T | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 955 | 885 | 760 | 885 | B-2-2b | 2029 | Change
BAGA1Q | BONN1- | 18.3 | 0 | OHL | 0.6862 | 3.8983 | 0.9904 | 238 | 220 | 191 | 220 | B-2-2b | 2029 | Change
BAGA1R | BONN1- | 18.4 | 0 | OHL | 0.69 | 3.9202 | 0.9957 | 238 | 220 | 191 | 220 | B-2-2b | 2029 | Change
BONB4- | DENN4- | 19.894 | 0 | OHL | 0.0255 | 0.3658 | 12.2977 | 2570 | 2570 | 2508 | 2570 | B-2-2b | 2029 | Change
BONB4A | DENN4- | 19.894 | 0 | OHL | 0.0255 | 0.3658 | 12.2977 | 2570 | 2570 | 2508 | 2570 | B-2-2b | 2029 | Addition
BREE1- | CLAW1- | 6.5 | 0 | OHL | 0.4883 | 1.4302 | 0.3423 | 199 | 191 | 178 | 191 | B-2-2b | 2029 | Addition
BRNX4- | ECCL4B | 34.2 | 0 | OHL | 0.0442 | 0.6403 | 20.975 | 2470 | 2350 | 2150 | 2350 | B-2-2b | 2029 | Addition
BRNX4- | SMEA4Q | 54.32 | 0 | OHL | 0.0716 | 1.0582 | 32.3337 | 2473 | 2349 | 2148 | 2349 | B-2-2b | 2029 | Addition
BRNX4Q | CRYR4- | 9.36 | 0 | OHL | 0.012 | 0.1717 | 5.799 | 2522 | 2397 | 2189 | 2397 | B-2-2b | 2029 | Addition
BRNX4R | ECCL4A | 34.2 | 0 | OHL | 0.0442 | 0.6403 | 20.975 | 2470 | 2350 | 2150 | 2350 | B-2-2b | 2029 | Addition
BROT1- | LINM1Q | 5.774 | 0 | OHL | 0.1373 | 1.3023 | 0.2972 | 134 | 123 | 123 | 123 | B-2-2b | 2029 | Change
CLYM4- | KINN4- | 49.48 | 0 | OHL | 0.0528 | 0.8203 | 33.5272 | 2780 | 2570 | 2220 | 2570 | B-2-2b | 2029 | Addition
COCK4Q | GALN4- | 35.5 | 0 | OHL | 0.0727 | 0.7644 | 19.1125 | 1120 | 1060 | 990 | 1060 | B-2-2b | 2029 | Addition
COCK4R | GALN4- | 35.5 | 0 | OHL | 0.0727 | 0.7644 | 19.1125 | 1120 | 1060 | 990 | 1060 | B-2-2b | 2029 | Addition
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1540 | 1480 | 1380 | 1480 | B-2-2b | 2029 | Change
CRYR4- | FALL4- | 13.86 | 0 | OHL | 0.0182 | 0.2732 | 8.1821 | 2473 | 2349 | 2148 | 2349 | B-2-2b | 2029 | Change
DALB2A | DALL2- | 5.7 | 0 | OHL | 0.0241 | 0.2328 | 1.5851 | 1380 | 1320 | 1230 | 1320 | B-2-2b | 2029 | Addition
DALB2B | WIYH2- | 72.45 | 0 | OHL | 0.3064 | 2.9592 | 20.1469 | 1380 | 1320 | 1230 | 1320 | B-2-2b | 2029 | Addition
DALL2- | INVR2- | 22.55 | 0 | OHL | 0.0954 | 0.921 | 6.2707 | 570 | 570 | 570 | 570 | B-2-2b | 2029 | Addition
DENN2- | DENN2T | 1 | 0 | OHL | 0 | 0 | 0 | 4763 | 4763 | 4763 | 4763 | B-2-2b | 2029 | Addition
DENN2- | LAMB2- | 31.991 | 0 | OHL | 0.1391 | 1.4345 | 8.3553 | 1380 | 1320 | 1230 | 1320 | B-2-2b | 2029 | Change
DENN2T | EERH2- | 24.88 | 0 | OHL | 0.0561 | 0.8727 | 7.9683 | 1500 | 1500 | 1500 | 1500 | B-2-2b | 2029 | Addition
DENN4- | KINN4- | 16.1 | 0 | OHL | 0.0178 | 0.273 | 10.7108 | 2550 | 2420 | 2210 | 2420 | B-2-2b | 2029 | Addition
DENN4- | KINN4- | 16.1 | 0 | OHL | 0.0178 | 0.273 | 10.7108 | 2550 | 2420 | 2210 | 2420 | B-2-2b | 2029 | Addition
DENN4- | LAMB4T | 32.18 | 0 | OHL | 0.0661 | 0.6818 | 17.786 | 2000 | 1920 | 1790 | 1920 | B-2-2b | 2029 | Addition
DEVM4- | WIYH4Q | 28.908 | 0 | OHL | 0.0586 | 0.5888 | 16.3967 | 1390 | 1280 | 1110 | 1280 | B-2-2b | 2029 | Change
DUNE1- | GALN1Q | 12.64 | 0 | OHL | 0.3239 | 2.287 | 0.7972 | 482 | 460 | 420 | 460 | B-2-2b | 2029 | Addition
DUNE1- | GALN1R | 12.64 | 0 | OHL | 0.3239 | 2.287 | 0.7972 | 482 | 460 | 420 | 460 | B-2-2b | 2029 | Addition
ECCL1- | GALA1- | 30.58 | 0 | OHL | 1.6249 | 6.7325 | 1.5989 | 242 | 232 | 214 | 232 | B-2-2b | 2029 | Addition
ECCL1- | GALN1Q | 41.14 | 0 | OHL | 1.8834 | 8.6227 | 2.2702 | 242 | 232 | 214 | 232 | B-2-2b | 2029 | Addition
ECCL4A | GALN4- | 30.4 | 0 | OHL | 0.0623 | 0.6546 | 16.3668 | 2000 | 1920 | 1790 | 1920 | B-2-2b | 2029 | Addition
ECCL4B | GALN4- | 30.4 | 0 | OHL | 0.0623 | 0.6546 | 16.3668 | 2000 | 1920 | 1790 | 1920 | B-2-2b | 2029 | Addition
EKIS2- | STHA2B | 5.8 | 0 | OHL | 0.0245 | 0.2366 | 1.614 | 1372 | 1324 | 1228 | 1324 | B-2-2b | 2029 | Change
ELVA1- | NLEI1- | 14 | 0 | OHL | 0.7436 | 2.9782 | 0.7639 | 226 | 216 | 200 | 216 | B-2-2b | 2029 | Addition
EUCH1- | LORG1- | 3.5 | 0 | OHL | 0.2629 | 0.7701 | 0.1843 | 167 | 160 | 148 | 160 | B-2-2b | 2029 | Addition
FALL4- | SMEA4R | 31.1 | 0 | OHL | 0.0414 | 0.6133 | 18.3526 | 2473 | 2349 | 2148 | 2349 | B-2-2b | 2029 | Change
GALA1- | GALN1R | 11 | 0 | OHL | 0.2819 | 1.9903 | 0.6938 | 482 | 460 | 420 | 460 | B-2-2b | 2029 | Addition
GHPS4- | REDS4- | 25 | 0 | OHL | 0.0514 | 0.5412 | 13.4707 | 1995 | 1926 | 1787 | 1926 | B-2-2b | 2029 | Addition
GHPS4- | REDS4- | 25 | 0 | OHL | 0.0514 | 0.5412 | 13.4707 | 1995 | 1926 | 1787 | 1926 | B-2-2b | 2029 | Addition
GLLU1R | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49 | B-2-2b | 2029 | Change
GLNI1- | REDH1- | 10.547 | 0 | OHL | 0.9555 | 2.3056 | 0.552 | 161 | 156 | 145 | 156 | B-2-2b | 2029 | Change
HOLM1T | QUAN1- | 6 | 0 | OHL | 0.4559 | 1.2998 | 0.3171 | 284 | 278 | 270 | 278 | B-2-2b | 2029 | Addition
JUNB1- | JUNV1- | 1 | 0 | OHL | 0 | 0.0001 | 0 | 2286 | 2286 | 2286 | 2286 | B-2-2b | 2029 | Change
KAIM2- | SMEA2- | 8.78 | 0 | OHL | 0.0374 | 0.3629 | 2.4323 | 1090 | 1030 | 925 | 1030 | B-2-2b | 2029 | Change
KINC2- | KINN2A | 1.9 | 0 | OHL | 0.0043 | 0.0666 | 0.6085 | 1390 | 1280 | 1110 | 1280 | B-2-2b | 2029 | Change
KINC2- | MOSM2- | 35.776 | 0 | OHL | 0.1612 | 1.5146 | 9.6208 | 1090 | 1030 | 925 | 1030 | B-2-2b | 2029 | Addition
KINC2- | WFIE2- | 33.449 | 0 | OHL | 0.1501 | 1.3961 | 9.079 | 1090 | 1030 | 925 | 1030 | B-2-2b | 2029 | Addition
LAMB2- | WIYH2- | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9716 | 1380 | 1320 | 1230 | 1320 | B-2-2b | 2029 | Change
LAMB4T | WIYH4Q | 17.88 | 0 | OHL | 0.0357 | 0.3452 | 10.5184 | 2000 | 1920 | 1790 | 1920 | B-2-2b | 2029 | Addition
LORG1- | SHRG1T | 10 | 0 | OHL | 0.7598 | 2.1663 | 0.5285 | 284 | 278 | 270 | 278 | B-2-2b | 2029 | Change
NEIL2- | WIYH2R | 25.453 | 0 | OHL | 0.1093 | 1.0873 | 6.9047 | 1372 | 1324 | 1228 | 1324 | B-2-2b | 2029 | Change
REDS1A | SPRB1- | 18 | 0 | OHL | 1.3662 | 4.0108 | 0.9183 | 284 | 278 | 270 | 278 | B-2-2b | 2029 | Addition
REDS1A | SPRB1- | 18 | 0 | OHL | 1.3662 | 4.0108 | 0.9183 | 284 | 278 | 270 | 278 | B-2-2b | 2029 | Addition
SMEA4Q | WISH4- | 61.77 | 0 | OHL | 0.1313 | 1.2264 | 35.999 | 2778 | 2736 | 2667 | 2736 | B-2-2b | 2029 | Change
SMEA4R | WISH4- | 61.77 | 0 | OHL | 0.1313 | 1.2264 | 35.999 | 2778 | 2736 | 2667 | 2736 | B-2-2b | 2029 | Change
STHA4A | WISH4- | 11.6 | 0 | OHL | 0.0243 | 0.2192 | 7.0076 | 2778 | 2736 | 2667 | 2736 | B-2-2b | 2029 | Change
STHA4B | WISH4- | 11.6 | 0 | OHL | 0.0243 | 0.2192 | 7.0076 | 2778 | 2736 | 2667 | 2736 | B-2-2b | 2029 | Change
ARFO1- | KNSH1- | 7 | 0 | OHL | 0.5259 | 1.5402 | 0.3686 | 199 | 191 | 178 | 191 | B-2-2b | 2032 | Addition
ARRS1- | GRNA1- | 19.2 | 0 | OHL | 1.0219 | 4.0809 | 1.0489 | 3 | 3 | 3 | 3 | B-2-2b | 2032 | Addition
AUBU1- | MAYB1- | 21 | 0 | OHL | 1.5776 | 4.6207 | 1.1059 | 167 | 160 | 148 | 160 | B-2-2b | 2032 | Addition
COAL4- | STHA4B | 21.73 | 0 | OHL | 0.0463 | 0.4262 | 12.4959 | 2770 | 2770 | 2770 | 2770 | B-2-2b | 2032 | Change
CONL2Q | GLRO2- | 2.14 | 0 | OHL | 0.0099 | 0.0977 | 0.5452 | 1096 | 1029 | 924 | 1029 | B-2-2b | 2032 | Addition
CONL2R | GLRO2- | 2.14 | 0 | OHL | 0.0099 | 0.0977 | 0.5452 | 1096 | 1029 | 924 | 1029 | B-2-2b | 2032 | Addition
CONL4- | GLRB4- | 12.54 | 0 | OHL | 0.0261 | 0.2255 | 7.8748 | 2770 | 2730 | 2660 | 2730 | B-2-2b | 2032 | Addition
CONL4- | WFIE4- | 9.94 | 0 | OHL | 0.0207 | 0.1787 | 6.242 | 2770 | 2730 | 2660 | 2730 | B-2-2b | 2032 | Addition
ECCL1- | ORLA1- | 2.2 | 0 | OHL | 0.1025 | 0.4194 | 0.5995 | 200 | 200 | 200 | 200 | B-2-2b | 2032 | Addition
EKIL2Q | STHA2A | 4.79 | 0 | OHL | 0.0217 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965 | B-2-2b | 2032 | Change
ELVA4- | GRNA4C | 65.54 | 0 | OHL | 0.1406 | 1.3109 | 37.3092 | 2770 | 2770 | 2770 | 2770 | B-2-2b | 2032 | Change
ELVA4- | MOFF4- | 23.5 | 0 | OHL | 0.0504 | 0.47 | 13.3784 | 2770 | 2770 | 2770 | 2770 | B-2-2b | 2032 | Change
GLLU1Q | KNSH1- | 4 | 0 | OHL | 0.3653 | 0.9499 | 0.1945 | 49 | 49 | 49 | 49 | B-2-2b | 2032 | Addition
GLLU1R | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 57 | 57 | 57 | 57 | B-2-2b | 2032 | Addition
HAZE1- | HAZE1T | 1.75 | 0 | OHL | 0.1313 | 0.3854 | 0.092 | 112 | 112 | 112 | 112 | B-2-2b | 2032 | Addition
KINC2- | LOAN2S | 4.28 | 0 | OHL | 0.0185 | 0.1856 | 1.1458 | 1372 | 1324 | 1229 | 1324 | B-2-2b | 2032 | Addition
KINC4Q | LOAN4S | 4.28 | 0 | OHL | 0.0088 | 0.0877 | 2.4242 | 1995 | 1926 | 1787 | 1926 | B-2-2b | 2032 | Addition
MOSM4- | WFIE4- | 8.243 | 0 | OHL | 0.0174 | 0.1577 | 4.9523 | 2770 | 2730 | 2660 | 2730 | B-2-2b | 2032 | Addition
WFIB4- | WFIE4- | 22.48 | 0 | OHL | 0.0468 | 0.4042 | 14.1168 | 2770 | 2730 | 2660 | 2730 | B-2-2b | 2032 | Addition
BOLN41 | LHOR4A | 28.1 | 0 | OHL | 0.0305 | 0.4887 | 18.5239 | 3102 | 2935 | 2765 | 2935 | B-2-2c | 2025 | Addition
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8859 | 3102 | 2935 | 2765 | 2935 | B-2-2c | 2025 | Change
CARR41 | DAIN41 | 3.352 | 0 | OHL | 0.0059 | 0.0653 | 1.9782 | 3102 | 3048 | 2958 | 3048 | B-2-2c | 2025 | Change
CARR42 | DAIN41 | 2.063 | 0 | OHL | 0.0032 | 0.0397 | 1.2352 | 1500 | 1500 | 1500 | 1500 | B-2-2c | 2025 | Change
COTT41 | KEAD4C | 34.628 | 0 | OHL | 0.054 | 0.673 | 20.467 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2025 | Change
COTT41 | KEAD4D | 34.479 | 0 | OHL | 0.0538 | 0.6702 | 20.3774 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2025 | Change
GART4B | KEAD41 | 5.689 | 0 | OHL | 0.0062 | 0.0989 | 3.7497 | 3420 | 3260 | 2980 | 3260 | B-2-2c | 2025 | Change
HAKB4- | HARK41 | 9.857 | 0 | OHL | 0.0157 | 0.1946 | 5.7661 | 2213 | 2126 | 1980 | 2126 | B-2-2c | 2025 | Change
HARG41 | HARK41 | 0.1 | 0 | OHL | 0.0001 | 0.0019 | 0.0602 | 2771 | 2771 | 2771 | 2771 | B-2-2c | 2025 | Addition
HARG41 | HUTT41 | 81.544 | 0 | OHL | 0.127 | 1.5659 | 48.8916 | 2771 | 2771 | 2663 | 2771 | B-2-2c | 2025 | Addition
HARK13 | JUNV1- | 1 | 0 | OHL | 1.194 | 2.729 | 0.743 | 199 | 191 | 178 | 191 | B-2-2c | 2025 | Change
KLYN41 | NECT41 | 30.347 | 0 | OHL | 0.0269 | 0.5209 | 20.404 | 2520 | 2520 | 2520 | 2520 | B-2-2c | 2025 | Addition
KLYN41 | WALP41 | 16.672 | 0 | OHL | 0.0148 | 0.286 | 11.2124 | 2520 | 2520 | 2520 | 2520 | B-2-2c | 2025 | Addition
LHOR4B | NINF41 | 23.2 | 0 | OHL | 0.0252 | 0.4035 | 15.2937 | 3102 | 2935 | 2765 | 2935 | B-2-2c | 2025 | Addition
NECT41 | NORM41 | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3326 | 3326 | 3317 | 3326 | B-2-2c | 2025 | Addition
NECT41 | NORM41 | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3326 | 3258 | 3060 | 3258 | B-2-2c | 2025 | Addition
NECT41 | WALP41 | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3326 | 3160 | 2971 | 3160 | B-2-2c | 2025 | Addition
ALVE4A | INDQ41 | 97.176 | 0 | OHL | 0.2121 | 1.9367 | 56.1415 | 1389 | 1284 | 1108 | 1284 | B-2-2c | 2027 | Addition
ALVE4A | INDQ41 | 97.294 | 0 | OHL | 0.2123 | 1.9391 | 56.2092 | 1389 | 1284 | 1108 | 1284 | B-2-2c | 2027 | Addition
ALVE4A | TAUN41 | 73.293 | 0 | OHL | 0.117 | 1.477 | 42.0344 | 1389 | 1284 | 1108 | 1284 | B-2-2c | 2027 | Addition
ALVE4A | TAUN42 | 73.437 | 0 | OHL | 0.1172 | 1.4799 | 42.117 | 1389 | 1284 | 1108 | 1284 | B-2-2c | 2027 | Addition
BRIM2A | WALX22 | 5.865 | 0 | OHL | 0.0193 | 0.2381 | 1.6636 | 2310 | 2100 | 2030 | 2100 | B-2-2c | 2027 | Change
BRIM2B | WALX22 | 5.997 | 0 | OHL | 0.0198 | 0.2434 | 1.701 | 2310 | 2100 | 2030 | 2100 | B-2-2c | 2027 | Change
BRIM4C | WALX41 | 5.97 | 0 | OHL | 0.0093 | 0.1145 | 3.5827 | 3100 | 3100 | 3100 | 3100 | B-2-2c | 2027 | Addition
BRIM4D | WALX41 | 5.97 | 0 | OHL | 0.0093 | 0.1145 | 3.5827 | 3100 | 3100 | 3100 | 3100 | B-2-2c | 2027 | Addition
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.0156 | 0.3015 | 11.7995 | 3330 | 3160 | 2970 | 3160 | B-2-2c | 2027 | Change
CREB41 | CREB42 | 14.835 | 0 | OHL | 0.0131 | 0.2548 | 9.9719 | 3075 | 3075 | 3075 | 3075 | B-2-2c | 2027 | Addition
CREB41 | CREB42 | 14.904 | 0 | OHL | 0.0132 | 0.256 | 10.0181 | 3075 | 3075 | 3075 | 3075 | B-2-2c | 2027 | Addition
CREB42 | THTO41 | 14.835 | 0 | OHL | 0.0131 | 0.2548 | 9.9719 | 3075 | 3075 | 3075 | 3075 | B-2-2c | 2027 | Addition
CREB42 | THTO42 | 14.904 | 0 | OHL | 0.0132 | 0.256 | 10.0181 | 3075 | 3075 | 3075 | 3075 | B-2-2c | 2027 | Addition
DISS4A | NORM41 | 29.7 | 0 | OHL | 0.0263 | 0.5101 | 19.9633 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2027 | Change
EGGB41 | MFSN41 | 10.37 | 0 | OHL | 0.0091 | 0.1781 | 6.9831 | 3070 | 2830 | 2420 | 2830 | B-2-2c | 2027 | Addition
EGGB42 | MFSN41 | 10.37 | 0 | OHL | 0.0091 | 0.1781 | 6.9831 | 3070 | 2830 | 2420 | 2830 | B-2-2c | 2027 | Addition
GWYD41 | TRAW41 | 39.445 | 0 | OHL | 0.0615 | 0.7568 | 23.67 | 3102 | 3048 | 2958 | 3048 | B-2-2c | 2027 | Addition
GWYD41 | TREU4A | 25.573 | 0 | OHL | 0.0398 | 0.4907 | 15.3454 | 3102 | 3048 | 2958 | 3048 | B-2-2c | 2027 | Addition
HAMB4A | STAH4A | 3.926 | 0 | OHL | 0.007 | 0.078 | 2.2826 | 1970 | 1870 | 1710 | 1870 | B-2-2c | 2027 | Change
HAMB4B | STAH4B | 3.926 | 0 | OHL | 0.007 | 0.078 | 2.2826 | 1970 | 1970 | 1970 | 1970 | B-2-2c | 2027 | Change
HARG41 | HUTT41 | 81.544 | 0 | OHL | 0.127 | 1.5659 | 48.8916 | 2771 | 2771 | 2771 | 2771 | B-2-2c | 2027 | Addition
KNAR21 | TADT2A | 25 | 0 | OHL | 0.1224 | 1.0976 | 6.5267 | 1500 | 1500 | 1300 | 1300 | B-2-2c | 2027 | Addition
KNAR21 | TADT2B | 25 | 0 | OHL | 0.1224 | 1.0976 | 6.5267 | 1500 | 1500 | 1300 | 1500 | B-2-2c | 2027 | Addition
MFSN2A | TADT2A | 14.18 | 0 | OHL | 0.0694 | 0.6225 | 3.7019 | 1500 | 1500 | 1300 | 1500 | B-2-2c | 2027 | Addition
OBST4A | YORK4A | 2.8 | 0 | OHL | 0.0051 | 0.0575 | 1.5702 | 1500 | 1500 | 1750 | 1300 | B-2-2c | 2027 | Addition
OBST4B | YORK4B | 2.8 | 0 | OHL | 0.0051 | 0.0575 | 1.5702 | 1500 | 1500 | 1750 | 1300 | B-2-2c | 2027 | Addition
OSBA41 | THTO43 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 3326 | 3160 | 2980 | 3160 | B-2-2c | 2027 | Change
OSBA42 | THTO42 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 3326 | 3160 | 2980 | 3160 | B-2-2c | 2027 | Change
OVER21 | POPP21 | 4.729 | 0 | OHL | 0.0257 | 0.2475 | 1.0505 | 680 | 540 | 540 | 680 | B-2-2c | 2027 | Addition
OVER21 | POPP21 | 4.634 | 0 | OHL | 0.0254 | 0.2439 | 1.0211 | 550 | 440 | 440 | 550 | B-2-2c | 2027 | Addition
OVER21 | TADT2A | 20.176 | 0 | OHL | 0.0988 | 0.8858 | 5.2674 | 1500 | 1500 | 1300 | 1500 | B-2-2c | 2027 | Addition
OVER21 | TADT2B | 20.176 | 0 | OHL | 0.0988 | 0.8858 | 5.2673 | 1500 | 1500 | 1300 | 1500 | B-2-2c | 2027 | Addition
PELH41 | RYEH4A | 23.015 | 0 | OHL | 0.0202 | 0.3952 | 15.4966 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2027 | Change
PELH41 | RYEH4B | 23.439 | 0 | OHL | 0.0206 | 0.4024 | 15.7811 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2027 | Change
PEMB41 | POAB41 | 74.6 | 0 | OHL | 0.081 | 1.2975 | 49.1773 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Addition
PEMB41 | SWAN41 | 83.854 | 0 | OHL | 0.091 | 1.4585 | 55.2774 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Change
PENT41 | WYLS41 | 27.13 | 0 | OHL | 0.0294 | 0.4719 | 17.8844 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Addition
POAB41 | SWAN41 | 9.35 | 0 | OHL | 0.0101 | 0.1626 | 6.1636 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Addition
RYEH41 | RYEH4B | 0.137 | 0 | OHL | 0.0001 | 0.0024 | 0.0923 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2027 | Change
RYEH41 | WALX4A | 5.324 | 0 | OHL | 0.0047 | 0.0914 | 3.5851 | 3326 | 3326 | 3326 | 3326 | B-2-2c | 2027 | Change
RYEH4A | WALX4B | 5.461 | 0 | OHL | 0.0048 | 0.0938 | 3.6774 | 3326 | 3326 | 3326 | 3326 | B-2-2c | 2027 | Change
SPEN42 | STEW41 | 37.795 | 0 | OHL | 0.0497 | 0.7368 | 22.4165 | 2780 | 2780 | 2480 | 2670 | B-2-2c | 2027 | Change
TRAW41 | TREU4B | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5726 | 3102 | 3048 | 2958 | 3048 | B-2-2c | 2027 | Change
WYLF41 | WYLS41 | 8.11 | 0 | OHL | 0.0088 | 0.1411 | 5.3462 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Addition
BRFO41 | TWIN4A | 28.419 | 0 | OHL | 0.0252 | 0.4881 | 19.1016 | 3820 | 3630 | 3320 | 3630 | B-2-2c | 2029 | Addition
BRFO41 | TWIN4B | 28.419 | 0 | OHL | 0.0252 | 0.4881 | 19.1016 | 3820 | 3630 | 3320 | 3630 | B-2-2c | 2029 | Addition
BRIN41 | CHTE41 | 22.375 | 0 | OHL | 0.0243 | 0.3892 | 14.7493 | 2810 | 2700 | 2510 | 2700 | B-2-2c | 2029 | Addition
COTT42 | WBUR42 | 6.76 | 0 | OHL | 0.0096 | 0.1298 | 4.0616 | 3326 | 3160 | 2971 | 3160 | B-2-2c | 2029 | Change
ELST41 | SUND41 | 34.834 | 0 | OHL | 0.0549 | 0.6691 | 20.9253 | 2400 | 2300 | 2140 | 2300 | B-2-2c | 2029 | Change
ELST4B | SUND42 | 34.706 | 0 | OHL | 0.0547 | 0.6666 | 20.848 | 3100 | 1732 | 1732 | 1732 | B-2-2c | 2029 | Change
FOUX41 | PENI4A | 23.025 | 0 | OHL | 0.0303 | 0.4488 | 13.6563 | 2780 | 2700 | 2510 | 2700 | B-2-2c | 2029 | Addition
GRAI41 | WALE41 | 1.68 | 0 | OHL | 0.0015 | 0.0288 | 1.1313 | 3326 | 3160 | 2633 | 2813 | B-2-2c | 2029 | Change
GREN41 | MARV4A | 26 | 0 | OHL | 0.0406 | 0.5007 | 15.5357 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Change
GREN41 | MARV4B | 26 | 0 | OHL | 0.0406 | 0.5007 | 15.5357 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Change
HAKB4- | HARG41 | 10.107 | 0 | OHL | 0.0175 | 0.1997 | 5.8779 | 3180 | 3130 | 3050 | 3130 | B-2-2c | 2029 | Change
HAKB4B | HARG41 | 10.107 | 0 | OHL | 0.0175 | 0.1997 | 5.8779 | 3180 | 3130 | 3050 | 3130 | B-2-2c | 2029 | Change
HAWP4A | NORT41 | 30.157 | 0 | OHL | 0.047 | 0.5786 | 18.0971 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Change
HAWP41 | NORT41 | 30.157 | 0 | OHL | 0.047 | 0.5786 | 18.0971 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Addition
HIMB21 | THUR2A | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 626 | 591 | 535 | 591 | B-2-2c | 2029 | Addition
HIMB41 | STAY41 | 20.939 | 0 | OHL | 0.0329 | 0.4037 | 12.4972 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Addition
HIMB41 | STOB41 | 39.671 | 0 | OHL | 0.0642 | 0.7694 | 23.5463 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Addition
MARV4A | SUND41 | 13.75 | 0 | OHL | 0.0215 | 0.2648 | 8.216 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Change
NORT41 | OBST4A | 70.35 | 0 | OHL | 0.0624 | 1.2083 | 47.2853 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2029 | Change
NORT41 | OBST4B | 70.35 | 0 | OHL | 0.0624 | 1.2083 | 47.2853 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2029 | Change
OBST4A | OSBA41 | 13.35 | 0 | OHL | 0.0118 | 0.2293 | 8.9731 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2029 | Change
OBST4B | OSBA42 | 13.35 | 0 | OHL | 0.0118 | 0.2293 | 8.9731 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2029 | Change
PELH41 | TWIN4A | 40.882 | 0 | OHL | 0.0362 | 0.7022 | 27.4783 | 3100 | 3100 | 3100 | 3100 | B-2-2c | 2029 | Addition
PELH41 | TWIN4B | 40.823 | 0 | OHL | 0.0362 | 0.7012 | 27.4387 | 3820 | 3630 | 3320 | 3630 | B-2-2c | 2029 | Addition
PELH41 | WYMO41 | 26.856 | 0 | OHL | 0.0291 | 0.4667 | 17.7225 | 2771 | 2771 | 2692 | 2771 | B-2-2c | 2029 | Change
PELH41 | WYMO41 | 26.891 | 0 | OHL | 0.0292 | 0.4677 | 17.7269 | 3180 | 3180 | 3180 | 3180 | B-2-2c | 2029 | Addition
PEMB41 | POAB41 | 74.6 | 0 | OHL | 0.081 | 1.2975 | 49.1773 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2029 | Addition
PENI4A | PENT41 | 4.545 | 0 | OHL | 0.0049 | 0.0722 | 3.2978 | 2780 | 2570 | 2220 | 2570 | B-2-2c | 2029 | Addition
POAB41 | SWAN41 | 9.454 | 0 | OHL | 0.0103 | 0.1644 | 6.232 | 2779 | 2779 | 2779 | 2779 | B-2-2c | 2029 | Addition
RATS41 | STAY4A | 43.614 | 0 | OHL | 0.0738 | 0.8539 | 25.6652 | 2147 | 2057 | 1905 | 2057 | B-2-2c | 2029 | Change
SUND41 | WYMO41 | 18.156 | 0 | OHL | 0.0197 | 0.3152 | 11.9934 | 3180 | 3180 | 3180 | 3180 | B-2-2c | 2029 | Change
SUND42 | WYMO41 | 17.986 | 0 | OHL | 0.0195 | 0.3128 | 11.8566 | 3180 | 3180 | 3180 | 3180 | B-2-2c | 2029 | Addition

## Composite
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
ABNE1R | AMUL1G | 28.099 | 0.001 | Composite | 2.8706 | 6.5818 | 1.397 | 132 | 123 | 106 | 123 | B-2-1a
AIGA1Q | KIOR1Q | 2.797 | 0.123 | Composite | 0.264 | 0.594 | 0.66 | 126 | 117 | 101 | 117 | B-2-1a
BEAU1K | KIOR1Q | 1.24 | 0.06 | Composite | 0.13 | 0.29 | 0.06 | 126 | 117 | 101 | 117 | B-2-1a
BEAU2J | FASN2- | 24.288 | 1.012 | Composite | 0.069 | 1.025 | 7.23 | 1910 | 1830 | 1710 | 1830 | B-2-1a
CHAR1S | GLAG1Q | 0.935 | 1.375 | Composite | 0.1697 | 0.3805 | 1.708 | 126 | 117 | 101 | 117 | B-2-1a
CHAR1T | GLAG1R | 0.935 | 1.375 | Composite | 0.1697 | 0.3805 | 1.708 | 126 | 117 | 101 | 117 | B-2-1a
FASN2- | FAUG2J | 24.384 | 1.016 | Composite | 0.069 | 1.029 | 7.259 | 1910 | 1830 | 1710 | 1830 | B-2-1a
SFEM1Q | SFER1L | 1.9 | 1.1 | Composite | 0.382 | 0.557 | 1.871 | 132 | 122 | 106 | 122 | B-2-1a
SFEM1R | SFER1M | 1.9 | 1.1 | Composite | 0.382 | 0.557 | 1.871 | 132 | 122 | 106 | 122 | B-2-1a
AREC1- | MAHI1- | 7.615 | 1.613 | Composite | 0.4363 | 1.668 | 2.5345 | 214 | 195 | 195 | 195 | B-2-1b
AREC3- | GLAP3- | 10.79 | 5.931 | Composite | 10.6428 | 36.9228 | 0.6748 | 40 | 38 | 38 | 38 | B-2-1b
BAGA1Q | DRCR1Q | 4.71 | 3.39 | Composite | 0.5756 | 1.4393 | 2.8779 | 146 | 146 | 146 | 146 | B-2-1b
BAGA1R | DRCR1R | 4.71 | 3.38 | Composite | 0.5752 | 1.4382 | 2.8701 | 146 | 146 | 146 | 146 | B-2-1b
BAIN1Q | BONN1- | 7.02 | 0.08 | Composite | 0.2761 | 1.4801 | 0.4755 | 114 | 114 | 114 | 114 | B-2-1b
BAIN1R | BONN1- | 7.02 | 0.28 | Composite | 0.2797 | 1.4992 | 0.7089 | 114 | 114 | 114 | 114 | B-2-1b
BERW1Q | ECCL1- | 21.54 | 0.31 | Composite | 1.622 | 4.903 | 1.5274 | 132 | 123 | 106 | 123 | B-2-1b
BERW1R | ECCL1- | 21.54 | 0.27 | Composite | 1.6213 | 4.8991 | 1.4716 | 132 | 123 | 106 | 123 | B-2-1b
BLCW1- | NECU1Q | 36.15 | 0.9 | Composite | 1.2839 | 7.3019 | 3.5807 | 167 | 160 | 148 | 160 | B-2-1b
BLKL1- | WISH1- | 5.33 | 6.13 | Composite | 0.6542 | 1.8052 | 6.2962 | 161 | 154 | 140 | 154 | B-2-1b
BLLX1- | LINM1Q | 12.85 | 5.24 | Composite | 1.1339 | 3.1699 | 7.5599 | 132 | 123 | 106 | 123 | B-2-1b
BONN1- | DENN1- | 4.04 | 0.3 | Composite | 0.1878 | 0.4755 | 1.1901 | 240 | 234 | 202 | 234 | B-2-1b
BONN1- | STIR1S | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 238 | 219 | 191 | 219 | B-2-1b
BONN1- | STIR1T | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 238 | 219 | 191 | 219 | B-2-1b
BONN2A | DENN2- | 3.812 | 0.55 | Composite | 0.0183 | 0.1734 | 4.382 | 722 | 647 | 593 | 647 | B-2-1b
BONN2B | DENN2- | 3.812 | 0.46 | Composite | 0.0181 | 0.1709 | 3.8346 | 722 | 647 | 593 | 647 | B-2-1b
BRAP1- | PAIS1R | 4.52 | 2.19 | Composite | 0.1309 | 0.9964 | 3.6706 | 274 | 274 | 274 | 274 | B-2-1b
CHAP1- | DUMF1- | 26.9 | 0.18 | Composite | 1.0661 | 6.0867 | 1.6344 | 171 | 155 | 155 | 155 | B-2-1b
CHAP1- | DUMF1- | 26.9 | 0.125 | Composite | 1.065 | 6.0817 | 1.5576 | 171 | 155 | 155 | 155 | B-2-1b
CHAP1- | ECCF1J | 6.569 | 0.23 | Composite | 0.6009 | 1.515 | 0.651 | 18 | 18 | 18 | 18 | B-2-1b
CHAP1- | ECCF1K | 6.569 | 0.185 | Composite | 0.6 | 1.5109 | 0.5882 | 21 | 21 | 21 | 21 | B-2-1b
CLYM2- | DALM2R | 4.21 | 0.093 | Composite | 0.0193 | 0.1737 | 1.8402 | 695 | 560 | 500 | 560 | B-2-1b
COAL1A | LINM1R | 5.774 | 3.14 | Composite | 0.2748 | 1.6606 | 2.8754 | 134 | 123 | 123 | 123 | B-2-1b
COAT2Q | NEAR2Q | 3.4 | 4.9 | Composite | 0.045 | 0.2476 | 17.1398 | 176 | 156 | 156 | 156 | B-2-1b
COAT2R | NEAR2R | 3.4 | 4.9 | Composite | 0.045 | 0.2476 | 17.1398 | 176 | 156 | 156 | 156 | B-2-1b
COYL1- | COYT1T | 4.37 | 0.27 | Composite | 0.4027 | 1.0118 | 0.5089 | 132 | 123 | 106 | 123 | B-2-1b
COYL1- | MAYT1T | 9.14 | 0.57 | Composite | 0.8423 | 2.157 | 1.0619 | 132 | 123 | 106 | 123 | B-2-1b
COYL2- | COYW2S | 1.29 | 0.08 | Composite | 0.0057 | 0.0515 | 0.4645 | 1500 | 1500 | 1500 | 1500 | B-2-1b
COYT1T | KILS1- | 15.215 | 4.815 | Composite | 1.4768 | 3.99 | 7.6706 | 132 | 123 | 106 | 123 | B-2-1b
COYT1T | MAYB1- | 17.666 | 0.28 | Composite | 1.6159 | 4.1178 | 1.1779 | 132 | 123 | 106 | 123 | B-2-1b
CRUA2Q | DALL2- | 8.16 | 0.4 | Composite | 0.0346 | 0.3435 | 4.3204 | 283 | 283 | 283 | 283 | B-2-1b
CRUA2R | DALL2- | 8.16 | 0.4 | Composite | 0.0346 | 0.3435 | 4.3204 | 283 | 283 | 283 | 283 | B-2-1b
CURR1A | GORG1Q | 1.49 | 5.8 | Composite | 0.261 | 0.9656 | 5.1127 | 111 | 100 | 92 | 100 | B-2-1b
CURR1A | LING1Q | 8.323 | 5.205 | Composite | 0.7926 | 2.2632 | 6.4813 | 132 | 123 | 106 | 123 | B-2-1b
CURR1B | GORG1R | 1.49 | 5.78 | Composite | 0.2603 | 0.9634 | 5.0953 | 111 | 100 | 92 | 100 | B-2-1b
CURR1B | LING1R | 8.323 | 5.335 | Composite | 0.7972 | 2.2773 | 6.5941 | 132 | 123 | 106 | 123 | B-2-1b
DESA1Q | NECU1- | 6.4 | 4.3 | Composite | 0.5652 | 1.7993 | 6.3388 | 167 | 160 | 147 | 160 | B-2-1b
DRUM2Q | WIYH2- | 2.46 | 0.29 | Composite | 0.0113 | 0.1081 | 3.8932 | 120 | 120 | 120 | 120 | B-2-1b
DUNE1- | SMEA1- | 17.838 | 0.621 | Composite | 1.098 | 3.6602 | 1.7709 | 154 | 131 | 127 | 131 | B-2-1b
ECCL4A | TORN4- | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840 | B-2-1b
ECCL4B | TORN4- | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840 | B-2-1b
EKIL2R | EKIL2T | 5.17 | 0.108 | Composite | 0.0141 | 0.186 | 2.1213 | 480 | 405 | 405 | 405 | B-2-1b
GARE1S | WIYH1- | 35.082 | 0.33 | Composite | 3.1938 | 7.8537 | 2.4208 | 109 | 105 | 101 | 105 | B-2-1b
GARE1T | WIYH1- | 34.74 | 0.162 | Composite | 3.1552 | 7.7595 | 2.0813 | 109 | 105 | 101 | 105 | B-2-1b
GOVA1Q | PAIS1Q | 4.52 | 4.03 | Composite | 0.2635 | 1.0894 | 8.2673 | 125 | 113 | 110 | 113 | B-2-1b
HELE1R | WIYH1- | 24.799 | 0.182 | Composite | 2.2553 | 5.5463 | 1.6125 | 109 | 105 | 101 | 105 | B-2-1b
HUNF1Q | KILW1R | 12.85 | 3.06 | Composite | 0.6044 | 3.1854 | 6.863 | 146 | 146 | 145 | 146 | B-2-1b
HUNF1R | SACO1R | 8.572 | 3.04 | Composite | 0.4215 | 2.2374 | 6.6019 | 146 | 146 | 145 | 146 | B-2-1b
KIER1Q | WIYH1- | 2.089 | 4.183 | Composite | 0.3881 | 0.9293 | 7.6166 | 100 | 80 | 60 | 80 | B-2-1b
KIER1R | WIYH1- | 2.089 | 4.095 | Composite | 0.3833 | 0.9197 | 7.4586 | 100 | 80 | 60 | 80 | B-2-1b
KINB2K | KINC2- | 10.325 | 0.385 | Composite | 0.0467 | 0.4255 | 6.9142 | 1090 | 1030 | 925 | 1030 | B-2-1b
LAMB2- | PORD2R | 3.94 | 0.177 | Composite | 0.0192 | 0.1721 | 2.1551 | 300 | 300 | 300 | 300 | B-2-1b
LOAN2- | MOSM2- | 31.496 | 0.174 | Composite | 0.1429 | 1.3311 | 11.6006 | 1090 | 1030 | 925 | 1030 | B-2-1b
MAYB1- | MAYT1T | 12.59 | 0.31 | Composite | 1.1567 | 3.0101 | 0.9444 | 132 | 123 | 106 | 123 | B-2-1b
NEIL1- | PAIS1Q | 8.29 | 0.29 | Composite | 0.1643 | 1.4877 | 1.704 | 268 | 268 | 268 | 268 | B-2-1b
NEIL1- | PAIS1R | 8.31 | 0.31 | Composite | 0.1648 | 1.493 | 1.7861 | 268 | 268 | 268 | 268 | B-2-1b
POOB2Q | SMEA2- | 7.79 | 0.19 | Composite | 0.0335 | 0.3227 | 2.9788 | 360 | 300 | 240 | 300 | B-2-1b
POOB2R | SMEA2- | 7.79 | 0.19 | Composite | 0.0335 | 0.3227 | 2.9788 | 360 | 300 | 240 | 300 | B-2-1b
STIR1S | WFIE1A | 37.6 | 5.816 | Composite | 3.218 | 9.4053 | 8.7867 | 162 | 154 | 141 | 154 | B-2-1b
STLE1R | WIYH1- | 12.892 | 0.291 | Composite | 1.1813 | 2.9041 | 1.2141 | 109 | 105 | 101 | 105 | B-2-1b
ABTH21 | UPPB22 | 27.035 | 0.547 | Composite | 0.1245 | 1.1595 | 13.2801 | 772 | 772 | 595 | 595 | B-2-1c
AXMI41 | CHIC4A | 30.7 | 8.8 | Composite | 0.0379 | 0.6609 | 130.8219 | 2779 | 2568 | 2217 | 2568 | B-2-1c
BAGB21 | MAGA21 | 12.629 | 1.389 | Composite | 0.0435 | 0.5216 | 17.0509 | 1204 | 1115 | 1018 | 1115 | B-2-1c
BAGB21 | SWAN21 | 18.21 | 1.439 | Composite | 0.0625 | 0.7488 | 19.1165 | 1548 | 1548 | 1431 | 1431 | B-2-1c
BEDD21 | CHSI21 | 17.836 | 0.286 | Composite | 0.068 | 0.7365 | 7.9729 | 944 | 882 | 762 | 835 | B-2-1c
BEDD21 | WIMB21 | 8.5 | 0.968 | Composite | 0.0409 | 0.3915 | 11.7005 | 859 | 827 | 623 | 694 | B-2-1c
BEDD22 | CHSI21 | 17.836 | 0.137 | Composite | 0.0677 | 0.7328 | 6.4221 | 762 | 762 | 662 | 662 | B-2-1c
BEDD23 | WIMB2A | 8.5 | 0.582 | Composite | 0.0398 | 0.3821 | 8.4754 | 995 | 930 | 728 | 806 | B-2-1c
BESW21 | OCKH21 | 56.939 | 0.731 | Composite | 0.2318 | 2.4208 | 22.7971 | 819 | 819 | 638 | 638 | B-2-1c
BRAW21 | ELLA21 | 16.802 | 0.081 | Composite | 0.0769 | 0.7134 | 5.4384 | 762 | 762 | 619 | 619 | B-2-1c
BRAW21 | KIRK21 | 17.279 | 4.547 | Composite | 0.0844 | 0.855 | 54.1379 | 762 | 762 | 619 | 619 | B-2-1c
BRED21 | SMAN21 | 10.004 | 5.629 | Composite | 0.0513 | 0.4604 | 46.762 | 865 | 865 | 749 | 749 | B-2-1c
BRFO41 | DISS4A | 31.4 | 0.1 | Composite | 0.0279 | 0.5404 | 23.1059 | 3326 | 3326 | 3326 | 3326 | B-2-1c
BRFO41 | DISS4B | 31.4 | 0.1 | Composite | 0.0279 | 0.5404 | 23.1059 | 3326 | 3326 | 3326 | 3326 | B-2-1c
BRIM2A | TOTT23 | 7.437 | 0.311 | Composite | 0.0345 | 0.3234 | 5.3982 | 1085 | 1031 | 925 | 1031 | B-2-1c
BRIM2C | TOTT24 | 7.455 | 0.235 | Composite | 0.0344 | 0.3223 | 4.5788 | 1085 | 1031 | 925 | 1031 | B-2-1c
BRIM2D | TOTT21 | 7.455 | 0.384 | Composite | 0.0347 | 0.3264 | 6.1984 | 1085 | 1031 | 925 | 1031 | B-2-1c
BRIN21 | CHTE21 | 22.464 | 0.22 | Composite | 0.0519 | 0.8305 | 9.3505 | 934 | 934 | 753 | 753 | B-2-1c
BRIN21 | JORD21 | 13.257 | 1.489 | Composite | 0.0647 | 0.5918 | 16.0432 | 557 | 557 | 499 | 499 | B-2-1c
BRIN21 | NORL2A | 13.257 | 2.845 | Composite | 0.0708 | 0.6085 | 24.8202 | 419 | 419 | 381 | 381 | B-2-1c
BRLE41 | DIDC41 | 37.691 | 5.7 | Composite | 0.0419 | 0.6724 | 87.0663 | 2779 | 2568 | 2217 | 2245 | B-2-1c
BRLE41 | DIDC41 | 37.691 | 5.7 | Composite | 0.0419 | 0.6719 | 134.3668 | 2277 | 2277 | 2037 | 2037 | B-2-1c
BRWA42 | BRWA4B | 4 | 0.462 | Composite | 0.0076 | 0.085 | 7.3611 | 2030 | 1930 | 1770 | 1930 | B-2-1c
BUSH21 | WIEN2B | 5.197 | 4.318 | Composite | 0.0311 | 0.3404 | 48.3427 | 762 | 762 | 681 | 681 | B-2-1c
BUST21 | NECH21 | 2.648 | 7.619 | Composite | 0.026 | 0.3163 | 76.3606 | 725 | 713 | 599 | 635 | B-2-1c
BUST21 | NECH21 | 2.648 | 7.648 | Composite | 0.026 | 0.3169 | 76.528 | 725 | 713 | 599 | 635 | B-2-1c
CARR21 | SMAN21 | 9.294 | 0.133 | Composite | 0.0414 | 0.4101 | 3.8882 | 835 | 835 | 665 | 665 | B-2-1c
CARR21 | SMAN21 | 10.747 | 0.23 | Composite | 0.0475 | 0.476 | 5.3274 | 835 | 835 | 665 | 665 | B-2-1c
CELL41 | DAIN41 | 53.412 | 2.31 | Composite | 0.0842 | 1.0314 | 76.8805 | 2508 | 2508 | 2300 | 2300 | B-2-1c
CHIC41 | EXET41 | 67.12 | 8.8 | Composite | 0.0786 | 1.3565 | 152.8884 | 2779 | 2568 | 2217 | 2568 | B-2-1c
CHIL41 | LOVE41 | 22.379 | 0.315 | Composite | 0.0201 | 0.389 | 20.2483 | 1109 | 1109 | 901 | 901 | B-2-1c
CHUE4A | TILB41 | 13.045 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2827 | 2827 | 2591 | 2591 | B-2-1c
CHUE4B | TILB41 | 13.045 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2924 | 2924 | 2591 | 2591 | B-2-1c
CONQ41 | GWYN4A | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 2665 | 2561 | 2217 | 2561 | B-2-1c
CONQ41 | GWYN4B | 30.217 | 0.21 | Composite | 0.0329 | 0.528 | 22.2116 | 2665 | 2561 | 2217 | 2561 | B-2-1c
COTT41 | STAY41 | 27.788 | 0.5 | Composite | 0.0506 | 0.5544 | 51.7563 | 2213 | 2126 | 1980 | 2052 | B-2-1c
COVE21 | RATS2A | 64.863 | 0.5 | Composite | 0.1812 | 2.5694 | 23.9446 | 1000 | 1000 | 1000 | 1000 | B-2-1c
DAIN41 | MACC41 | 33.593 | 2.4 | Composite | 0.0535 | 0.6515 | 66.7385 | 2397 | 2302 | 2144 | 2300 | B-2-1c
DINO41 | PENT41 | 4.545 | 7.305 | Composite | 0.0088 | 0.1776 | 95.0951 | 1623 | 1623 | 1571 | 1571 | B-2-1c
DRAK41 | OLDB4A | 48.818 | 0.5 | Composite | 0.0921 | 0.9799 | 36.5074 | 1169 | 1169 | 1068 | 1068 | B-2-1c
EGGB41 | ROCH4A | 84.875 | 0.7 | Composite | 0.1416 | 1.6214 | 64.456 | 1239 | 1239 | 1122 | 1122 | B-2-1c
EGGB41 | THOM41 | 28.07 | 0.197 | Composite | 0.0293 | 0.4897 | 21.8489 | 2217 | 2217 | 1801 | 1801 | B-2-1c
ELLA21 | KIRK21 | 33.995 | 5.044 | Composite | 0.1618 | 1.5765 | 64.0738 | 762 | 762 | 619 | 619 | B-2-1c
ELST21 | MILH2A | 6.375 | 6.338 | Composite | 0.0548 | 0.3963 | 55.677 | 524 | 524 | 430 | 430 | B-2-1c
ELST21 | MILH2B | 6.375 | 6.282 | Composite | 0.0546 | 0.3952 | 55.2004 | 524 | 524 | 430 | 430 | B-2-1c
ELST21 | WARL21 | 59.208 | 0.261 | Composite | 0.2449 | 2.4665 | 19.2619 | 762 | 762 | 619 | 619 | B-2-1c
ELST21 | WATS21 | 5.398 | 0.399 | Composite | 0.0254 | 0.2396 | 5.8016 | 762 | 762 | 619 | 619 | B-2-1c
ELST22 | WARL21 | 59.244 | 0.59 | Composite | 0.2456 | 2.4772 | 22.8481 | 762 | 762 | 619 | 619 | B-2-1c
ELST22 | WATS22 | 5.398 | 0.222 | Composite | 0.0251 | 0.2347 | 3.8776 | 762 | 762 | 619 | 619 | B-2-1c
FERR21 | SKLG21 | 20.033 | 0.685 | Composite | 0.0991 | 0.9874 | 9.8077 | 865 | 823 | 752 | 823 | B-2-1c
FERR22 | FERR2B | 0.554 | 0.16 | Composite | 0.002 | 0.0234 | 1.3262 | 1031 | 1031 | 981 | 981 | B-2-1c
FERR2B | SKLG21 | 19.545 | 0.56 | Composite | 0.0975 | 0.9671 | 8.7544 | 865 | 823 | 752 | 823 | B-2-1c
FFES21 | TRAW21 | 7.291 | 0.133 | Composite | 0.0771 | 0.3081 | 2.8868 | 551 | 512 | 442 | 512 | B-2-1c
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570 | B-2-1c
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570 | B-2-1c
GRST2A | LACK2A | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1175 | 1119 | 1023 | 1119 | B-2-1c
GRST2A | LACK2B | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1129 | 1119 | 1000 | 1000 | B-2-1c
GRST2B | LACK2B | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1129 | 1119 | 1000 | 1000 | B-2-1c
GRST2B | LACK2C | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1129 | 1119 | 1000 | 1000 | B-2-1c
HACK2A | TOTT2B | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 1093 | 1031 | 926 | 1031 | B-2-1c
HACK2B | TOTT2A | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 1093 | 1031 | 926 | 1031 | B-2-1c
HAMB4A | PEWO41 | 19.698 | 0.752 | Composite | 0.0308 | 0.3917 | 24.9792 | 2473 | 2473 | 2189 | 2189 | B-2-1c
HAMB4B | PEWO41 | 19.698 | 0.592 | Composite | 0.0308 | 0.3911 | 20.9006 | 2473 | 2473 | 2189 | 2189 | B-2-1c
HAMH41 | WILE41 | 84.14 | 0.7 | Composite | 0.1001 | 1.549 | 78.4627 | 2009 | 1912 | 1746 | 1912 | B-2-1c
HARK23 | STEW21 | 83.682 | 0.117 | Composite | 0.4944 | 3.549 | 23.7211 | 774 | 774 | 676 | 676 | B-2-1c
HAWP21 | NORT21 | 30.238 | 0.459 | Composite | 0.0719 | 1.1367 | 14.2369 | 908 | 874 | 720 | 801 | B-2-1c
HIGM41 | WBUR41 | 14.852 | 0.229 | Composite | 0.0254 | 0.2958 | 13.2571 | 2212 | 2125 | 1979 | 2125 | B-2-1c
HINP41 | SAFO41 | 26.58 | 8.94 | Composite | 0.0421 | 0.5573 | 218.3267 | 2009 | 1911 | 1746 | 1911 | B-2-1c
HINP41 | SEAB41 | 57.813 | 8.99 | Composite | 0.0765 | 1.1045 | 239.9146 | 2009 | 1911 | 1746 | 1911 | B-2-1c
HURS21 | LITT2A | 5.164 | 2.938 | Composite | 0.0279 | 0.3019 | 12.6277 | 864 | 864 | 824 | 861 | B-2-1c
HURS21 | LITT2B | 5.14 | 2.863 | Composite | 0.0277 | 0.2987 | 12.3347 | 864 | 864 | 824 | 861 | B-2-1c
IMPP41 | MELK41 | 78.775 | 3.913 | Composite | 0.0882 | 1.4129 | 130.2038 | 1424 | 1424 | 1424 | 1424 | B-2-1c
IROA21 | MELK2A | 33.683 | 0.38 | Composite | 0.1862 | 1.7591 | 10.7703 | 581 | 581 | 524 | 524 | B-2-1c
IROA21 | MELK2B | 33.683 | 0.951 | Composite | 0.1877 | 1.7704 | 15.6295 | 581 | 581 | 524 | 524 | B-2-1c
IVER21 | WWEY22 | 25.652 | 0.342 | Composite | 0.0975 | 1.059 | 10.9579 | 960 | 960 | 839 | 839 | B-2-1c
IVER22 | WATS21 | 13.881 | 0.483 | Composite | 0.0643 | 0.601 | 9.0158 | 776 | 776 | 631 | 631 | B-2-1c
IVER22 | WATS22 | 13.881 | 0.436 | Composite | 0.0642 | 0.5997 | 8.5049 | 776 | 776 | 631 | 631 | B-2-1c
IVER2A | LALE21 | 17.186 | 0.402 | Composite | 0.0656 | 0.7143 | 9.2206 | 841 | 841 | 665 | 665 | B-2-1c
KEAR21 | WHGA21 | 14.509 | 0.241 | Composite | 0.0667 | 0.6208 | 6.5558 | 835 | 835 | 665 | 665 | B-2-1c
KEAR21 | WHGA21 | 14.509 | 0.129 | Composite | 0.0665 | 0.6177 | 5.3384 | 213 | 213 | 289 | 289 | B-2-1c
KITW21 | OLDB21 | 7.704 | 0.597 | Composite | 0.0301 | 0.3318 | 8.6639 | 667 | 667 | 619 | 619 | B-2-1c
KITW21 | OLDB2A | 8.278 | 0.222 | Composite | 0.0317 | 0.3449 | 4.7492 | 772 | 772 | 619 | 619 | B-2-1c
KNAR21 | MONF21 | 38.531 | 0.141 | Composite | 0.2716 | 1.7712 | 11.0429 | 551 | 513 | 443 | 513 | B-2-1c
LACK41 | SALH41 | 10.237 | 0.25 | Composite | 0.0184 | 0.2024 | 10.54 | 1831 | 1739 | 1588 | 1739 | B-2-1c
LACK41 | THTO41 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2030 | B-2-1c
LACK41 | THTO42 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2030 | B-2-1c
LITT41 | WTHU4E | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1815 | B-2-1c
LITT41 | WTHU4F | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1815 | B-2-1c
NEEP21 | PITS21 | 0.851 | 3.975 | Composite | 0.0214 | 0.1378 | 26.8236 | 419 | 419 | 381 | 381 | B-2-1c
NEEP21 | SHEC21 | 0.851 | 4.428 | Composite | 0.0234 | 0.1494 | 29.8542 | 419 | 419 | 381 | 381 | B-2-1c
OCKH21 | WIEN2A | 4.623 | 0.283 | Composite | 0.0216 | 0.202 | 4.2819 | 672 | 672 | 599 | 599 | B-2-1c
PEMB41 | WALH41 | 217.727 | 5.468 | Composite | 0.2372 | 3.8063 | 207.4152 | 2779 | 2568 | 2217 | 2568 | B-2-1c
RASS41 | WALH41 | 72.788 | 5.269 | Composite | 0.0799 | 1.2847 | 109.6583 | 2779 | 2568 | 2217 | 2568 | B-2-1c
RATS41 | WILE41 | 21.748 | 0.216 | Composite | 0.0397 | 0.435 | 16.174 | 1309 | 1309 | 1067 | 1067 | B-2-1c
REBR21 | TOTT23 | 3.305 | 9.678 | Composite | 0.0166 | 0.2027 | 106.1327 | 1205 | 1127 | 1044 | 1127 | B-2-1c
REBR22 | TOTT24 | 3.305 | 11.448 | Composite | 0.0174 | 0.2151 | 125.3726 | 1205 | 1127 | 1044 | 1127 | B-2-1c
ROCH21 | WHGA21 | 11.489 | 0.257 | Composite | 0.053 | 0.4934 | 5.9105 | 841 | 841 | 665 | 665 | B-2-1c
ROCH21 | WHGA21 | 11.489 | 0.238 | Composite | 0.0529 | 0.4929 | 5.7039 | 419 | 419 | 404 | 404 | B-2-1c
SEAB41 | WHSO4A | 30.426 | 3.89 | Composite | 0.0374 | 0.5858 | 97.4265 | 1424 | 1424 | 1424 | 1424 | B-2-1c
STAL4A | THOM41 | 69.271 | 6.952 | Composite | 0.0793 | 1.2727 | 151.2452 | 1442 | 1442 | 1314 | 1314 | B-2-1c
STAL4B | STSB4A | 26.581 | 7.031 | Composite | 0.0345 | 0.532 | 124.2199 | 1436 | 1436 | 1308 | 1308 | B-2-1c
THOM21 | WMEL21 | 23.791 | 0.947 | Composite | 0.1105 | 1.0548 | 15.8849 | 764 | 764 | 698 | 698 | B-2-1c
THOM2A | WMEL21 | 24.413 | 0.8 | Composite | 0.1126 | 1.0793 | 10.588 | 955 | 882 | 762 | 882 | B-2-1c
GARB1Q | SLOY1K | 14.229 | 0.671 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Change
GARB1R | SLOY1J | 14.185 | 0.715 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Change
GARB1S | SLOY1J | 14.229 | 0.671 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Change
GARB1T | SLOY1K | 14.185 | 0.715 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Change
CONN2J | LOCB2J | 76.071 | 0.269 | Composite | 0.458 | 4.1987 | 16.184 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
AREX1A | MAHI1B | 7.5 | 0.5 | Composite | 0.5731 | 1.6545 | 1.2722 | 365 | 360 | 350 | 360 | B-2-2b | 2025 | Addition
BENB1T | BLCW1- | 32.15 | 0.9 | Composite | 1.1801 | 6.5296 | 3.3413 | 199 | 191 | 178 | 191 | B-2-2b | 2025 | Addition
CLYS3A | WHBR3A | 13.1 | 2.5 | Composite | 16.4566 | 43.5395 | 0.3436 | 42 | 40 | 36 | 40 | B-2-2b | 2025 | Addition
CLYS3B | WHBR3B | 13.1 | 2.5 | Composite | 17.1837 | 42.3511 | 0.2892 | 42 | 40 | 36 | 40 | B-2-2b | 2025 | Addition
CROO1Q | NEIL1- | 12.56 | 0.22 | Composite | 0.4737 | 2.7011 | 0.9855 | 229 | 211 | 183 | 211 | B-2-2b | 2025 | Change
CROO1R | NEIL1- | 12.56 | 0.23 | Composite | 0.4738 | 2.702 | 0.9994 | 229 | 211 | 183 | 211 | B-2-2b | 2025 | Change
MOFF1- | SCOP1- | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293 | B-2-2b | 2025 | Addition
MOFF1A | SCOP1A | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293 | B-2-2b | 2025 | Addition
MOFF1A | SCOP1A | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293 | B-2-2b | 2025 | Addition
CHAP1- | OFOA1T | 24.82 | 0.18 | Composite | 0.984 | 5.6173 | 1.5274 | 171 | 155 | 155 | 155 | B-2-2b | 2027 | Addition
CLAW1- | DESA1Q | 6.4 | 2.3 | Composite | 0.5256 | 1.6179 | 3.5471 | 167 | 160 | 147 | 160 | B-2-2b | 2027 | Addition
CRYR4- | TORN4- | 9.36 | 1.97 | Composite | 0.0144 | 0.2171 | 44.1355 | 1415 | 1415 | 1415 | 1415 | B-2-2b | 2027 | Change
CULR2- | LOAN2- | 3.75 | 0.174 | Composite | 0.0171 | 0.1576 | 4.1452 | 1096 | 1029 | 924 | 1029 | B-2-2b | 2027 | Addition
DUNF1Q | INKE1Q | 7.58 | 0.09 | Composite | 0.5757 | 1.7891 | 0.5513 | 132 | 122 | 106 | 122 | B-2-2b | 2027 | Change
DUNF1R | INKE1R | 7.58 | 0.09 | Composite | 0.5757 | 1.7891 | 0.5513 | 132 | 122 | 106 | 122 | B-2-2b | 2027 | Change
EAST1Q | GLLE1- | 1.5 | 0.3 | Composite | 0.1236 | 0.3498 | 0.4484 | 133 | 124 | 107 | 124 | B-2-2b | 2027 | Addition
GLLE1- | WNUK1- | 17 | 0.5 | Composite | 1.2996 | 3.7201 | 1.6799 | 200 | 200 | 200 | 200 | B-2-2b | 2027 | Addition
GNSH1- | KEOO1Q | 10.1 | 0.9 | Composite | 0.7816 | 2.2655 | 2.0167 | 272 | 231 | 231 | 231 | B-2-2b | 2027 | Addition
KILS2- | KILT2Q | 3.56 | 0.29 | Composite | 0.0165 | 0.1465 | 2.1425 | 204 | 177 | 177 | 177 | B-2-2b | 2027 | Change
KILS2- | KILT2R | 3.56 | 0.33 | Composite | 0.0168 | 0.1474 | 2.2967 | 204 | 177 | 177 | 177 | B-2-2b | 2027 | Change
SMEA4Q | TORN4- | 54.32 | 1.94 | Composite | 0.0742 | 1.1033 | 70.0791 | 1360 | 1280 | 1280 | 1280 | B-2-2b | 2027 | Change
BLAH1- | GLGL1Q | 13.6 | 0.375 | Composite | 0.5207 | 2.9382 | 1.1932 | 181 | 164 | 164 | 164 | B-2-2b | 2029 | Change
BLAH1- | GLGL1R | 13.6 | 0.375 | Composite | 0.5207 | 2.9382 | 1.1932 | 181 | 164 | 164 | 164 | B-2-2b | 2029 | Change
BRAP1- | ERSK1Q | 3.17 | 5.4 | Composite | 0.3985 | 1.1026 | 12.4454 | 121 | 110 | 106 | 110 | B-2-2b | 2029 | Change
BRAP1- | ERSK1R | 3.45 | 6.23 | Composite | 0.4418 | 1.1771 | 12.9647 | 102 | 79 | 79 | 79 | B-2-2b | 2029 | Change
CHAP1- | GRNA1- | 12.83 | 0.3 | Composite | 0.797 | 3.0442 | 0.9509 | 144 | 144 | 144 | 144 | B-2-2b | 2029 | Change
CLFO1- | CURR1A | 27 | 1.6 | Composite | 2.1169 | 6.0497 | 3.3907 | 133 | 124 | 107 | 124 | B-2-2b | 2029 | Addition
COAL1A | KENN1- | 16 | 3.4 | Composite | 1.2963 | 3.7441 | 5.0291 | 167 | 160 | 148 | 160 | B-2-2b | 2029 | Change
CRDY3A | EWEH3- | 4.736 | 0.35 | Composite | 3.8899 | 14.1591 | 0.06 | 38 | 38 | 38 | 38 | B-2-2b | 2029 | Change
CRDY3B | EWEH3- | 4.775 | 0.35 | Composite | 3.9211 | 14.2732 | 0.0602 | 38 | 38 | 38 | 38 | B-2-2b | 2029 | Change
CURR2- | SIGH2Q | 1.54 | 1.7 | Composite | 0.0169 | 0.1036 | 6.0402 | 120 | 120 | 120 | 120 | B-2-2b | 2029 | Change
CURR2- | SIGH2R | 1.54 | 1.67 | Composite | 0.0168 | 0.103 | 5.941 | 120 | 120 | 120 | 120 | B-2-2b | 2029 | Change
DAER1- | MOFF1A | 6.1 | 6.8 | Composite | 0.6601 | 1.7847 | 8.6959 | 133 | 124 | 107 | 124 | B-2-2b | 2029 | Addition
DEVO1- | STIR1T | 5.8 | 5.816 | Composite | 0.3236 | 1.8724 | 7.2413 | 162 | 154 | 141 | 154 | B-2-2b | 2029 | Change
DUNB1Q | INWI1Q | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 102 | 91 | 91 | 91 | B-2-2b | 2029 | Change
DUNB1R | INWI1R | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 102 | 91 | 91 | 91 | B-2-2b | 2029 | Change
ELDE1Q | NEIL1- | 3.82 | 0.18 | Composite | 0.1455 | 0.8324 | 0.4574 | 229 | 211 | 183 | 211 | B-2-2b | 2029 | Change
ELDE1R | NEIL1- | 3.82 | 0.23 | Composite | 0.1461 | 0.8373 | 0.5271 | 229 | 211 | 183 | 211 | B-2-2b | 2029 | Change
EWEH1Q | GRNA1- | 15.9 | 0.36 | Composite | 1.2138 | 3.4754 | 1.4335 | 241 | 241 | 241 | 241 | B-2-2b | 2029 | Change
GLNI1- | MOSM1A | 1.41 | 0.09 | Composite | 0.0651 | 0.2344 | 0.3797 | 229 | 229 | 229 | 229 | B-2-2b | 2029 | Change
GLNI1- | MOSM1B | 1.41 | 0.11 | Composite | 0.0654 | 0.2362 | 0.4421 | 171 | 171 | 171 | 171 | B-2-2b | 2029 | Change
HLND1- | WISH1- | 17 | 1.01 | Composite | 1.3056 | 3.8061 | 2.1392 | 167 | 160 | 148 | 160 | B-2-2b | 2029 | Addition
KNOK1- | MAHI1C | 2.5 | 0.5 | Composite | 0.1407 | 0.5692 | 0.9179 | 241 | 230 | 210 | 230 | B-2-2b | 2029 | Addition
MAHI3- | TRLO3- | 8.722 | 5.5 | Composite | 12.1114 | 32.1139 | 0.6017 | 25 | 25 | 25 | 25 | B-2-2b | 2029 | Change
BODE41 | CONQ41 | 30.717 | 0.21 | Composite | 0.0335 | 0.5367 | 22.5401 | 2665 | 2561 | 2217 | 2561 | B-2-2c | 2027 | Addition
BODE41 | CONQ42 | 30.717 | 0.21 | Composite | 0.0335 | 0.5367 | 22.5401 | 2665 | 2561 | 2217 | 2561 | B-2-2c | 2027 | Addition
BODE41 | PENT41 | 49.211 | 0.8 | Composite | 0.0653 | 0.9665 | 36.8939 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Addition
BODE41 | PENT41 | 49.211 | 0.8 | Composite | 0.0653 | 0.9665 | 36.8939 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Addition
BRIM2A | TOTT21 | 7.437 | 0.311 | Composite | 0.025 | 0.3106 | 5.4901 | 2310 | 2100 | 2030 | 2100 | B-2-2c | 2027 | Change
BRIM2B | TOTT22 | 7.305 | 0.393 | Composite | 0.0247 | 0.3075 | 6.344 | 2310 | 2100 | 2030 | 2100 | B-2-2c | 2027 | Change
BRIM4C | HACK41 | 13.209 | 0.527 | Composite | 0.0209 | 0.2597 | 13.6792 | 3100 | 3100 | 3100 | 3100 | B-2-2c | 2027 | Addition
BRIM4D | HACK41 | 13.209 | 0.676 | Composite | 0.021 | 0.2614 | 15.3056 | 3100 | 3100 | 3100 | 3100 | B-2-2c | 2027 | Addition
DRAX41 | EGGB42 | 11.188 | 0.64 | Composite | 0.0129 | 0.1991 | 15.0423 | 2089 | 2089 | 1878 | 1878 | B-2-2c | 2027 | Change
KINO41 | WALE41 | 9.467 | 0.8 | Composite | 0.0104 | 0.1673 | 17.2184 | 3326 | 3160 | 2633 | 2813 | B-2-2c | 2027 | Addition
MFSN2B | TADT2B | 14.18 | 0.6 | Composite | 0.0705 | 0.6359 | 10.1219 | 1500 | 1500 | 1300 | 1500 | B-2-2c | 2027 | Addition
NORT41 | SPEN41 | 21.134 | 2 | Composite | 0.0276 | 0.4062 | 12.7287 | 2810 | 2700 | 2510 | 2700 | B-2-2c | 2027 | Change
NORT41 | SPEN42 | 21.134 | 2 | Composite | 0.0276 | 0.4062 | 12.7287 | 2810 | 2700 | 2510 | 2700 | B-2-2c | 2027 | Change
SPEN41 | STEW41 | 37.795 | 0.126 | Composite | 0.0498 | 0.7386 | 24.4993 | 2780 | 2670 | 2480 | 2670 | B-2-2c | 2027 | Change
SWAN41 | WALH41 | 133.752 | 5.468 | Composite | 0.146 | 2.3458 | 152.0578 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Addition
BARK41 | WHAM41 | 9.662 | 0.124 | Composite | 0.0151 | 0.1915 | 10.4342 | 3100 | 3100 | 3100 | 3100 | B-2-2c | 2029 | Change
BRAI4A | BRFO41 | 41 | 8 | Composite | 0.0441 | 0.8075 | 127.9671 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2029 | Addition
BRAI4B | BRFO41 | 41 | 8 | Composite | 0.0442 | 0.8076 | 127.9635 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2029 | Addition
BRIN41 | CHTE41 | 22.464 | 0.22 | Composite | 0.0245 | 0.3933 | 17.2091 | 2810 | 2700 | 2510 | 2700 | B-2-2c | 2029 | Addition
BRLE41 | MELK41 | 77.5 | 4.4 | Composite | 0.1029 | 1.4603 | 101.331 | 2830 | 2770 | 2680 | 2770 | B-2-2c | 2029 | Change
COTT41 | HIMB41 | 7.099 | 0.25 | Composite | 0.0113 | 0.1388 | 9.876 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Addition
COWL41 | MITY41 | 100.105 | 2.092 | Composite | 0.1293 | 1.8315 | 98.6831 | 1180 | 1132 | 877 | 979 | B-2-2c | 2029 | Change
COWL41 | WALH41 | 89.553 | 2.092 | Composite | 0.1112 | 1.627 | 92.3926 | 1180 | 1132 | 877 | 979 | B-2-2c | 2029 | Change
FECK41 | MITY41 | 65.268 | 7.5 | Composite | 0.0997 | 1.2484 | 222.0437 | 2830 | 2770 | 2680 | 2770 | B-2-2c | 2029 | Change
FECK41 | WALH41 | 55.11 | 7.5 | Composite | 0.082 | 1.0511 | 215.9994 | 2830 | 2770 | 2680 | 2770 | B-2-2c | 2029 | Change
FOUX41 | TRAW41 | 14.128 | 9.54 | Composite | 0.0248 | 0.3917 | 231.479 | 1830 | 1830 | 1830 | 1830 | B-2-2c | 2029 | Addition
GRAI41 | TILB41 | 26.642 | 2.049 | Composite | 0.0267 | 0.4794 | 61.4717 | 2950 | 2950 | 2950 | 2950 | B-2-2c | 2029 | Change
HIMB41 | WBUR41 | 14.852 | 0.229 | Composite | 0.0224 | 0.2868 | 17.1381 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Addition
KINO41 | TILB41 | 15.478 | 1.835 | Composite | 0.0149 | 0.2859 | 47.1231 | 2950 | 2950 | 2950 | 2950 | B-2-2c | 2029 | Change
MARV4B | SUND42 | 13.955 | 1 | Composite | 0.0218 | 0.2688 | 8.3345 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Change
PENT41 | TRAW41 | 41.698 | 9.71 | Composite | 0.0611 | 0.9304 | 251.71 | 1830 | 1830 | 1830 | 1830 | B-2-2c | 2029 | Change
RATS41 | STOB41 | 26.72 | 0.179 | Composite | 0.0451 | 0.5238 | 21.6497 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Change

## Series Capacitor
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
ECCL4A | ECCL4C | 0 | 0 | Series Capacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771 | B-2-1b
ECCL4B | ECCL4D | 0 | 0 | Series Capacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771 | B-2-1b
GRNA4- | GRNA4C | 0 | 0 | Series Capacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771 | B-2-1b
MOFF4- | MOFF4C | 0 | 0 | Series Capacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771 | B-2-1b
HUTT41 | HUTT42 | 0 | 0 | Series Capacitor | 0 | 0.5114 | 0 | 2771 | 2771 | 2771 | 2771 | B-2-1c
HUTT41 | HUTT43 | 0 | 0 | Series Capacitor | 0 | 0.5114 | 0 | 2771 | 2771 | 2771 | 2771 | B-2-1c

## Series Reactor
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
EKIL3A | EKIL3B | 0 | 0 | Series Reactor | 0.5744 | 108.498 | 0 | 30 | 30 | 30 | 30 | B-2-1b
KAIM3- | KAIM3A | 0 | 0 | Series Reactor | 0.0625 | 13.5546 | 0 | 120 | 120 | 120 | 120 | B-2-1b
KAIM3- | KAIM3B | 0 | 0 | Series Reactor | 0.0624 | 13.55 | 0 | 120 | 120 | 120 | 120 | B-2-1b
LOAN2- | LOAN2Q | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620 | B-2-1b
LOAN2- | LOAN2R | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620 | B-2-1b
WIYH2- | WIYH2R | 0 | 0 | Series Reactor | 0.005 | 1.5 | 0 | 1000 | 1000 | 1000 | 1000 | B-2-1b
DIDC41 | DIDC41 | 0 | 0 | Series Reactor | 0.0063 | 0.5 | 0 | 2640 | 2640 | 2640 | 2640 | B-2-1c
DRAX41 | DRAX42 | 0 | 0 | Series Reactor | 0.006 | 2 | 0 | 1320 | 1320 | 1320 | 1320 | B-2-1c
ELST41 | ELST4A | 0 | 0 | Series Reactor | 0.0125 | 1.1437 | 0 | 2000 | 2000 | 2000 | 2000 | B-2-1c
FIDF21 | FIDF21 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750 | B-2-1c
FIDF21 | FIDF21 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750 | B-2-1c
GRAI41 | GRAI41 | 0 | 0 | Series Reactor | 0.0027 | 2.3091 | 0 | 2002 | 2002 | 2002 | 2002 | B-2-1c
LISD21 | LISD2A | 0 | 0 | Series Reactor | 0.0173 | 1.387 | 0 | 750 | 750 | 740 | 740 | B-2-1c
SELL4A | SELL4A | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 1860 | 1860 | 1860 | 1860 | B-2-1c
SHUR41 | SHUR41 | 0 | 0 | Series Reactor | 0 | 2 | 0 | 2400 | 2400 | 2400 | 2400 | B-2-1c
WBUR41 | WBUR42 | 0 | 0 | Series Reactor | 0.0026 | 2.3169 | 0 | 1500 | 1500 | 1500 | 1500 | B-2-1c
WTHU4C | WTHU4E | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400 | B-2-1c
WTHU4D | WTHU4F | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400 | B-2-1c
ELST41 | ELST4B | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 2000 | 2000 | 2000 | 2000 | B-2-2c | 2029 | Addition
ELST41 | ELST4B | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 2000 | 2000 | 2000 | 2000 | B-2-2c | 2029 | Addition

## SSSC
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
BLYT21 | BLYT22 | 0 | 0 | SSSC | 0 | 1.5868 | 0 | 1360 | 1307 | 1217 | 1307 | B-2-1c
BLYT21 | BLYT23 | 0 | 0 | SSSC | 0 | 1.5868 | 0 | 1360 | 1307 | 1217 | 1307 | B-2-1c
HARK21 | HARK23 | 0 | 0 | SSSC | 0 | 1.8512 | 0 | 774 | 774 | 676 | 676 | B-2-1c
HARK21 | HARK24 | 0 | 0 | SSSC | 0 | 3.7025 | 0 | 854 | 795 | 700 | 795 | B-2-1c
KEAD43 | KEAD44 | 0 | 0 | SSSC | 0 | 0.25 | 0 | 3326 | 3159 | 2971 | 3159 | B-2-1c
PEWO2A | PEWO2C | 0 | 0 | SSSC | 0 | 0.476 | 0 | 1521 | 1461 | 1360 | 1461 | B-2-1c
PEWO2B | PEWO2D | 0 | 0 | SSSC | 0 | 0.476 | 0 | 1521 | 1461 | 1360 | 1461 | B-2-1c
SALH41 | SALH42 | 0 | 0 | SSSC | 0 | 0.125 | 0 | 1831 | 1739 | 1588 | 1739 | B-2-2c | 2025 | Addition

## Zero Length
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
GRAI41 | GRAI41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159 | B-2-1c
GRAI41 | GRAI41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159 | B-2-1c
GRAI41 | GRAI41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159 | B-2-1c
MANN41 | MANN41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159 | B-2-1c
MANN41 | MANN41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159 | B-2-1c
MARH41 | MARH4A | 0 | 0 | Zero Length | 0 | 0 | 0 | 2860 | 2860 | 2860 | 2860 | B-2-1c
MARH42 | MARH4B | 0 | 0 | Zero Length | 0 | 0 | 0 | 2860 | 2860 | 2860 | 2860 | B-2-1c
NECT41 | NECT4A | 0 | 0 | Zero Length | 0 | 0 | 0 | 1364 | 1364 | 1250 | 1250 | B-2-1c
NECT41 | NECT4B | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159 | B-2-1c
TOTT2A | TOTT22 | 0 | 0 | Zero Length | 0 | 0 | 0 | 904 | 904 | 904 | 904 | B-2-1c
TOTT2A | TOTT24 | 0 | 0 | Zero Length | 0 | 0 | 0 | 950 | 950 | 830 | 830 | B-2-1c
TOTT2B | TOTT21 | 0 | 0 | Zero Length | 0 | 0 | 0 | 904 | 904 | 904 | 904 | B-2-1c
TOTT2B | TOTT23 | 0 | 0 | Zero Length | 0 | 0 | 0 | 950 | 950 | 830 | 830 | B-2-1c
WIMB21 | WIMB2A | 0 | 0 | Zero Length | 0 | 0 | 0 | 995 | 930 | 728 | 806 | B-2-1c

## Series Compensation
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
CELL41 | CELL42 | 0 | 0 | Series Compensation | 0 | 0.375 | 0 | 2420 | 2330 | 2170 | 2330 | B-2-2c | 2027 | Addition
CELL41 | CELL43 | 0 | 0 | Series Compensation | 0 | 0.125 | 0 | 2420 | 2330 | 2170 | 2330 | B-2-2c | 2027 | Addition
COTT42 | COTT43 | 0 | 0 | Series Compensation | 0 | 0.3125 | 0 | 3326 | 3160 | 2971 | 3160 | B-2-2c | 2027 | Addition

## Mechanically Switched Capacitor
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Sheet_Name | Year | Status
ALYTH | ALYT2A | 1 | 100 | 0 | Mechanically Switched Capacitor | 275 | B-4-1a
BEAULY | BEAU1J | 1 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1a
BEAULY | BEAU1K | 1 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1a
KINARDOCHY | KINA2K | 1 | 100 | 0 | Mechanically Switched Capacitor | 275 | B-4-1a
MACDUFF | MACD3- | 1 | 10 | 0 | Mechanically Switched Capacitor | 33 | B-4-1a
TEALING | TEAL1- | 1 | 90 | 0 | Mechanically Switched Capacitor | 132 | B-4-1a
Cockenzie | COCK2- | 1 | 231 | 0 | Mechanically Switched Capacitor | 275 | B-4-1b
Elvanfoot | ELVA4- | 1 | 226 | 0 | Mechanically Switched Capacitor | 400 | B-4-1b
Longannet | LOAN2- | 1 | 225 | 0 | Mechanically Switched Capacitor | 275 | B-4-1b
Longannet | LOAN2- | 2 | 225 | 0 | Mechanically Switched Capacitor | 275 | B-4-1b
Moffat | MOFF4- | 1 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1b
Windyhill | WIYH2- | 1 | 150 | 0 | Mechanically Switched Capacitor | 275 | B-4-1b
Aberthaw | ABTH11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Aberthaw | ABTH11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Abham | ABHA11 | 3 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Abham | ABHA12 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Alverdiscott | ALVE11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Beddington | BEDD21 | 4B | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Beddington | BEDD22 | 3B | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Berkswell | BESW11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Berkswell | BESW12 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Berkswell | BESW12 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bishops Wood | BISW11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bishops Wood | BISW11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Blyth | BLYT21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Blyth | BLYT21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Bolney | BOLN11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bolney | BOLN11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bolney | BOLN12 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bolney | BOLN12 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bolney | BOLN41 | 7 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Bolney | BOLN41 | 5 | 228 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Bradford West | BRAW11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bramford | BRFO11 | 1B | 59 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bramford | BRFO11 | 1A | 59 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bramford | BRFO11 | 1C | 59 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bridgewater | BRWA11 | 1A | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bridgewater | BRWA11 | 1B | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Burwell Main | BURW41 | -2 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Burwell Main | BURW41 | -1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Bushbury | BUSH11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bushbury | BUSH11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bushbury | BUSH11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bushbury | BUSH21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Capenhurst | CAPE21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Cellarhead | CELL11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Cellarhead | CELL11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Cellarhead | CELL12 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Cellarhead | CELL12 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Cellarhead | CELL41 | 7 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Cellarhead | CELL41 | 8 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Chickerell | CHIC42 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
City Road | CITR41 | 2 | 56 | 0 | Mechanically Switched Capacitor | 13 | B-4-1c
City Road | CITR41 | 4 | 56 | 0 | Mechanically Switched Capacitor | 13 | B-4-1c
Coventry | COVE11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Coventry | COVE11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Coventry | COVE12 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Cowley | COWL11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Cowley | COWL11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Cowley | COWL11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Drakelow | DRAK41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Drakelow | DRAK41 | 3 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
East Claydon | ECLA12 | 3 | 61 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
East Claydon | ECLA41 | 5 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Enderby | ENDE41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Enderby | ENDE41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Exeter | EXET11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Exeter | EXET41 | 1 | 28 | 0 | Mechanically Switched Capacitor | 13 | B-4-1c
Exeter | EXET41 | 2 | 28 | 0 | Mechanically Switched Capacitor | 13 | B-4-1c
Fleet | FLEE11 | 2B | 53 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Fleet | FLEE11 | 2C | 53 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Fleet | FLEE11 | 2A | 53 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Fleet | FLEE41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Grendon | GREN11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Grendon | GREN11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Grendon | GREN11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Grendon | GREN41 | 6 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Grendon | GREN41 | 5 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Grendon | GREN41 | 3 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Grendon | GREN41 | 4 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Hams Hall | HAMH41 | 3 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Hams Hall | HAMH41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Harker | HARK21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Harker | HARK41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Harker | HARK41 | 3A | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Harker | HARK41 | 3B | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Hurst | HURS21 | 2B | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Hutton | HUTT41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Indian Queens | INDQ11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Indian Queens | INDQ11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Indian Queens | INDQ11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Indian Queens | INDQ41 | 5 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Iron Acton | IROA11 | 6 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Ironbridge | IRON11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Ironbridge | IRON12 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Ironbridge | IRON12 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Ironbridge | IRON41 | 5 | 231 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Kearsley | KEAR11 | 1C | 53 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Kearsley | KEAR11 | 1B | 53 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Kearsley | KEAR11 | 1A | 53 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Kirkby | KIBY11 | 1A | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Kirkby | KIBY11 | 4A | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Kirkby | KIBY11 | 2A | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Kirkby | KIBY11 | 3B | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Kirkstall | KIRK21 | 3 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Landulph | LAND11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Legacy | LEGA41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Lovedean | LOVE41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Mannington | MANN11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Mannington | MANN11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Mannington | MANN11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Mannington | MANN11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Mannington | MANN11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Mannington | MANN11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Melksham | MELK11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Melksham | MELK11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Melksham | MELK11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Monk Fryston | MONF21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Ninfield | NINF41 | 2 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Ocker Hill | OCKH21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Pelham | PELH41 | -1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Pelham | PELH41 | -2 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Port Ham | PORH11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Port Ham | PORH11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Rainhill | RAIN11 | 2 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Rainhill | RAIN11 | 4 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Rainhill | RAIN12 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Rainhill | RAIN12 | 3 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Richborough | RICH41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Rochdale | ROCH11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Rochdale | ROCH11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Rochdale | ROCH11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Rye House | RYEH41 | -1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Rye House | RYEH41 | -2 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Skelton Grange | SKLG11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Skelton Grange | SKLG11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Skelton Grange | SKLG11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Skelton Grange | SKLG21 | 6 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
St. Johns Wood | SJOW11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
St. Johns Wood | SJOW11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
St. Johns Wood | SJOW11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Stella West | STEW41 | 2 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Stella West | STEW41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Sundon | SUND41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Sundon | SUND42 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Uskmouth | USKM12 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Walham | WALH41 | 1 | 57 | 0 | Mechanically Switched Capacitor | 13 | B-4-1c
Walpole | WALP11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Walpole | WALP11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Walpole | WALP11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Warley | WARL11 | 1C | 52 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Warley | WARL11 | 1B | 52 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Warley | WARL11 | 1A | 52 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
West Ham | WHAM41 | 4 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
West Melton | WMEL12 | 3C | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
West Melton | WMEL12 | 3A | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
West Melton | WMEL12 | 3B | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Whitegate | WHGA21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Wymondley | WYMO41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Wymondley | WYMO41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
ALYTH | ALYT4J | 1 | 100 | 0 | Mechanically Switched Capacitor | 400 | B-4-2a | 2027 | Addition
KINARDOCHY | KINA4B | 1 | 100 | 0 | Mechanically Switched Capacitor | 400 | B-4-2a | 2029 | Addition
Kincardine | KINC2- | 2 | 232 | 0 | Mechanically Switched Capacitor | 275 | B-4-2b | 2029 | Addition
Kincardine | KINC2- | 1 | 232 | 0 | Mechanically Switched Capacitor | 275 | B-4-2b | 2029 | Addition
Harker GIS | HARG41 | 4 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2027 | Addition
Harker GIS | HARG41 | 5A | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2027 | Addition
Harker GIS | HARG41 | 5B | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2027 | Addition
Lackenby | LACK41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2027 | Addition
Norton | NORT41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2027 | Addition
Spennymoor | SPEN41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2027 | Addition
Penwortham | PEWO41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2028 | Addition
Penwortham | PEWO41 | 2 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2028 | Addition
Harker GIS | HARG41 | 4 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2029 | Addition

## SVC
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Sheet_Name | Year | Status
ALYTH | ALYT2A | 1 | 225 | 225 | SVC | 275 | B-4-1a
BEAULY | BEAU2J | 1 | 150 | 150 | SVC | 275 | B-4-1a
KINARDOCHY | KINA2J | 1 | 225 | 225 | SVC | 275 | B-4-1a
TEALING | TEAL2J | 1 | 225 | 75 | SVC | 275 | B-4-1a
Bolney | BOLN41 | 6 | 225 | 100 | SVC | 32 | B-4-1c
Cellarhead | CELL41 | 6 | 150 | 95 | SVC | 7.9 | B-4-1c
Cellarhead | CELL41 | 5 | 150 | 95 | SVC | 7.9 | B-4-1c
Exeter | ELLA21 | 5 | 150 | 95 | SVC | 7.9 | B-4-1c
Exeter | ELLA21 | 3 | 150 | 95 | SVC | 7.9 | B-4-1c
FECKENHAM | FECK21 | 6 | 150 | 75 | SVC | 275 | B-4-1c
Harker | HARK21 | 7 | 146 | 124 | SVC | 14 | B-4-1c
Harker | HARK21 | 8 | 146 | 124 | SVC | 14 | B-4-1c
Landulph | LAND42 | H | 60 | 60 | SVC | 13 | B-4-1c
Lovedean | LOVE41 | 5 | 150 | 95 | SVC | 7.9 | B-4-1c
Ninfield | NINF41 | 5 | 225 | 100 | SVC | 56.6 | B-4-1c
NINFIELD | NINF41 | 6 | 150 | 150 | SVC | 400 | B-4-1c
Richborough | RICH41 | 1 | 225 | 100 | SVC | 32 | B-4-1c
Sellindge Compound A | SELL4A | 2 | 150 | 150 | SVC | 56.6 | B-4-1c
Sellindge Compound A | SELL4A | 1 | 150 | 150 | SVC | 56.6 | B-4-1c
ST.JOHNS WOOD | SJOW21 | 1 | 150 | 106 | SVC | 275 | B-4-1c
ST.JOHNS WOOD | SJOW21 | 3 | 150 | 106 | SVC | 275 | B-4-1c
ALYTH | ALYT4J | 1 | 225 | 225 | SVC | 400 | B-4-2a | 2027 | Addition
KINARDOCHY | KINA4A | 1 | 225 | 225 | SVC | 400 | B-4-2a | 2029 | Addition
Mannington | MANN82 | 2 | 150 | 95 | SVC | 400 | B-4-2c | 2025 | Addition

## Shunt Reactor - SGT tertiary
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Sheet_Name | Year | Status
BEAULY | BEAU3U | 1 | 0 | 90 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
BEAULY | BEAU3V | 2 | 0 | 90 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
CROSSAIG | CRSS3W | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
CROSSAIG | CRSS3X | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
DOUNREAY | DOUN3W | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
DOUNREAY | DOUN3X | 2 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
FORT AUGUSTUS | FAUG3W | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
FORT AUGUSTUS | FAUG3X | 2 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
FORT AUGUSTUS | FAUG3Y | 3 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
FORT AUGUSTUS | FAUG3Z | 4 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
KINTORE | KINT3W | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
KINTORE | KINT3Y | 2 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
TEALING | TEAL3W | 1 | 0 | 28.96 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
TEALING | TEAL3Y | 1 | 0 | 28.89 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
DOUNREAY | DOUN3Y | 1 | 0 | 90 | Shunt Reactor - SGT tertiary | 33 | B-4-2a | 2029 | Addition
ORKNEY FINSTOWN | FINS3Y | 1 | 0 | 90 | Shunt Reactor - SGT tertiary | 33 | B-4-2a | 2029 | Addition

## Shunt Reactor
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Sheet_Name | Year | Status
KINTORE | KINT1- | 1 | 0 | 100 | Shunt Reactor | 132 | B-4-1a
KINTORE | KINT1B | 2 | 0 | 100 | Shunt Reactor | 132 | B-4-1a
TEALING | TEAL1- | 1 | 0 | 100 | Shunt Reactor | 132 | B-4-1a
Bonnybridge | BONN3U | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Bonnybridge | BONN3V | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Coalburn | COAL3U | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Coalburn | COAL3V | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Crystal Rig | CRYR3V | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Currie | CURR3W | 3 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Dewar Place | DEWP3- | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Dewar Place | DEWP3- | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Eccles | ECCL3V | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Elvanfoot | ELVA3V | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Hunterston North | HUNN3W | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Hunterston North | HUNN3X | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Kilgallioch | KILG2- | 1 | 0 | 60 | Shunt Reactor | 275 | B-4-1b
Kilmarnock South | KILS3U | 4 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Kilmarnock South | KILS3X | 6 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Mark Hill | MAHI3U | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Moffat | MOFF3U | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Neilston | NEIL3U | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Neilston | NEIL3V | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Smeaton | SMEA3U | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Smeaton | SMEA3V | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Strathaven | STHA3V | 4 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Torness | TORN4- | 1 | 0 | 150 | Shunt Reactor | 400 | B-4-1b
Torness | TORN4- | 2 | 0 | 150 | Shunt Reactor | 400 | B-4-1b
Wishaw (Gowkthrapple) | WISH3W | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Windyhill | WIYH3W | 3 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Barking | BARK22 | 2B WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Barking | BARK22 | 2B WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Barking | BARK22 | 4B WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Barking | BARK22 | 4B WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Beddington | BEDD21 | 3B | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Beddington | BEDD21 | 1B | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Beddington | BEDD21 | 5B | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Beddington | BEDD22 | 4B | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Beddington | BEDD23 | 2B | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Beddington | BEDD23 | 6A | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Birkenhead | BIRK21 | 4 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Birkenhead | BIRK21 | 4 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bolney | BOLN41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Bolney | BOLN41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Bradford West | BRAW21 | 4 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bradford West | BRAW21 | 4 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bradford West | BRAW21 | 3 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Bradford West | BRAW21 | 5 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Bramford | BRFO41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Bredbury | BRED21 | 102 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bredbury | BRED21 | 101 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bredbury | BRED21 | 301 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bredbury | BRED21 | 302 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bushbury | BUSH2* | 3 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Bustleholme | BUST21 | 1 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bustleholme | BUST21 | 1 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bustleholme | BUST21 | 4 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Canterbury North | CANT41 | 4 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Cellarhead | CELL41 | 2 WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Cellarhead | CELL41 | 3 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Cellarhead | CELL41 | 2 WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Cellarhead | CELL41 | 3 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Chesterfield | CHTE21 | 4 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Chickerell | CHIC41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Chickerell | CHIC41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Chickerell | CHIC42 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Cilfynydd | CILF41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Cilfynydd | CILF41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Cilfynydd | CILF41 | 6 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Cilfynydd | CILF41 | 4 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
City Road | CITR41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Coventry | COVE21 | 3 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Cowley | COWL41 | 2 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Cowley | COWL41 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Drakelow | DRAK41 | 6 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Drakelow | DRAK41 | 4 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Drax | DRAX41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Drax | DRAX41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
East Claydon | ECLA41 | 1 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
East Claydon | ECLA41 | 2 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
East Claydon | ECLA41 | 2 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
East Claydon | ECLA41 | 1 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Elland | ELLA21 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Elstree | ELST41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Feckenham | FECK41 | 4 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Feckenham | FECK41 | 4 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Fleet | FLEE41 | 3 WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Fleet | FLEE41 | 4A WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Fleet | FLEE41 | 4A WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Fleet | FLEE41 | 3 WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Frodsham | FROD41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Grain | GRAI41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Grendon | GREN41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Greystones A | GRST2A | 1 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Greystones B | GRST2B | 3 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Hams Hall | HAMH41 | 4 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Hurst | HURS21 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Hurst | HURS21 | 3 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Hurst | HURS21 | 4 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Hurst | HURS21 | 7 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Hurst | HURS21 | 2A | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Hurst | HURS21 | 1 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Indian Queens | INDQ41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Indian Queens | INDQ41 | 2 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Iver | IVER21 | 1A | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Iver | IVER21 | 3A | 0 | 60 | Shunt Reactor | 13 | B-4-1c
IVER | IVER4A | 6B | 0 | 55 | Shunt Reactor | 400 | B-4-1c
IVER | IVER4B | 5A | 0 | 55 | Shunt Reactor | 400 | B-4-1c
Jordanthorpe 33kV | JORD31 | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1c
Kearsley | KEAR21 | 3A | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Kingsnorth | KINO41 | 2 WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Kingsnorth | KINO41 | 1 WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Kingsnorth | KINO41 | 2 WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Kingsnorth | KINO41 | 1 WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Kingsnorth | KINO41 | 4 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Kingsnorth | KINO41 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Kirkstall | KIRK21 | 4 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Kirkstall | KIRK21 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Laleham | LALE21 | 1 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Laleham | LALE21 | 2 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Laleham | LALE21 | 3 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Landulph | LAND41 | 2 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Landulph | LAND41 | 2 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Landulph | LAND42 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Legacy | LEGA41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Legacy | LEGA41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Lister Drive | LISD21 | 1 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Lovedean | LOVE41 | 3 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Lovedean | LOVE41 | 4A | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Lovedean | LOVE41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Lovedean | LOVE41 | 7 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Melksham | MELK41 | 5 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Melksham | MELK41 | 6 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Melksham | MELK41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Mill Hill | MILH2A | 2A WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Mill Hill | MILH2A | 1B WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Mill Hill | MILH2A | 1B WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Mill Hill | MILH2B | 2A WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Nechells | NECH21 | 4 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Nechells | NECH21 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Nechells | NECH21 | 4 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
New Cross | NEWX21 | 6 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
New Cross | NEWX21 | 5 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Ninfield | NINF41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Nursling | NURS41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Oldbury | OLDB21 | 2 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Oldbury | OLDB21 | 2 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Pelham | PELH41 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Pembroke | PEMB41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Pembroke | PEMB41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Pentir | PENT41 | 2 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Pentir | PENT41 | 5 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Penwortham | PEWO41 | 6 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Pitsmoor 33kV | PITS31 | 4 | 0 | 60 | Shunt Reactor | 33 | B-4-1c
Pitsmoor 33kV | PITS31 | 3 | 0 | 60 | Shunt Reactor | 33 | B-4-1c
Ratcliffe-On-Soar | RATS41 | 2 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Rayleigh | RAYL41 | 5 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Sandford | SAFO41 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Sandford | SAFO41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Skelton Grange | SKLG21 | 3 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Spennymoor | SPEN41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
St. Johns Wood | SJOW21 | 2B | 0 | 60 | Shunt Reactor | 13 | B-4-1c
St. Johns Wood | SJOW41 | 2 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
St. Johns Wood | SJOW41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
St. Johns Wood | SJOW41 | 4 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Stalybridge | STAL41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Stella West | STEW21 | 2 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Stocksbridge | STSB41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Sundon | SUND41 | 5 WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Sundon | SUND41 | 5 WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Sundon | SUND42 | 8 WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Sundon | SUND42 | 8 WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Thorpe Marsh | THOM42 | 6 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Tottenham | TOTT21 | 5 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Tottenham | TOTT21 | 1 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Tottenham | TOTT22 | 3 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Tynemouth | TYNE21 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Walham | WALH41 | 3 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Walham | WALH41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Walham | WALH41 | 4 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Walpole | WALP41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Walpole | WALP41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
West Ham | WHAM41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
West Weybridge | WWEY21 | 1 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Whitegate | WHGA21 | 4B | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Whitegate | WHGA21 | 4A | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Willesden | WISD21 | 2B | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Willesden | WISD21 | 3B WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Willesden | WISD21 | 3B WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Wimbledon | WIMB21 | 4 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Wimbledon | WIMB21 | 2 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Wimbledon | WIMB41 | -5 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Wimbledon | WIMB41 | 6 | 0 | 225 | Shunt Reactor | 400 | B-4-1c
Wylfa | WYLF41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Wymondley | WYMO41 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
BROADFORD | BROA1A | 1 | 0 | 60 | Shunt Reactor | 132 | B-4-2a | 2029 | Addition
BROADFORD | BROA1B | 1 | 0 | 60 | Shunt Reactor | 132 | B-4-2a | 2029 | Addition
EDINBANE | EDIN1A | 1 | 0 | 60 | Shunt Reactor | 132 | B-4-2a | 2029 | Addition
EDINBANE | EDIN1B | 1 | 0 | 60 | Shunt Reactor | 132 | B-4-2a | 2029 | Addition
Arecleoch Repowering Windfarm | ARCR2- | 1 | 0 | 60 | Shunt Reactor | 275 | B-4-2b | 2027 | Addition
Gretna | GRNA3U | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-2b | 2027 | Addition
HUNE4- | HUNE4- | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2b | 2025 | Addition
Cottam | COTT41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2025 | Addition
East Claydon | ECLA41 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2025 | Addition
Ironbridge | IRON41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2025 | Addition
Melksham | MELK41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2025 | Addition
Rowdown | ROWD41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2025 | Addition
Taunton | TAUN42 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2025 | Addition
Willington East | WILE41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2025 | Addition
Bramford | BRFO41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2029 | Addition
Bramford | BRFO41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2029 | Addition
Chesterfield | CHTE41 | 4 | 0 | 60 | Shunt Reactor | 400 | B-4-2c | 2029 | Addition
Elstree | ELST41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2029 | Addition
Feckenham | FECK41 | 1 | 0 | 230 | Shunt Reactor | 400 | B-4-2c | 2029 | Addition
Melksham | MELK41 | 1 | 0 | 230 | Shunt Reactor | 400 | B-4-2c | 2029 | Addition

## STATCOM
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Sheet_Name | Year | Status
MELGARVE | MELG4J | 1 | 100 | 100 | STATCOM | 400 | B-4-1a
MELGARVE | MELG4K | 1 | 100 | 100 | STATCOM | 400 | B-4-1a
Hunterston Converter Station | HUCS4- | 1 | 248 | 382 | STATCOM | 400 | B-4-1b
PHOENIX HYBRID REACTIVE COMPENSATION | NEIL2- | 1 | 70 | 70 | STATCOM | 275 | B-4-1b
ECCLES | ECCL4A | 1 | 150 | 150 | STATCOM | 400 | B-4-2b | 2025 | Addition
ECCLES | ECCL4B | 1 | 150 | 150 | STATCOM | 400 | B-4-2b | 2025 | Addition

## Sync Comp
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Sheet_Name | Year | Status
PHOENIX HYBRID REACTIVE COMPENSATION | NEIL2- | 1 | 70 | 33 | Sync Comp | 275 | B-4-1b
ORKNEY FINSTOWN | FINS1- | 1 | 70 | 35 | Sync Comp | 132 | B-4-2a | 2029 | Addition
ORKNEY FINSTOWN | FINS1- | 2 | 70 | 35 | Sync Comp | 132 | B-4-2a | 2029 | Addition
EDINBANE | EDIN8A | 1 | 125 | 50 | Sync Comp | 132 | B-4-2a | 2029 | Addition
EDINBANE | EDIN8B | 1 | 125 | 50 | Sync Comp | 132 | B-4-2a | 2029 | Addition
ECCLES | ECCL4A | 1 | 150 | 70 | Sync Comp | 400 | B-4-2b | 2025 | Addition
ECCLES | ECCL4B | 1 | 150 | 70 | Sync Comp | 400 | B-4-2b | 2025 | Addition